## L-Specs Review Comments
Review Comments - L-Specs
Project: | L-Specs Revision (L-100 through L-119) |  |  |  |  | CR AVD Group Chief: | Luke Bowland
[6 empty] | CR AVI Specs Engineer: | Virginia Groeschel
[6 empty] | Statewide Electrical Engineer: | Jeff Carleton
Number | Section | MOS Description | MOS Justification | FAA Comments | WAS-Kinney Engineering Comments | LPS-STANTEC Comments | DH-MBA Consulting Comments | DOT Comments | Response By | Response Date
L-100: RUNWAY AND TAXIWAY LIGHTING
1 | 100-2.1a(1) | Constant Current Regulator, L-828. Added 2nd sentence to item description | Most aviation electrical work includes a regulator. |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-21
1.1 | 100-2.1 | spelled out quantity of submittals | CSI / AP style guide for numerals. |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-21
2 | 100-2.1a.(2) | Runway Edge Light, Bi-directional High-Intensity, L-862 Revised paragraph | Revised to meet current industry standards and practice. |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-21
3 | 100-2.1a.(3) | Runway Edge Light, Medium Intensity, L-861 a) Removed "incandescent" b) Revised "lamp" to "halogen lamp (LED)" c) Replaced "Lexan" with "glass" | Revised to meet current industry standards and practice. |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-21
4 | 100-2.1a.(4) | Taxiway Edge Light, Medium Intensity, L861T a) Removed "incandescent" b) Revised "lamp" to "halogen lamp (LED)" c) Replaced "Lexan" with "glass" | Revised to meet current industry standards and practice. |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-21
5 | 100-2.1a.(5) | Airport Signs, L-858 Added additional description after, "lighted" | Adds clarity and more information to description. |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-21
6 | 100-2.1a.(7) | Airport Light Base, L-867 Revised paragraph | Adds clarity and more information to description. |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-21
7 | 100-2.1a.(8) | Airport Light Base, L-867 Added Note to Designer on HDPE light bases | As of AC 150/4345-53D addendum (5/2018), HDPE light bases are currently not FAA certified. Added Note to Designer to check the AC for certified equipment. If HDPE light bases not certified, discuss with project manager for spec language revision and material replacement. |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-21
8 | 100-2.1a.(9) | Airport Light Base, L-868 a) Removed "12 inches deep" after "Size B" b) Added 2nd sentence | Started at ANC, but now used elsewhere in the state. |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-21
9 | 100-2.1a.(10) | Isolating Transformer, L-830 Removed "30/45 W or 200 W" | Updates description. |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-25
10 | 100-2.1a.(11) | Isolating Transformer, L-830 Removed 2nd sentence | Updates description. |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-25
11 | 100-2.1a.(12) | Isolating Transformer, L-830-1 Removed item | Addressed in 100-2.1a.(10). |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-25
12 | 100-2.1a.(13) | Isolating Transformer, L-830-6 Removed item | Addressed in 100-2.1a.(10). |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-25
13 | 100-2.1a.(14) | Radio Control Equipment, L-854 a) Added "Style A" after "Type I" b) Added "field-adustable frequency" after "antenna and feedline and" c) Renumbered to 100-2.1a.(12) | Updates description and numbering. |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-25
14 | 100-2.1a.(15) | Flush Taxiway Centerline Light Fixture a) Revised paragraph b) Renumbered to 100-2.1a.(13) | C,D,K are for low-visibility. A,B are for standard. All ANC fixtures have been C,D,K. |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-25
15 | 100-2.1a.(16) | Flush Runway Light Fixture a) Revised paragraph b) Renumbered to …(14) | Updates description to current usage of LED and equipment. |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-25
16 | 100-2.1a.(17) | Primary Handhole, L-868 a) Revised paragraph b) Renumbered to…(15) | Modified paragraph to let the project drawings determine drain holes and conduit entries. |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-25
17 | 100-2.1a.(18) | Wind Cone Primary Handhole, L-867 a) Revised paragraph b) Renumbered to…(16) | Modified paragraph to let the project drawings determine drain holes and conduit entries. |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-25
18 | 100-2.1a.(19) | Handhole, L-867, Size B, Watertight Renumbered to …(17) | Renumbered |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-25
19 | 100-2.1a.(20) | Elevated Runway Guard Light a) Added equipment b) Renumbered to…(18) | Revised to meet current industry standards and practice. |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-25
20 | 100-2.1a.(21) | Flush Guard Light Fixture a) Added equipment b) Renumbered to…(19) | Revised to meet current industry standards and practice. |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-25
21 | 100-2.1a.(22) | Flush Runway Edge Light Fixture a) Added equipment b) Renumbered to…(20) | Revised to meet current industry standards and practice. |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-25
22 | 100-2.1a.(23) | Spacer Ring, L-867 a) Added equipment b) Renumbered to…(21) | Revised to meet current industry standards and practice. |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-25
23 | 100-2.1a.(24) | Light Base Extension, L-867 a) Added equipment b) Renumbered to…(22) | Revised to meet current industry standards and practice. |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-25
23.1 | 100-2.1b. | Sealer: (1) no change (2) added subparagraph for re-enterable conduit sealant usee by DOT&PF for watertight seal applications | Revised to meet current industry standards and practice. |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-25
24 | 100-2.1c. | Transformer Support Platform Replaced, "13 3/4 inch high prefabricated steel" with "12 inch high non-metallic" | Industry moving away from traditional metal transformer stand due to poor manufacturing, leading to sharp edges and damage to cables and personnel. |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-25
24.1 | 100-2.1e. | Regularly Used Commercial Items: Clarified electrical items must be third party listed and labeled. | Compliance with State code and industry standard requirements. |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg / jsc | 2019-02-25
25 | 100-2.1h. | Lubricant and Sealant Added 2nd sentence | Originally requested for Ted Stevens Anchorage International Airport (ANC), but modified for use on applicable projects. |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-25
26 | 100-2.1i. | Soft Gasket Removed, "in watertight lighting system" |  |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-25
27 | 100-2.1m. | Fixture Bolts Added new subsection | F593C to be used as the new high-strength standard. The maximum length can be adjusted based on project needs. Updated in accordance with FAA documentation and manufacturer's recommendations. |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-25
28 | 100-2.1n. | Temporary Runway Lighting System Added new subsection | Use of temporary runway lighting system is frequent enough to include, but discussion may be needed as previous product specified is no longer manufactured, with few alternatives. A recent King Salmon project used solar-powered, radio-controlled lights rather than hard wired. |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-25
29 | 100-2.1o. | Drain Rock Added new subsection | Included to define the drain rock where detailed under light bases. Added a "Note to Designer" to remove subsection if drain rock defined elsewhere in project specifications. |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-25
30 | 100-2.1o. | Table 1. Gradation of Drain Rock Added Table | Included to define the drain rock where detailed under light bases. Added a "Note to Designer" to remove subsection if drain rock defined elsewhere in project specifications. |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-25
31 | 100-3.1 | General Added last 2 paragraphs | Accompanies temporary lighting in subsection 100-2.1n. Needs revisions if solar lighting is adopted. This is the typical language that has been used on past projects, but will need to confirm if DOT&PF wants to retain temporary fixtures for use on future projects. |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-25
31.1 | 100-3.1 | Added description of NEC in first sentence | Clarification of electrical standard |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | jsc / vg | 2019-02-25
32 | 100-3.2 | Installation of Non-Watertight Edge Lights a) Added two new sentences after 1st sentence b) Replaced "duct" with "light base" in 3rd sentence c) Added to 2nd to last sentence, "at an elevation that will place the frangible break point below finished grade as indicated on the Plans" d) Removed 4th paragraph | c) Commonly requested by various M&Os. Drawings usually define 1/4-1/2 below. d) This spec language is usually removed, as we don't want the contractor die-stamping the baseplate and light base and harming the finish coatings, causing corrosion. |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-25
33 | 100-3.3 | Installation of Flush Lights Revised subsection | 1. Revisions reflect typical installation applying to all flush-mounted lights. 2. Revised torque to 500 inch-pounds per manufacturers recommendations basd on new FAA data. 3. Revised setting outboard edge of the fixture to 1/8 inch (+/- 1/16 inch). This is below AC standards, but has been generally accepted on past projects. M&O would prefer to set fixtures lower. The last ANC project changed this to 5/16 inch. |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-25
34 | 100-3.4 | Installation of Watertight Edge Lights | Added "When called for on the Plans" to allow drawings to indicate use of insulating material. |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-25
34.1 | 100-3.4 | Installation of Watertight Edge Lights: - 3rd paragraph, change "duct seal" to "approved sealant" - 4th pararaph, add item b. to require conduit sealant. | Added specific requirement to seal conduit openings with an approved material. |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-25
| 100-3.8 | Spare Parts Revised paragraph | Updated paragraph and added language to include visual aid categories. |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-25
35 | 100-3.8 | Lump Sum. Revised formatting | Added subsection 100-4.1 for clarity. |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-25
36 | 100-4.1b | Unit Prices. Revised formatting | Added subsection 100-4.2 for clarity. |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-25
37 | 100-4.1c | Contingent Sum. Revised formatting and added language | Added subsection 100-4.3 for clarity. |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-25
38 | 100-5.1 | Items of Work Paid in Other Sections. Revised formatting and language | Revised formatting and added 3rd paragraph for clarity and description. |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-25
39 | 100-5.2 | Items of Work Paid in This Section 1. Revised language and updated references to pay items. 2. Items revised to AASHTOWare pay item number system. | Added language for clarity and consistency, where items involve similar work (e.g.: all elevated lights, all flush lights, etc.). |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-25
40 | 100-5.2 | Item L-100h, Remove Runway and Taxiway Light: 1. Updated pay item to AASHTOWare number system 2. Added language | 1. Updated pay item to align with AASHTOWare launch. 2 Revised to include a demolition note on the plans indicating that all associated conduit and conductors, concrete, foundations, etc are included in the removal. |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-25
41 | 100-5.2 | Item L-100r, Temporary Runway Lighting System: 1. Updated pay item to AASHTOWare number system 2. Added language | 1. Updated pay item to align with AASHTOWare launch. 2. Added Note to Designer: Add paragraph if temporary runway sections are included in specs. Otherwise, remove. |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-25
42 | 100-5.2 | "Payment will be made under:" 1. Added AASHTOWare pay item numbers 2. Added Note to Designers for guidance | This section revised with AASHTOWare pay items and descriptions. Any need for additional pay items will come from what the Designer uses from AASHTOWare’s Engineer’s Estimate and will be added in with track changes on. |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-25
43 | 100-5.2 | "Payment will be made under:" 1. Added AASHTOWare pay item numbers 2. Added Note to Designers for guidance | This section revised with AASHTOWare pay items and descriptions. Any need for additional pay items will come from what the Designer uses from AASHTOWare’s Engineer’s Estimate and will be added in with track changes on. |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-25
L-101: AIRPORT ROTATION BEACONS
1 |  | Spec Title Revised title | Updated for 10G conformance. |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-25
2 | 101-1.1 | Description Added "conduit" to included work. Added last sentence for removal and disposal of existing rotating beacons | Adds clarity and more information to description. |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-25
3 | 101-2.1b. | Removed 2.1b, c, d | b, c, & d are addressed in GCP 10, 20, 60 |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-25
4 | 101-2.2a. | Beacon. Added "400W" and removed "150W" before "strip heater" | Changed to 400W to match Class II beacons being installed. |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-25
5 | 101-2.3 thru 101-2.8 | Added 101-2.3 BEACON INSTALLATION paragraph back in referencing the AC and Plans. Numbering now matches 10G. |  | Why title/subject changed? Titles and subject for 101-1.1 - 101-2.8 should match | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-25
6 | 101-2.5 | Wire Revised paragraph | 1. Removed section for 10G conformance. 5000V cable is not anticipated to be used for rotating beacon installations. 2. Revised to "thermoset" and "XHHW-2" for low-temperature applications in Alaska. |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-25
7 | 101-2.6 | Conduit, revised paragraph | Clarification of allowance for IMC as acceptable material, and correction of UL 514B designation. |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | jsc/vjg | 2019-02-25
8 | 101-2.8 | Updated 2.8 with 10H sections a to e, and added f. | Added section from 10H. However, further discussion may be needed to ensure paint specs conform to current industry standards. May need input from paint subject matter expert. | If the spec is out date, say so and propose an alternative | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-25
9 | 101-2.9 | Added paragraph " 101.2.9 Disconnect Switch" to conform with 10H | NEC requires local disconnect for motorized equipment. Paragraph now 101-2.9; added for local disconnect in type 4X enclosure. |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-25
10 | 101-3.1 to 3.6 | Revised to conform to 10H |  |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-25
11 | 101-3.7 | Wiring. 1. Removed, "under paved areas" 2. Removed last sentence. 3. First paragraph, added second sentence. | 1. Deleted to apply L-108 and L-110 to all conduits, not just in paved areas. 2. Removed last sentence to quantify the run from the vault to the beacon tower. 3. Added sentence in first paragraph to match 10H. |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | jsc / vjg | 2019-02-25
12 | 101-3.8 | Panel and Cabinet. Added "If shown in the plans," and removed "Unless otherwise specified," | This is not typical for DOT installations, so changed to "if." |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-25
13 | 101-3.9 | Conduit. Added "fixed" before "steel beacon tower" Revised minimum conduit size and added sentence for LFMC per 10H. | Revised for clarity. |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-25
14 | 101-3.11 | Photo Electrical Control. Revised paragraph. | Clarify requirements for photoelectric control unit suitable for aviation service. |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | jsc | 2019-02-25
15 | 101-3.13 | Updated with 10H | Added section from 10H. However, further discussion may be needed to ensure paint specs conform to current industry standards. May need input from paint subject matter expert. | If the spec is out date, say so and propose an alternative | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-25
16 | 101-3.14 | Testing. Replaced "50" with "1,000", before "megohms" | For new installations, it is typical to get readings in the 1000's of megohms. The test results in this section have been increased at the request of state inspectors on past projects. The new results exceed the 100 megohm minimum standards required in 10G and by NETA. | See comments on L-108 | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-25
17 | 101-3.15 | Guarantee removed | Described in GCP 90-10 Construction Warranty provides a written warranty (GCP 90-10g(2)). Removed. |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-25
18 | 101-3.16 | Spare Parts. Added subsection, "101-3.15 Spare Parts." | Added subsection to include spare parts. Spare lamps as indicated are consistent with 10G. |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-25
19 | 101-4.2 | Method of Measurement. Added subsections, "101-4.2" | Added subsection for clarity regarding payment for removal of existing rotating beacon. | consistency with what? | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-25
20 | 101-4.3 | Method of Measurement. Added subsection, "101-4.3" | Added subsection for clarity regarding how spare parts to be paid. | consistency with what? | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-26
21 | 101-5.1 | Basis of Payment. 1. Added information about how "Spare Parts" will be paid 2. Pay item numbers changed to AASHTOWare pay items numbers | 1. All "Spare Parts" to be paid under one contingent sum item rather than having a small item in each spec (see example: Aniak Airport Improvements project). 2. Updated pay items to align with AASHTOWare. |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-26
22 | References |  |  |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | jsc / vjg | 2019-02-26
L-103: AIRPORT BEACON TOWERS
1 |  | Spec Title Revised title | Updated for 10H conformance. |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-26
2 | 103-1.1 | Description revised conform to 10H | Adds clarity and more information to description. |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-26
3 | 103-2.1 | Updated section to 10H | b, c, & d are addressed in GCP 10, 20, 60 | Why paragraphs b, c, d and e omitted? | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-26
4 | 103-2.2-b. | change "guide" to "guy" | typo correction. |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-26
5 | 103-2.3 | Updated section to 10H. Title revised to match 10G. Additional information included as subparagraphs under Lightning Protection. | Lightning protection information revised to reflect typical installation practices in Alaska. 10H only refers to NFPA 780. Current practice allows use of pole steel for the lightning protection down conductor on hinged beacon poles as stated in added language. | Why the change in title? | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-26
6 | 103-2.4 | Updated section to include 10H Paint language. Paragraphs reformatted as subparagraphs. Subsequent numbering revised. |  | Why the change in title? | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-26
7 | 103-2.5 | Foundation. | Section retained and revised to allow option for engineer design or contractor design. | ?? | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-26
8 | 103-2.6 | Ground Clamp. Removed | Removed to conform with 10H |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-26
9 | 103-3.2 | Excavation and Fill. Revised 4th paragraph | Revised 1st sentence to provide clarity. Edits are based on contractor-designed foundation and may be updated based on further discussion on subsection 103-2.8. |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-26
10 | 103-3.4 | Lighting Protection. 1. Added reference to NFPA 780 2. 4th paragraph, 3rd sentence: replaced "ground connector or clamp" with "exothermic welding" 3. 5th paragraph: added last sentence | 1. Reference added to conform to 10H. 2. 4th paragraph - Connection changed to exothermic weld to be consistent with other buried grounding connection requirements. 2. 5th paragraph - Added to conform to 10H. |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-26
11 | 103-3.5 | Painting. 1. Subsection 103-3.5a: Revised 1st and 3rd paragraphs 2. Subsection 103-3.5b: Revised sentence 3. Subsection 103-3.5c: Revised sentence | Revised to reflect factory-finished, or painted prior to erection of tower, to achieve higher quality finished product. |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-26
12 | 103-4.1 | modifed sentence | to match 10H |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-26
13 | 103-4.2 | Method of Measurement. Added subsections, "103-4.2" | Added subsection for clarity and consistency with other sections regarding concrete. |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-26
14 | 103-4.3 | Method of Measurement. Added subsections, "103-4.3" | Added subsection for clarity and consistency with other sections regarding payment for demo. |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-26
15 | 103-5.1 | Basis of Payment. Pay item numbers changed to to align with AASHTOWare | Updated pay items to align with AASHTOWare. |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-26
16 | References | References updated per 10H |  |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-26
L-107: AIRPORT WIND CONES
1 |  | Spec Title Revised title | Updated for 10H conformance. |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-26
2 | 107-1.1 | Description 1. 1st paragraph: Added last sentence 2. 2nd paragraph: Revised language | 1. Added for clarity and more information to description. 2. Revised to quantify conduit and conductors between the source and first handhole. Based on typical/current industry construction. 3. Relocated removal description to match 10H |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-26
3 | 107-2.1 | Removed c-f | c-f subsections are addressed in state GCP 10, 20, 60 | Why were para c - f omitted? | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-26
4 | 107-2.2 | Wind Cones. Revised language and added L-806 wind cones | Revised to add L-806 wind cones. Statement from Lucas Schneller: "Jeff [Jeffers] raised the question about the need to include additional information here similar to L-103 - design parameters, etc. Because the wind cone and pole are a certified assembly, the AC included already has all of the structural design and construction parameters defined. I don't know that additional information is needed." Question for Statewide: per previous statement, are additional requirements required to be included if AC covers structural requirements of certified assembly? | Need to state why there is a need to expand on the requirements of 150/5345-27 and address how to incorporate the optional language in 10G regarding source of power for the wind cone. | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-26
5 | 107-2.3 | Electrical Wire and Cable. Removed, "Type C cross-linked polyethylene insulated wire" and added "2" after "type XHHW-" | Removed "Type C..." to be consistent with 10G. 10G just refers to the L-824 spec and doesn't indicate types. Type B may be included as an option. |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | Discuss with Statewide and FAA | vjg | 2019-02-26
6 | 107-2.5 | Foundation. Added 2nd paragraph and highlighted for discussion purposes. Revised to allow option for engineer design or contractor design. | May need additional coordination/discussion with regions on language. Currently, only CR delegates the foundation design to the contractor. In NR and SC, the engineer designs the foundations. Statement/Question from Lucas Schneller: "Do we want design parameters included here similar to L-103 (120mph, etc)? Jeff had mentioned this. Thoughts on what these parameters should be - 120mph, etc similar to L-103 or the AC parameters for the wind cone assembly construction (which are much less)? If 120mph, they should be included, if AC maybe we're covered?" Additional discussion with Statewide/FAA: This item includes only the conduit from the wind cone to the first handhole. Plastic conduit, particularly PVC, is not used for this short section. Conduit beyond the first handhole is typically handled per L-110. | Why was 107-2.5 Plastic conduit ommited and para # assigned to "foundation"? | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | Discuss with Statewide and FAA | vjg | 2019-02-26
7 | 107-2.6 | Paint 1. Subsection 107-2.6a: Revised to match L-101 and L-103 2. Subsection 107-2.6c: Revised to match L-101 and L-103 3. Subsection 107-2.6d: Added subsection paragraph | Added to allow manufacturer's standard finish. Concrete is included in Foundation paragraph. Numbering is different due to plastic conduit being omitted. | Why was 107-2.6 concrete ommitted and para # assigned to paint? | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-26
8 | 107-2.7 | Wind Cone. Revised to "Windsock" | Revised to better define windsock fabric portion of the wind cone (the AC uses windsock to mean the fabric portion of the wind cone) and avoid confusion with subsection 107-2.2 Wind Cones. Numbering is different due to plastic conduit being omitted. | Similar to above comment | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-26
9 | 107-3.1 | Installation. 1. 1st sentence: Replaced "support" with "hinged" 2. Subsection 107-3.1b, 1st sentence: Removed "lighted" before "wind cone" and added "foundation" after "wind cone" | Added for clarity. |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-26
10 | 107-3.3 | Electrical Connection. Revised subsection | Revised to apply L-108 and L-110 to all conduit and cable, not just paved areas. Added second sentence in first paragraph to match 10H. Revised second paragraph to reflect division/payment of conduit and conductors to match the description in 1.1. |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-26
11 | 107-3.4 | Booster Transformer. Removes the reference to "Special Provisions" | Revised for clarity and conformance to 10H |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-26
12 | 107-3.5 | Ground Connection and Ground Rod. Revised paragraph | Added ground rod size to be consistent with other sections, and revised to exothermic weld to be consistent with other buried ground connection requirements. |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-26
13 | 107-3.6 | Painting. Revised paragraph | Revised to utilize factory-finish on manufactured components for a higher quality finish, considering it may reduce quality to have the contractor adding another coat of paint on factory-finished materials. |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-26
14 | 107-3.7 | Light Sources. Replaced "lamps" with "light sources" and added at the end of the paragraph, "for the source type designated on the Plans." | Revised for clarity and conformance to 10H |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-26
15 | 107-3.8 | Winch and Padlock. Revised 2nd paragraph | Revised for clarity and conformance to 10H |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-26
16 | 107-3.9c. | Testing. Revised "50 megaohms" to "2,000 megohms" and "10 megohms" to "1,000 megohms" | For new installations, it is typical to get readings in the 1000's of megohms. The test results in this section have been increased at the request of state inspectors on past projects. The new results exceed the 100 megohm minimum standards required in 10G and by NETA for 600V and the 1000 megohm NETA minimum for 5000V. See response on L-108. | See comment on L-108 | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-26
17 | 107-3.11 | Spare Parts. Added subsection 107-3.11 Spare Parts | Added to provide spare parts, within the limits of AIP funding per L-100. |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-26
18 | 107-4.1 | Method of Measurement. Added the last sentence to subsection 107-4.1 | Revised and added to clarify scope of pay item. |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-26
19 | 107-4.2 | Method of Measurement. Added subsections, "107-4.2" | Added subsection for clarity and consistency with other sections regarding concrete. |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-26
20 | 107-4.3 | Method of Measurement. Added subsections, "107-4.3" | Added subsection for clarity and consistency with other sections regarding payment for demo. |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-26
21 | 107-4.4 | Method of Measurement. Added subsections, "107-4.4" | Added subsection for clarity and consistency with other sections regarding spare parts. |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-26
22 | 107-5.1 | Basis of Payment Revised to AASHTOWare pay item numbers | Updated pay items to align with AASHTOWare. |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-26
23 | 107-5.1 | Material Requirements Added "Fed. Spec. TT-P-664D..." | Added for clarity. |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-26
24 | References | Updated title, added refs | Conform to 10H |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-26
L-108: UNDERGROUND POWER CABLE FOR AIRPORTS
1 |  | Spec Title Revised title | Updated for 10G conformance. |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-26
2 | 108-1.1 | Description Added last sentence | Added for clarity and more information to description. Statement regarding installation of cable for FAA added. | Why was the statement regarding "or furnishing or installation of cable for FAA owned/operated facilities." deleted? | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-26
3 | 108-2.1 | Removed c-f | c-f subsections are addressed in state GCP 10, 20, 60 | Why were para c - f from 10G not included? 108-2.1 Leave the language the same as 10G. Office names and internet address change frequently. | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-26
4 | 108-2.2 | Cable. 1. 3rd paragraph: Replaced, "UL type-2 and FAA type C" with "type XHHW-2" and revised "190°F" to "194°F" 2. 5th paragraph: Removed "copper" before "shielded" | Revised to reflect readily available materials. Recent experience has shown may not be posssible to find a copper shield and aluminum was approved by FAA as an alternate. "190°F" to "194°F" to match NEC. |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | jsc / vjg | 2019-02-26
5 | 108-2.3 | Bare Copper Wire (Counterpoise or Grounding). 1. Removed "Bare" from the subsection title 2. Revised 1st paragraph and added new 2nd paragraph | 2a. Added Insulated ground wire to allow use where required. 2b. Relocated from subsection 108-3.9 to a more appropriate location and consistent with 10H. |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-26
6 | 108-2.4 | Cable Connections. 1. 1st paragraph: Added last sentence 2. 108-2.4a: Removed manufacturer's name 3. 108-2.4b: Removed subsection 4. 108-2.4c: Revised paragraph 5. 108-2.4d: Added sentence from 108-2.4c 6. 108-2.4e: Revised paragraph 7. Added last two paragraphs | 1. Added for clarity and more information. 2. Removed per Statewide's comment. 3. Removed due to lack of use and not included in 10G. 4. Relocated sentence to factory-molded splice section in 108-2.4d. 5. Added sentence from 108-2.4c for relevance. 6. Replaced manufacturer's name with material spec and requirements, per Statewide's comments. 7. Added to apply to all cases listed in 108-2.4 and to be consistent with 10H. 8. Added additional figures to subparagraph b for accuracy. |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-26
7 | 108-2.5 - 108-2.8 | Added 2.5 Splicer Qualifications | Other 10H items described already in specs, per Electrical Engineers, in sections more closely related to construction testing. | Why were these renumbered and renamed vs 10G? | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-26
8 |  |  | Existing circuits paragraph was included in Part 3, as this paragraph addresses installation/construction rather than material topics. | Why was 10G 108-2.11 Existing Circuits deleted? Why was 10G 108-2.12 Detectable warning tape deleted? | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-26
9 |  |  | Added detectable marker tape to be consistent with L-110. (Note: 10H only includes detectable, not non-detectable.) |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-26
10 | 108-2.10 | Electrical Tape. Added subsection 108-2.10 Electrical Tape | This subsection added for typical industry use. |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-26
11 | 108-3.1-3.10 | Trenches, Backfill, and Restoration reformatted as subheadings under Installation in Trenches | Better match to 10H | Why re-title, renumbering and reformatting from what is in 10-G to what you have proposed? The titles and subjects of 108-3.1-3.10 should mirror what is in 10-G | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-26
12 | 108-3.1 | General. 1. 3rd paragraph: Revised paragraph 2. 4th paragraph, 1st sentence: Replaced "insulating" with "isolation" 3. 5th paragraph: Added new paragraph 4. Paragraph regarding slack cable added. 5. Proposed identification requirements are included in third paragraph of 108-3.1 | 1. Revised to clarify and expand circuit labeling requirements. 2. Revised for clarity. 3. Added paragraph to be consistent with 10H. 4. Added paragraph to match 10H. 5. Added a combination of DOT spec and 10H language; relocated labeling paragraph to more closely resemble 10H. | Why were these 10-G paragraphs deleted? "Provide not less than 3 feet (1 m) of cable slack on each side of all connections, isolation transformers, light units, and at points where cable is connected to field equipment. Where provisions must be made for testing or for future above grade connections, provide enough slack to allow the cable to be extended at least one foot (30 cm) vertically above the top of the access structure. This requirement also applies where primary cable passes through empty light bases, junction boxes, and access structures to allow for future connections, or as designated by the Engineer. Primary airfield lighting cables installed shall have cable circuit identification markers attached on both sides of each L-823 connector and on each airport lighting cable entering or leaving cable access points, such as manholes, hand holes, pull boxes, junction boxes, etc. Markers shall be of sufficient length for imprinting the cable circuit identification legend on one line, using letters not less than 1/4 inch (6 mm) in size. The cable circuit identification shall match the circuits noted on the construction plans." | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-26
13 | 108-3.2 | Installation in Duct or Conduit. 1. 3rd to the last sentence: Added "and shall not exceed cable manufacturer's recommendations" after "pulls or bends" 2. Removed fifth paragraph 3. 6th paragraph, last sentence: Replaced "1 foot" with "2 feet" before "above grade". 4. Paragraphs added. 5. Added Note to Designer | 1. Added to be consistent with 10H. 2. Removed paragraph in favor of revised requirements in 108-3.1. 3. Revised to provide additional slack for connections, per industry/contractor request. 4. Added to be consistent with 10H 5. Note to designer clarifies ensuring ratios of raceway to conductor or cable outside of 2.8 and 3.2, to prevent jamming. | Why were these paragraphs deleted: "Unless otherwise designated in the plans, where ducts are in tiers, use the lowest ducts to receive the cable first, with spare ducts left in the upper levels. Check duct routes prior to construction to obtain assurance that the shortest routes are selected and that any potential interference is avoided." "The Contractor shall submit the recommended pulling tension values to the Engineer prior to any cable installation. If required by the Engineer, pulling tension values for cable pulls shall be monitored by a dynamometer in the presence of the Engineer. Cable pull tensions shall be recorded by the Contractor and reviewed by the Engineer. Cables exceeding the maximum allowable pulling tension values shall be removed and replaced by the Contractor at the Contractor’s expense." | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | jsc /vjg | 2019-02-26
14 | 108-3.3 | Trenches, Backfill, and Restoration reformatted as subheadings under Installation in Trenches | More closely matches 10H. | Why was 103-3.3 title changed to "Trenching"?, Why the additional requirements | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | jsc /vjg | 2019-02-26
15 | 108-3.3 | Trenches, Backfill, and Restoration reformatted as subheadings under Installation in Trenches | More closely matches 10H. | Why was 103-3.3 title changed to "INSTALLATION IN TRENCHES."? | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-26
16 | 108-3.4 | Cable Markers. Added "When called for in the Plans" to allow the plans to determine their use. | Concrete slab cable markers for cable/conduit are rarely used in Alaska as they tend to be damaged or removed by snow removal operations. |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-26
17 | 108-3.5 | 1. Revised title to "Splicing" 2. Added marker tape requirement to backfilling | 1. Matches 10H 2. Matches 10H | Why title/subject changed? | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-26
18 | 108-3.6 | Revised title | More closely matches 10H. | Why title/subject changed? | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-26
19 | 108-3.7 | Title not revised to match 10H | Lightning protection/grounding paragraphs left closer to previous DOT spec based on local installation practices. 10H is much more extensive in this area of the spec, and doesn't match what is normally installed locally | Why title/subject changed? | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-26
20 | 108-3.7 | Grounding System. Revised subsection | 1. 1st paragraph: Revised to reflect ground wire in conduit as typically installed in Alaska and added language to ensure reliability of circuit ground through light bases. 2. 2nd paragraph: Relocated last sentence to subsection 108-2.3, which is consistent with 10G. 3. 4th paragraph: Added paragraph to reflect typical installation in accordance with ACs. Consistent with 10G. 4. Same paragraphs included, but renumbered due to separation of paragraphs indicated above. 5. Grounding and lightning protection paragraphs modified to reflect typical installations in Alaska. | Why title/subject changed? | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-26
21 | 108-3.8 | (Revised to Section 3.5) Splicing. 1. Subsection 108-3.8b: Removed entire subsection 2. Subsection 108-3.8c: Added last sentence 3. Subsection 108-3.8d: Added last sentence 4. Revised subparagraphs b and c to include finishing options. 5. Added heat trace paragraph to match 10H. 6. Revised section to 3.5 - Same paragraphs included, but renumbered due to rearrangment of paragraphs. | 1. Removed due to lack of general use and not in 10H. 2. Revised to add heat shrink as commonly installed in Alaska. 3. Revised to add heat shrink as commonly installed in Alaska. 4. Similar to 10H. 5. Matches 10H 6. Matches better to 10H Statement from Lucas Schneller: "This methodology varies from airport to airport, but this provides two common methods. | Why title/subject changed? | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-26
22 | 108-3.9 | 1. Revised to Section 3.6 2. Bare Counterpoise Wire Installation and Grounding for Lightning Protection. Removed last sentence in 1st paragraph 3. Paragraphs renumbered per above. 4. Grounding and lightning protection paragraphs modified to reflect typical installations in Alaska. 5. Changed minimum size to 6awg 6. Added exothermic bonding paragraph 7. Added option to allow bare ground wire for bonding of baseplates. | 1. Title matches 10H. 2. Relocated sentence to subsection 108-2.3, which is consistent with 10H. 3. - 7. Revisions to match 10H | Why title/subject changed? | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-26
23 | 108-3.11 | (Revised to 3.10) Testing. Revised subsections 108-3.10c & d | 1. Subsection 108-3.10c: Removed last sentence when subsection 3.12 added. 2. Subsection 108-3.10d: Replaced "multiple" with "600V" and "50" to "1,000". For new installations, it is typical to get readings in the 1000's of megohms. The test results in this section have been increased at the request of state inspectors on past projects. The new results exceed the 100 megohm minimum standards required in 10H and by NETA for 600V and the 1000 megohm NETA minimum for 5000V. 3. Response to FAA Question: For new installations, it is typical to get readings in the 1000's of megohms and the test numbers in this section have been increased at the request of state inspectors on past projects. | Why 1000 megohms when 10G only requires 100 megohms? | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-26
24 | 108-3.12 | (Revised to 3.8) Existing Circuits. Added new subsection 108-3.8 Existing Circuits | Added to be consistent with 10H For new installations, it is typical to get readings in the 1000's of megohms and the test numbers in this section have been increased at the request of state inspectors on past projects. Added "unless otherwise approved by the Engineer" to account for the possibility of a situation where it is not a contractor installation issue causing a decrease in insulation resistance. | This paragraph should go under 108-2.11 to match 10G | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-26
25 | 108-4.4 | Method of Measurement. Added last sentence | Added language to allow ground rods to be specified as subsidiary in other sections if desired. |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-26
26 | 108-4.6 | Method of Measurement. Added new subsection | Added subsection for clarity and consistency with other sections regarding payment for demo. |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-26
27 | 108-4.7 | Method of Measurement. Added new subsection | Added subsection to allow quantifying of temporary jumpers if desired. |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-26
28 | 108-5.1 | Basis of Payment Revised to AASHTOWare pay item numbers | Updated pay items to align with AASHTOWare. |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-26
L-109: AIRPORT TRANSFORMER VAULT AND VAULT EQUIPMENT
1 |  | Spec Title Revised title | Updated for 10H conformance. |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-26
2 |  | General Statement | Statement/Question from Lucas Schneller: "This section includes much more that we typically see. Normally we use small prefabricated buildings and DOT does not want field-constructed enclsoures. I would anticipate that if a larger facility (ie: ANC or FAI) constructs a new vault, they would normally use more in-depth CSI-type specs as an appendix. Do we want to strip out the field-constructed paragraphs from this section?" |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-26
3 | 109-1.1 | Added option for removal activities Removed potheads (previously removed from materials area of spec). | Matches 10H. |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-26
4 | 109-2.1 | General. Added subsection 109-2.1c Spelled out sumittal quantity to be consistent with other sections. | Added subsection to draw attention to Buy American requirements in GCP-60. GCPs 10, 20, 60 address submittal process, but can keep for electrical submittals. Future consideration to add electrical submittals to GCP 60. | Why the need rewrite and reformat entire paragraph? | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-26
5 | 109-2.5 | Rigid Steel and Intermediate Conduit. Revised subsection title to "Steel Conduit" and added information | a) Revised title to include steel conduits other than just rigid. b) Added 2nd paragraph in subsection to include EMT for interior use. |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | jsc/vjg | 2019-02-26
6 | 109-2.6 | Plastic Conduit. Replaced entire subsection | a) Removed previous subsection, "Asbestos Cement Duct" as it's obsolete and not in 10H. b) Replaced previous subsection with, "Plastic Conduit" per 10H. - Plastic conduit paragraph added. Doors moved to later paragraph. | Why were doors added? If needed add para at end so para #s match 10G | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-26
7 | 109-2.7 | Lighting. Added 2nd sentence to 1st paragraph and added 2nd paragraph | Revised to combine separate lighting sections and further define requirements. |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-26
8 | 109-2.8 | Outlets. Revised paragraph | Removed, "specification grade NEMA performance receptacles," to eliminate conflict with previous sentence. |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-26
9 | 109-2.9 | Switches. Replaced "NEMA Specification Grade Standard" with "heavy-duty grade" | Revised to specify higher-quality device. |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-26
10 | 109-2.10 | Paint. Added 10H section. To be discussed with regions & FAA | To be discussed with regions / FAA: Recent contractor/supplier discussions on projects have indicated that the previous paint specs are out of date. Consider discusion with FAA to confirm 10H language is current with industry standards/practice. | Propose something to replace out of date spec. | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-26
11 | 109-2.11 | High Voltage Bus. Removed entire subsection; replaced with Ground Bus | Removed subsection as equipment not used in Alaska and not in 10H. |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-26
12 | 109-2.12 | Bus Connectors Removed entire subsection; replaced with Square Duct | Removed subsection as equipment not used in Alaska and not in 10H. |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-26
13 | 109-2.13 | Bus Supports. Removed entire subsection; replaced with Ground Rods. Removed bolted ground rod connections (exothermic welds typically used and called out on plans). | Removed subsection as equipment not used in Alaska and not in 10H. |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-26
14 | 109-2.14 | Doors. Relocated and revised subsection. | Relocated subsection to separate doors for field-constructed buildings and doors for prefab buildings. Revised to clarify requirements. |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-26
15 | 109-2.15 | Square Duct. Revised subsection to 2.12; (Now Prefabricated Metal Housing) | Revised to replace named products with material specs. |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-26
16 | 109-2.16 | (Previously 2.19) FAA-Approved Equipment Added paragraph at end of section | Added to expand requiremets of control panels. Lucas Schneller Response to FAA: This requirement is overkill for the very small systems that make up the majority of projects in Alaska. A registered engineer is already determining the available fault current to meet the labeling requirements of NEC 110.24A and selecting the appropriate equipment to meet this fault current. | Why was 10G 109-2.19 Short circuit / coordination / device evaluation / arc flash analysis deleted? | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-26
17 | 109-2.17 | Potheads. Removed entire subsection (Now Other Electrical Equipment) Spelled out and included standards organization abbreviations. | Removed subsection as equipment not used in Alaska and not in 10H. |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-26
18 | 109-2.17 | Other electrical equipment. | Spellled out and included standards organization abbreviations. |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-26
19 | 109-2.21 | (Now 2.18) Wire. Revised 1st paragraph and subsection (b.) sizes | Revised paragraph to be consistent with 10H. Added use of thermoset and XHHW-2 for cold-weather application. Revised sizes to reflect typical installations. |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-26
20 | 109-2.22 | Section revised to 109-2.19 | Defines the floor system of the prefabricated building specified in 2.23. | Why the need for this para? | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-26
21 | 109-2.23 | (Now Section 109-2.20) Electrical Enclosure. | Section revised to reflect additional and updated construction requirements for prefabricated enclosures and to limit use of named products. |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-26
22 | 109-2.23a.(1) | (Now Section 109-2.20) Panels and Facings. Revised subsection to 109-2.20 | Increased to 3/4-inch for equipment and component mounting. Revised to require plywood on exterior regardless of finish material for added durability. |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-26
23 | 109-2.23g. | (Now Section 109-2.20) Electrical Enclosure. Revised subsection (g.) | Added second opening and exhaust fan. |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-26
24 | 109-2.23h. | (Now Section 109-2.20) Electrical Enclosure. Removed "Kason Industries No. 1053" references | Removed brand named products per Statewide comments. |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-26
25 | 109-2.23i. | (Now Section 109-2.20) Electrical Enclosure. Highlighted for discussion purposes | May need additional coordination/discussion with regions/FAA on removing or keeping brand names, which are referenced throughout ACs. |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-26
26 | 109-2.23j. | (Now Section 109-2.20) Electrical Enclosure. Revised cabinet size and deleted last sentence. | Previous cabinet was discontinued. Removed brand named products pwer Statewide comments. Justification - DOT M&O states the cabinet is used for safe storage of consumables and lighting parts; and the desk is used as a workspace | Need in justification why this section is needed. | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-26
27 | 109-2.27 | (Now Section 109-2.23) Radio Control Equipment. Added "Style A" after "Type 1", and added "field-adjustable" before receiver | Added for clarity and more information. Equipment installed in typical system installation. | Need in justification why this section is needed. | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-26
28 | 109-2.28 | (Now Section 109-2.24) Antenna for the Receiver-Controller. Revised subsection | Revised to be less project specific about antenna mounting location. Equipment installed in typical GA airport system installation. | Need in justification why this section is needed. | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-26
29 | 109-2.29 | (Now Section 109-2.25) Apron Floodlight. Revised subsection | Revised to replace named products with material requirements. Equipment installed in typical GA airport system installation. | Need in justification why this section is needed. | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-26
30 | 109-2.30 | (Now Section 109-2.26) Photo Electrical Control. Revised subsection | Revised to replace named products with material requirements. Equipment installed in typical GA airport system installation. Revised photo electrical control paragraph to match new requirements in L-101. | Need in justification why this section is needed. | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-26
31 | 109-2.34 | (Now Section 109-2.30) Service Entrance Equipment. Removed "Q0M2100VH" before "main breaker" | Removed brand-specific part number. Equipment installed in typical GA airport system installation. | Need in justification why this section is needed. | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | jsc /vjg | 2019-02-26
32 | 109-2.35 | (Now Section 109-2.31) Plug Cutout Added "lockable," before "2-pole Type" | Revised for clarity. Equipment installed in typical GA airport system installation. | Need in justification why this section is needed. | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-26
33 | 109-2.39 | Indoor Lighting Fixtures. Removed entire section | Removed subsection to reduce redundant information. Relocated relevant information from 109-2.39 into 109-2.7. Equipment installed in typical GA airport system installation. | Need in justification why this section is needed. | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-26
34 | 109-2.41 | (Now Section 109-2.36) Exhaust Fan. Added subsection | Added exhaust fan for ventilation of enclosure. Equipment installed in typical GA airport system installation. | Need in justification why this section is needed. | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-26
35 | 109-3.14 | Cable Entrance System Removed high voltage bus system and references to high voltage service and potheads. | Equipment already removed from other parts of specification. |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | jsc / vjg | 2019-02-26
36 | 109-3.15 | Wiring and Connections. References to L-108 added for installation and testing. |  |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-26
37 | 109-3.16b. | Marking and Labeling. Revised subsection | Revised labels from stenciled paint to engraved plastic. |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-26
38 | 109-4.3 | Method of Measurement Added wording to make removal of enclosures subsidiary to installation of new. |  |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-26
39 | 109-4.4 | Method of Measurement Added wording to make removal of equipment subsidiary to installation of new. |  |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-26
40 | 109-5.2 | Basis of Payment 1. Added paragraph, "Lighting regulators are paid for under section L-100." 2. Revised to AASHTOWare pay item numbers | 1. Revised for clarity and consistency. 2. Updated pay items to align with AASHTOWare. |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-26
L-110: AIRPORT UNDERGROUND ELECTRICAL DUCT BANKS AND CONDUITS
1 |  | Spec Title Revised title | Updated for 10H conformance. |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-26
2 | 110-1.1 | Description. Replaced "steel drag wires" with "pull ropes" and add the last sentence. | Revised for clarity and more information. Removal option language relocated to more closely match 10H. |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-26
3 | 110-2.1 |  | b-e addressed in GCP 10, 20, 60 | Why 10G para b, c, d and e omitted? | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-26
4 | 110-2.2 | Bituminous Fiber Duct. Removed entire subsection | Obsolete material, not included in 10H. Numbers revised. | Para numbers should match 10G 2.2 Steel Conduit, 2.3 Plastic Conduit etc. | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-26
5 | 110-2.3 | Asbestos Cement Duct. Removed entire subsection | Obsolete material, not included in 10G. |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-26
6 | 110-2.6b. | (Now Section 2.3) Plastic Conduit. Removed "elbows" after "saddle fittings," and added last sentence. | Revised to provide additional requirements for HDPE fittings. Added UL reference for HDPE. |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | jsc /vjg | 2019-02-26
7 | 110-2.7 | (Now Section 110-2.5) Liquidtight Flexible Metal Conduit. | LFMC used for equipment and building connections from underground. | Why is FMC required? | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | jsc /vjg | 2019-02-26
8 | 110-2.8 | (Now 110-2.7) Marker Tape. Added new subsection | Detectable marker tape was added because it was required by FAA for their conduits. 10G lists detectable only. May need further discussion with regions/FAA. |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-26
9 | 110-2.10 | (Now Section 110-2.8) Detectable Marker Tape. Added new subsection | Detectable marker tape was added because it was required by FAA for their conduits. 10G lists detectable only. May need further discussion with regions/FAA. |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-26
10 | 110-2.11 | (Now Section 110-2.9) Electrical Manholes. Added new subsection | Manholes are not utilized on enough Alaska projects to justify a dedicated spec section as included in 10G, so they have been added here on past projects where they are used. Included in this section on past projects as they are not included in other DOT specifications. | Why added? Not in 10G? | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-26
11 | 110-2.12 | (Now Section 110-2.10) Drywells. Added subsection and Table 1. Gradation of Drywell Drain Rock | Added requirements for drywells as they are used for drainage of conduit systems. Used for drainage of conduit systems. | Because? | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-26
12 | 110-3.1 | General. Revised subsection | Revised Teflon tape to conductive sealant to ensure electrical continuity of conduit joints. Revised pull wire to pull rope to be consistent with general practice. Clarified concrete envelope applies to areas subject to aircraft traffic, as conduits are not always concrete encased under non-aircraft paved areas. Added duct spacer language to match 10H. Marker tape language relocated from 110-3.6 to match 10H. | Need discuss what was changed and why | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-26
13 | 110-3.2 | Ducts Encased in Concrete. Removed last two paragraphs in the subsection | Obsolete materials, not included in 10H. "Duct banks" infers multiple ducts routed together, however, this section is also used to define the requirements for single ducts/conduits with concrete encasement. | Why the title change? | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-26
14 | 110-3.3 | Ducts Without Concrete Encasement. Replaced "PE" with "HDPE" | PE revised to HDPE for consistency. May need further discussion to recommend just standardiziing HDPE throughout. Duct and conduit used interchangably. | Why the title change | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-26
15 | 110-3.4 | PVC Conduit. Removed last paragraph | Delete repeated paragraph from subsection 110-3.1 General. Recommend leaving conduit-type-specific requirements adjacent to general conduit installation requirements to help ensure application of both. | Keep section numbers to match 10G. Add this at the end if a section on PVC | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-26
16 | 110-3.5 | HDPE Conduit. Revised 1st paragraph and added last two paragraphs | Revised to add HDPE-specific installation requirements. Recommend leaving conduit-type-specific requirements adjacent to general conduit installation requirements to help ensure application of both. | Keep section numbers to match 10G. Add this at the end if a section on HDPE | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-26
17 | 110-3.8 | Restoration. Added Turfing specs reference, "(T-901, T-903, T-904, T-905, T-908, T-920)" | Added Turfing specs for clarity and more information. Recommend leaving in section 3.8, so logical progression of construction from Backfilling to Restoration. Order in specs follows logical progression. | similar to above comment | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-26
18 | 110-3.9 | Drywells. Added new subsection | Added requirements for drywells as they are used for drainage of conduit systems. | similar to above comment | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-26
19 | 110-4.2 | Method of Measurement Added subsection 110-4.2 | New subsection number added for consistency in numbering. |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-26
20 | 110-4.3 | Method of Measurement Added subsection 110-4.3 | New subsection added for payment of manhole and drywell items |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-26
21 | 110-5.1 | Basis of Payment Revised subsection as well as updated pay items to AASHTOWare | Revised 1st paragraph and added two paragraphs, as well as, updated pay items to align with AASHTOWare. |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-26
22 | 110-5.1 | Material Requirements Added "UL Standard 651" and "UL Standard 651A, and removed "Fed. Spec. W-C-571" and "UL Standard 543" | Revised for clarity |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | jsc / vjg | 2019-02-26
L-119: AIRPORT OBSTRUCTION LIGHTS
1 |  | Spec Title Revised title | Updated for 10H conformance. |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-27
2 | 119-1.1 | Description Revised 2nd paragraph | Insulating changed to isolation throughout to correct previous incorrect term. |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-27
3 | 119-2.1 | 1. Revised last sentence of 119-2.1a regarding internet link. 2. Removed c-f | 1. Updated internet link and title. 2. c-f addressed in GCP 10, 20, 60 | Recommend deleting Office name and website for AC as these change periodically. Use 10G para a. Why deletion of para c, d, e and f? | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-27
4 | 119-2.3 | Insulating Transformers. Replaced "Insulation" with "Isolation" in title and in subsection | Insulating changed to isolation throughout to correct previous incorrect term. |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-27
5 | 119-2.5 | Added plastic conduit language | Language is scaled-back version of 10H section. |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | jsc /vjg | 2019-02-27
6 | 119-2.6 | Plastic Conduit (For Use Below Grade Only). Revised subsection | Title and section match 10H. | Need to propose something and justify. Why was plastic conduit para omitted? Why was title changed from Electrical Wire and Cable to Wires? | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | jsc / vjg | 2019-02-27
| 119-2.7 | Renamed to Electrical Wire and Cable | Title matches 10H. Removed material requirements for 5000V cable to allow Type B or C cable and just refer to L-824 requirements. Revised 600V cable to "thermoset" and "XHHW-2" for low temperature applications in Alaska and to be consistent with 10H. |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | jsc / vjg | 2019-02-27
7 | 119-3.5 | Series Insulating Transformers Replaced "Insulation" with "Isolation" in title and in subsection | Insulating changed to isolation throughout to correct previous incorrect term. Matches 10H. Added "If it is designed for use in a series lighting circuit" to match 10H. |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-27
8 | 119-3.6 | Wiring. Removed "under paved areas" and "and paid for under" in subsection | a) Removed "under paved areas" to apply L-108 and L-110 to all conduits, not just paved areas. b) Removed "and paid for under" to allow project specific flexibility in how conduit and cable are paid for. |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-27
9 | 119-3.7c. | Lamps Added subsection (c.) | LED light source added. This section is often included in projects by request because there is an obstruction light on the wind cone. By default, the obstruction light on an LED wind cone will be LED. Left LED in spec, but added note to designer that LED obstruction lights are not AIP eligible. | EB-98 includes requirements for LED obstruction lights, however, LED Obstruction lights are not currently AIP eligible. Remove reference to LED obstruction lights | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-27
10 | 119-5.1 | Basis of Payment Added 2nd sentence and updated pay item numbers | Added to allow obstruction lights to be subsidiary to other work if desired, and updated pay items to align with AASHTOWare (AWP). Removed L119.020.0000. | Remove reference to "Warning Light System, Road - per lump sum" | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-27
11 | 119-5.1 | Material Requirements. -Added "UL Standard 6", "UL Standard 514", "UL Standard 1242", UL 651 and 651A | Added for clarity |  | WAS-KE concurs | LPS-STANTEC concurs | DH-MBA concurs | DOT concurs | vjg | 2019-02-27
L-125: INSTALLATION OF AIRPORT LIGHTING SYSTEMS
1 |  | Renumbered L-100 to L-125, revised title, added language from 10H | Updated for 10H conformance.
2 | 125-1.1 | Added 2nd sentence (from 10H) | Updated for 10H conformance.
3 | 125-2.1 | Added language to allow electronic submittals | Updated for 10H conformance and industry standards.
4 | 125-2.1a | 1. Added 3rd and 4th sentences (from 10H) 2. Revised last sentence of 125-2.1a regarding internet link | 1. Updated for 10H conformance. 2. Updated internet link and title.
5 | 125-3.1 | Added fourth sentence in second paragraph (from 10H) | Updated for 10H conformance.
6 | 125-3.3 | Added second paragraph (from 10H) | Updated for 10H conformance.
7 | 125-3.5 | Added section (from 10H) | Updated for 10H conformance.
8 | 125-3.6 | Added section (from 10H) | Updated for 10H conformance.
9 | 125-3.9 | Added second and third sententences (from 10H) | Updated for 10H conformance.
10 | 125-5.2 | Added second sentence (from 10H) | Updated for 10H conformance.
L-130: SURFACE SENSORS
1 | 130-1.1 | 1. Added last three sentences in first paragraph. 2. Revised language in last paragraph. | Updated for clarity and consistency with 10H and State Accepted Specifications.
2 | 130 - Section 2 | Changed title to "EQUIPMENT AND MATERIALS" | Updated for 10H conformance.
3 | 130-2.1 | Added GENERAL paragraph. | Updated for clarity and consistency with 10H and State Accepted Specifications.
4 | 130-2.2 | Added ELECTRICAL paragraph. | Updated for clarity and consistency with 10H and State Accepted Specifications.
5 | 130-2.3 | Added CONCRETE paragraph. | Updated for clarity and consistency with 10H and State Accepted Specifications.
6 | 130-2.4f | Changed "L-100" to "L-125" and added section titles | Updated for clarity and consistency with 10H and State Accepted Specifications.
7 | 130 - Section 3 | Changed title to "CONSTRUCTION METHODS" | Updated for 10H conformance.
8 | 130-3.1 | Added third paragraph (moved from "TESTING" paragraph) | This paragraph is more consistent with "CONSTRUCTION METHODS" than "TESTING".
9 | 130-3.1 | 1. Changed "first lift of asphalt" to "first lift of Type V asphalt". 2. Fourth paragraph: Changed "L-100" to "L-125" and added section titles | 1. Updated to better describe the installation method. 2. Updated for clarity and consistency with 10H and State Accepted Specifications.
10 | 130-3.2 | 1. Deleted the first sentence. 2. Added last two sentences. | Updated for clarity.
11 | 130-3.4 | Added GUARANTEE paragraph. | Updated for clarity and consistency with 10H and State Accepted Specifications.
12 | 130-5.1 | Added "Payment will be made at" and "removal and disposal of existing system components". | Updated for clarity and consistency with 10H and State Accepted Specifications.
13 | 130-5.1 | Added paragraphs noting that P-610, L-110, L-108, and L-125 items are subsidiary to L-130. | Updated for clarity and consistency with 10H and State Accepted Specifications.
L-132: APPRAOCH LIGHTING AIDS
1 | 132-1.1 | Revised first paragraph to include a better description of the work. | Updated for clarity and consistency with 10H and State Accepted Specifications.
2 | 132 - Section 2 | Changed title to "EQUIPMENT AND MATERIALS" | Updated for 10H conformance.
3 | 132-2.1 | Added GENERAL paragraph. | Updated for clarity and consistency with 10H and State Accepted Specifications.
4 | 132-2.2 | Added ELECTRICAL paragraph. | Updated for clarity and consistency with 10H and State Accepted Specifications.
5 | 132-2.3 | Added CONCRETE paragraph. | Updated for clarity and consistency with 10H and State Accepted Specifications.
6 | 132 - Section 3 | Changed title to "CONSTRUCTION METHODS" | Updated for 10H conformance.
7 | 132-3.2 | 1. Incorporated the "TESTING" title into 132-3.2. 2. Added insulation resistance testing. 3. revised language for final testing. | 1. Revised for clarity and consistency with 10H and State Accepted Specifications. 2. Updated to add insulation resistance testing. 3. Revised for clarity .
8 | 132-3.3 | Added GUARANTEE paragraph. | Updated for clarity and consistency with 10H and State Accepted Specifications.
9 | 132-3.2 | Renumbered from 4.1 to 3.2 | Updated for clarity and consistency with 10H and State Accepted Specifications.
10 | 132-4.1 | Renumbered from 5.1 to 4.1 | Updated for clarity and consistency with 10H and State Accepted Specifications.
11 | 132-5.1 | Renumbered from 6.1 to 5.1 | Updated for clarity and consistency with 10H and State Accepted Specifications.
12 | 132-5.1 | Added detailed description of payment. | Updated for clarity and consistency with 10H and State Accepted Specifications.
13 | 132-5.1 | Added paragraphs noting that P-610, L-108, and L-110 items are subsidiary to L-130. | Updated for clarity and consistency with 10H and State Accepted Specifications.
L-135: FAA EQUIPMENT
1 | 135-1.1 | Revised first paragraph to include a better description of the work. | Updated for clarity and consistency with 10H and State Accepted Specifications.
2 | 135 - Section 2 | Changed title to "EQUIPMENT AND MATERIALS" | Updated for 10H conformance.
3 | 135-2.1 | Added GENERAL paragraph. | Updated for clarity and consistency with 10H and State Accepted Specifications.
4 | 135-2.2 | Revised ELECTRICAL paragraph. | Updated for clarity and consistency with 10H and State Accepted Specifications.
5 | 135-2.4 | Added CONCRETE paragraph. | Updated for clarity and consistency with 10H and State Accepted Specifications.
6 | 135 - Section 3 | Changed title to "CONSTRUCTION METHODS" | Updated for 10H conformance.
7 | 135-3.7 | Added TESTING paragraph. | Updated for clarity and consistency with 10H and State Accepted Specifications.
8 | 135-3.8 | Added GUARANTEE paragraph. | Updated for clarity and consistency with 10H and State Accepted Specifications.
9 | 135-5.1 | Added detailed description of payment. | Updated for clarity and consistency with 10H and State Accepted Specifications.
10 | 135-5.1 | Added paragraphs noting that P-610, L-108, L-110, and L-125 items are subsidiary to L-130. | Updated for clarity and consistency with 10H and State Accepted Specifications.
L-145: STANDBY GENERATOR AND ENCLOSURE
1 | 145 - Section 2 | Changed title to "EQUIPMENT AND MATERIALS" | Updated for 10H conformance.
2 | 145-2.1 | Added GENERAL paragraph. | Updated for clarity and consistency with 10H and State Accepted Specifications.
3 | 145-2.2 | Revised ELECTRICAL paragraph. | Updated for clarity and consistency with 10H and State Accepted Specifications.
4 | 145-2.3 | Added CONCRETE paragraph. | Updated for clarity and consistency with 10H and State Accepted Specifications.
5 | 145-2.4 | Renumbered from 145-2.1 | Renumbered to allow insertion of 145-2.1, 145-2.2, and 145-2.3.
6 | 145 - Section 3 | Changed title to "CONSTRUCTION METHODS" | Updated for 10H conformance.
7 | 145-3.2 | Added GUARANTEE paragraph. | Updated for clarity and consistency with 10H and State Accepted Specifications.
8 | 145-4.1 | Revised to "This item will not be measured for payment" | Updated for clarity and consistency with 10H and State Accepted Specifications.
9 | 145-5.1 | Added detailed description of payment. | Updated for clarity and consistency with 10H and State Accepted Specifications.
10 | 145-5.1 | Added paragraphs noting that P-610, L-108, L-110, and L-125 items are subsidiary to L-130. | Updated for clarity and consistency with 10H and State Accepted Specifications.
L-150: WEATHERPROOF OUTLETS
1 | 150-1.1 | Revised first paragraph to include a better description of the work. | Updated for clarity and consistency with 10H and State Accepted Specifications.
2 | 150 - Section 2 | Changed title to "EQUIPMENT AND MATERIALS" | Updated for 10H conformance.
3 | 150-2.1 | Added GENERAL paragraph. | Updated for clarity and consistency with 10H and State Accepted Specifications.
4 | 150-2.2 | Revised ELECTRICAL paragraph. | Updated for clarity and consistency with 10H and State Accepted Specifications.
5 | 150-2.3 | Added CONCRETE paragraph. | Updated for clarity and consistency with 10H and State Accepted Specifications.
6 | 150-2.4 | Renumbered from 150-2.1 | Renumbered to allow insertion of 150-2.1, 150-2.2, and 150-2.3.
7 | 150 - Section 3 | Changed title to "CONSTRUCTION METHODS" | Updated for 10H conformance.
8 | 150-3.1 | Seventh paragraph: Revised '2"-inch minus backfill' to '1"inch minus backfill' | Updated for consistency with State Accepted Specifications and industry standards.
9 | 150-3.2 | Added TESTING paragraph. | Updated for clarity and consistency with 10H and State Accepted Specifications.
10 | 150-3.3 | Added GUARANTEE paragraph. | Updated for clarity and consistency with 10H and State Accepted Specifications.
11 | 150-4.1 | Revised to "This item will not be measured for payment" | Updated for clarity and consistency with 10H and State Accepted Specifications.
12 | 150-5.1 | Added detailed description of payment. | Updated for clarity and consistency with 10H and State Accepted Specifications.
13 | 150-5.1 | Added paragraphs noting that P-610, L-108, L-110, and L-125 items are subsidiary to L-130. | Updated for clarity and consistency with 10H and State Accepted Specifications.
L-155: FLOOD LIGHTING
1 | 155-1.1 | Revised first paragraph to include a better description of the work. | Updated for clarity and consistency with 10H and State Accepted Specifications.
2 | 155 - Section 2 | Changed title to "EQUIPMENT AND MATERIALS" | Updated for 10H conformance.
3 | 155-2.1 | Added GENERAL paragraph. | Updated for clarity and consistency with 10H and State Accepted Specifications.
4 | 155-2.2 | Revised ELECTRICAL paragraph. | Updated for clarity and consistency with 10H and State Accepted Specifications.
5 | 155-2.3 | Added CONCRETE paragraph. | Updated for clarity and consistency with 10H and State Accepted Specifications.
6 | 155-2.4 | Renumbered from 155-2.1 | Renumbered to allow insertion of 155-2.1, 155-2.2, and 155-2.3.
7 | 155 - Section 3 | Changed title to "CONSTRUCTION METHODS" | Updated for 10H conformance.
8 | 155-3.1 | Fifth paragraph: Revised '2"-inch minus backfill' to '1"inch minus backfill' | Updated for consistency with State Accepted Specifications and industry standards.
9 | 155-3.2 | Added TESTING paragraph. | Updated for clarity and consistency with 10H and State Accepted Specifications.
10 | 155-3.3 | Added GUARANTEE paragraph. | Updated for clarity and consistency with 10H and State Accepted Specifications.
11 | 155-4.1 | Revised to "This item will not be measured for payment" | Updated for clarity and consistency with 10H and State Accepted Specifications.
12 | 155-5.1 | Added detailed description of payment. | Updated for clarity and consistency with 10H and State Accepted Specifications.
13 | 155-5.1 | Added paragraphs noting that P-610, L-108, L-110, and L-125 items are subsidiary to L-130. | Updated for clarity and consistency with 10H and State Accepted Specifications.
L-160: ELECTRICAL LOAD CENTERS
1 | 160-1.1 | Revised first paragraph to include a better description of the work. | Updated for clarity and consistency with 10H and State Accepted Specifications.
2 | 160 - Section 2 | Changed title to "EQUIPMENT AND MATERIALS" | Updated for 10H conformance.
3 | 160-2.1 | Added GENERAL paragraph. | Updated for clarity and consistency with 10H and State Accepted Specifications.
4 | 160-2.2 | Revised ELECTRICAL paragraph. | Updated for clarity and consistency with 10H and State Accepted Specifications.
5 | 160-2.3 | Added CONCRETE paragraph. | Updated for clarity and consistency with 10H and State Accepted Specifications.
6 | 160-2.4 | Renumbered from 160-2.1 | Renumbered to allow insertion of 160-2.1, 160-2.2, and 160-2.3.
7 | 160 - Section 3 | Changed title to "CONSTRUCTION METHODS" | Updated for 10H conformance.
8 | 160-3.1 | Fifth paragraph: Revised '2"-inch minus backfill' to '1"inch minus backfill' | Updated for consistency with State Accepted Specifications and industry standards.
9 | 160-3.2 | Added TESTING paragraph. | Updated for clarity and consistency with 10H and State Accepted Specifications.
10 | 160-3.3 | Added GUARANTEE paragraph. | Updated for clarity and consistency with 10H and State Accepted Specifications.
11 | 160-5.1 | Added detailed description of payment. | Updated for clarity and consistency with 10H and State Accepted Specifications.
12 | 160-5.1 | Added paragraphs noting that P-610, L-108, L-110, and L-125 items are subsidiary to L-130. | Updated for clarity and consistency with 10H and State Accepted Specifications.
L-161: ELECTRICAL METER CENTERS
1 | 161-1.1 | Revised first paragraph to include a better description of the work. | Updated for clarity and consistency with 10H and State Accepted Specifications.
2 | 161 - Section 2 | Changed title to "EQUIPMENT AND MATERIALS" | Updated for 10H conformance.
3 | 161-2.1 | Added GENERAL paragraph. | Updated for clarity and consistency with 10H and State Accepted Specifications.
4 | 161-2.2 | Revised ELECTRICAL paragraph. | Updated for clarity and consistency with 10H and State Accepted Specifications.
5 | 161-2.3 | Added CONCRETE paragraph. | Updated for clarity and consistency with 10H and State Accepted Specifications.
6 | 161-2.4 | Renumbered from 161-2.1 | Renumbered to allow insertion of 161-2.1, 161-2.2, and 161-2.3.
7 | 161 - Section 3 | Changed title to "CONSTRUCTION METHODS" | Updated for 10H conformance.
8 | 161-3.2 | Added TESTING paragraph. | Updated for clarity and consistency with 10H and State Accepted Specifications.
9 | 161-3.3 | Added GUARANTEE paragraph. | Updated for clarity and consistency with 10H and State Accepted Specifications.
10 | 161-4.1 | Revised to "This item will not be measured for payment" | Updated for clarity and consistency with 10H and State Accepted Specifications.
11 | 161-5.1 | Added detailed description of payment. | Updated for clarity and consistency with 10H and State Accepted Specifications.
12 | 161-5.1 | Added paragraphs noting that P-610, L-108, L-110, and L-125 items are subsidiary to L-130. | Updated for clarity and consistency with 10H and State Accepted Specifications.