SECTION 661
ELECTRICAL LOAD CENTERS

Special Provisions

Section 661: C661.1	Related Sect/Sp: 550/C550.1; 660/C660.1; 662/C662; 667/C667; 669/; 708/C708.HSM20.31, 740/C740.1.HSM20.31

HSM20-31 incorporated into C661.1.

Apply to all projects with work related to Section 661 and load centers. C661.1 does not require C661.2. Include C661.3 and C550.1.C661.1.

661-2.01 MATERIALS.

Add the following:

Anchor Bolts	Subsection 740-2.02

Load Center.

Replace the 1st and 2nd paragraphs with the following two paragraphs:

NEMA 3R enclosure constructed of .125” thick aluminum, with no external screws, bolts, or nuts.

Shop coat cabinet components with a 2-part urethane paint undercoat and 2-part urethane finish coat. Finish coats must be standard white for removable panels and non-gloss silver-gray, closely matching AMS-STD-595 Color No. 36622, for the enclosure.

Equipment List(s) and Drawings.

Replace No. 1. with the following:

1.	Materials on the Qualified Products List:  The Qualified Products List does not apply to the 661 Pay Items.  Provide catalog cuts of materials to the Engineer for review and approval.

3.	Materials Not Requiring Certification:  Replace the 2nd sentence with the following:

Submit these materials for review and approval if included on the Materials Certification List (MCL) or requested by the Engineer.

Add the following materials:

Ground Rods.  Furnish one piece 3/4” diameter by 10 feet long copper clad steel rods.

Ground Rod Clamps.  Furnish one piece bronze clamps with a hex head setscrew that are suitable for direct burial and for use with copper clad ground rods.

Meters.  Furnish meter sockets and landing pads rated for 200 Ampere Service.

Photoelectric Controls.

Delete the first sentence and substitute the following:

Use three wire photoelectric controls that directly switch a circuit from one conductor to another.  Furnish two piece photoelectric controls that consist of a plug-in control unit and a locking type receptacle set in a cast aluminum adapter.

1.	Plug-in Control Unit.

Furnish photoelectric control units that consist of a light sensitive element connected directly to a normally closed, single-pole, single-throw, and control relay free of intermediate amplifications.  For highway lighting, use horizontal or zenith type sensing units that:

a.	Operate at voltages between 120 and 277 VAC, 60 Hz,

b.	Handle loads up to 1,800 volt-amperes,

c.	Operate at temperatures from -40 °F to +150 °F,

d.	Consumes less than 10 watts of power,

e.	Feature a 3-prong, EEI-NEMA standard, twist-lock plug,

f.	Turn-on between 1.0 and 5.0 foot-candles and turn-off at light levels between 1.5 and 5.0 times those at turn-on.

Measurements must meet the procedures in EEI-NEMA Standards for Physical and Electrical Interchangeability of Light-Sensitive Control Devices used in the Control of Roadway Lighting.

Screen the photoelectric control units to prevent artificial light from interfering with normal photoelectric control operation.  Extend screens to the top of the control units.  Use 3 inch wide x 0.063 inch thick (min) aluminum meeting ASTM B209, Alloy 3003-H14.

2.	Locking Receptacles.

Furnish twist lock type, phenolic resin receptacles set in one of the following cast-aluminum adapters.

a.	For photoelectric controls installed on signal poles and load centers, furnish a mounting adapter with a threaded connection that fits conduit outlet bodies threaded for 1/2 inch rigid metal conduit, General Electric model MB-PECTL or approved equal.

b.	For photoelectric controls installed atop lighting poles (with mast arms,) furnish a pole top adapter:  equipped with a terminal block, made to slip over the ends of poles 3 1/2 to 4 1/2 inches in outside diameter, and secured by set-screws, General Electric model PTA-PECTL or approved equal.

661-3.01 CONSTRUCTION REQUIREMENTS.

Replace the 11th paragraph with the following:

Install two ground rods at least 8 feet apart at each load center.  Connect the neutral bus to the ground rods with a soft drawn bare copper grounding electrode conductor sized per the NEC, 6 AWG minimum.  Bond non-current carrying metal parts in each load center to the ground bus.  At Type 1 load centers, install one ground rod inside the base, readily accessible though the removable cover, and the second ground rod outside the base.  Route the grounding electrode conductor to the second ground rod through one of the knockouts.

Replace the 12th paragraph with the following:

Install photoelectric controls at the locations indicated. Orient photoelectric control units to face the north sky.  Install a screen to prevent artificial light from interfering with normal photoelectric control operation.

For photoelectric controls installed on load centers, install a Myers hub in a cabinet wall shielded from traffic.  To the hub, attach an assembly that consists of a Type LB conduit body, a length of conduit, and a Type C conduit body.  Fabricate the conduit at least 3 ft long and locate the photoelectric control 1 ft above the top of the load center.  Mount the photoelectric control adapter on the Type C conduit body.  Install a conduit hanger to brace the top of the conduit.

For photoelectric controls installed on signal poles, install a Myers hub in the center of the rain cap.  Attach a Type C conduit body to the hub with a close nipple.  Mount the photoelectric control adapter on the conduit body.  Use five conductor 14 AWG wire to connect the photoelectric control to the load center.

For photoelectric controls installed on electroliers, install a pole top adapter.  When the photoelectric control is on a lighting standard with a slip base or frangible coupling style base, use an approved breakaway disconnect in the base of the light standard.  Restrain the cable in a similar manner as the illumination cable in the pole base.  Use five conductor 14 AWG wire to connect the photoelectric control to the load center.

Add the following:

Coordinate new load centers with existing and or new service utilities.

Failed Equipment and Workmanship

For the term of the Contract from initial equipment installation through final acceptance, Subsection 105-1.16, when directed, promptly replace failed equipment, equipment components and repair failed workmanship.

661-5.01 BASIS OF PAYMENT.

Add the following:

The following work is subsidiary to 661 Pay Items:

	All necessary hardware for mounting (shelf angles, rack, shelving, harness, etc.).

	Removing existing load centers being replaced with new load centers, their foundations, and ground rods.

	Payment of fees required by the local authority for electrical inspection(s) and the costs of correcting the deficiencies noted during the inspection(s).

	All work including, but not limited to, contacting and coordinating with the utilities for service; maintenance and usage payments until the Engineer provides the notice of final acceptance.

	Replaced failed equipment, equipment components and repaired failed workmanship.

C661.1-21.1231-2