SECTION 661
ELECTRICAL LOAD CENTERS

Special Provisions

Sect 661: C661.2	Related Sect/Sp: 550/C550.1; 660/C660.1; 662/C662; 667/C667; 669/; 740/C740.1.2.3

C661.2 - when a load center requires an uninterruptable power supply (UPS), add C661.2, C661.1, C661.3, and C550.1.

661-1.01 DESCRIPTION.

Add the following:

Furnish and install load center assembly Type 1A with an integral uninterruptible power supply (secondary power source) to power intersection traffic and pedestrian signals (no lighting) and control equipment during interruptions to the utility power (primary power source).

Add the following load center type:

Type 1A with UPS:	Pad mounted with underground service (large)

Add the following Subsections 661-1.02 Acronyms, 661-1.03 Definitions:

661-1.02 ACRONYMS.

BBS	Battery Backup System

LC	Load Center

LCD	Liquid Crystal Display

LED	Light Emitting Diode

LC/UPS	Load Center with Integral Uninterruptible Power Supply

MBPS	Manual Bypass Switch

MMU	Malfunction Management Unit

PLC	Powerline Communications

PTS	Power Transfer Switch

THD	Total Harmonic Distortion

UPS	Uninterruptible Power Supply

661-1.03 DEFINITIONS.

BUCK-BOOST.  Switch-mode voltage regulator in which voltage can be above or below the input voltage.

661-2.01 MATERIALS.

Add the following:

1.	Load Center with Integral Uninterruptible Power Supply (LC/UPS).

Design, fabricate, deliver, and install as specified in the Specifications and Plans.

a.	Design of LC/UPS

Design and manufacture for outdoor applications and the environment specific to the project location.

The UPS shall be designed to provide for efficient fabrication and assembly using standard, readily available industry components facilitating the current project requirements.  The design shall provide for future quick replacement of the complete system or the individual components.  The design shall allow the maintenance department to quickly acquire a replacement UPS or replacement parts and personnel to easily remove the existing UPS and install the new UPS or UPS parts as may be needed (complete turnkey system with all necessary hardware).  Special tools shall not be required to install the UPS.

The design shall specifically include a shelf-mount, rack-mount, swing-tray mount, or combination thereof.  The UPS and PTS units individually shall not exceed 5.25” in height.  If swing-trays are used, a minimum of 6 bolts/fasteners shall be used to secure the tray to the cabinet rack.

b.	Submit.

Submit shop drawings, equipment technical specifications, and certifications for review and approval.  Do not begin manufacture of the LC/UPS prior to submitting and receiving approval of shop drawings and required certifications for the system assembly, the individual equipment pieces, components, and hardware.  Provide documentation confirming delivery dates of the individual pieces of equipment and overall system in-place completion date satisfying the project construction schedule.

c.	Manufacturers.

(1)	Meyers Power Products, Inc.

LC/UPS:  Power Model MEUG35-PB Metered/Unmetered with MP2000 UPS

Address:

2950 E Philadelphia Street

Ontario, CA 91761

Ph: (909) 923-1800 or (866) 696-9377

(2)	Or equal:

Manufacturers satisfying the requirements of the Plans, Specifications and Contractual requirements for the assembled system, including delivery, quality and timeliness of installation and responsive remote and onsite service, shall submit, as a substitution, for review and approval.

d.	UPS Run Time Capacity.

Power intersection LED traffic, pedestrian signals, and control equipment for the consecutive time periods noted below: (lighting and traffic controller auxiliary circuits are not included)

TABLE 661-2.01-1

RUN TIME CAPACITY

| Operation Mode | Continuous Uninterruptible Operation Time* |
| --- | --- |
| Normal | 2 Hours |
| Flash | 2 Hours |
| Total (Normal + Flash) | 4 hours |

*Continuous uninterruptible operation time at 77°F (25°C) at load 875 W.

e.	Operation.

The transfer from utility power to the UPS shall not interfere with the normal operation of the traffic controller, MMU and other peripheral devices within the traffic controller assembly.

The MBPS shall be rated at 240 VAC, 40 Amps minimum.  The MBPS shall allow replacement of the UPS without interrupting power to the intersection. The MBPS and PTS shall be separate units.  Without interrupting power to the intersection, the MBPS shall permit the replacement of the PTS, and the MBPS and PTS shall each permit replacement of the UPS.

The UPS shall use a temperature compensated battery charging system. The charging system shall compensate over a range of 2.5 to 4 mV / °C / Cell and be rated 10 Amps at 48 VDC. Batteries shall not be charged when battery temperature exceeds 122 °F ± 5.4 °F (50 °C ± 3 °C). The temperature sensor shall be external to the UPS unit and supplied with 9' - 10" of wire.

The UPS shall automatically and continually monitor and display the current percent of battery power available for use.  A "Battery Not Connected" alarm shall be issued if battery power is not present. When utilizing battery power, the UPS output voltage shall be between 110 VAC and 125 VAC, pure sine wave output with THD < 3% at 60 Hz +/- 3 Hz.

The UPS shall provide adequate power capacity to supply an external fan with field programmable temperature setting capability located in the same or in a separate battery cabinet. The temperature setting shall be adjustable locally and remotely.  The temperature range shall be from +68 °F to +131 °F (+20 °C to +55 °C) in 1 degree F increment.

In the event of UPS failure, battery failure, or complete battery discharge, the PTS shall revert to the utility or line mode (in a de-energized state) where utility power is supplying the cabinet.

f.	Components:

The LC/UPS shall include all equipment, hardware, foundation and foundation materials, interconnecting wiring and other materials for a complete operable LC/UPS inclusive of materials and performance requirements specified herein, but not limited to:

(1)	UPS

(2)	UPS Controller Unit

(a)	Re-settable Inverter Event Counter

(b)	Cumulative Inverter Timer

(c)	Event log, Time and Dated (stores the last 100 events, minimum)

(d)	Self-Test (programmable in 1-minute increments from 1 min. to 255 min.)

(e)	Low Battery Alarm (programmable, adjustable in increments of .25 VDC)

(f)	Buck-Boost Mode (UPS shall be capable of Buck-Boost 10% ±)

(3)	PTS (activated during Buck-Boost operations; transfer times 10 milliseconds)

(4)	MBPS (non-electrical)

(5)	Batteries and Battery Enclosure

(6)	Battery Heater Mats

(7)	Cabinets and Enclosures

(8)	External Fan

g.	UPS Access and Password Protection.

	Provide local and remote access.

	Provide the UPS with a default password.

Access:

(1)	Local – provide an LCD display screen and touch pad as part of the UPS

(2)	Remote

(a)	RS232 interface

(b)	USB interface

Local and remote access shall provide same access use.

User:

(1)	The “User” includes the Department Traffic Engineers and Maintenance Personnel.

(2)	The User shall be able to monitor the following at the LC/UPS cabinet (locally) and remotely.

Use:

(1)	Provide the Department with the default password and administrative authority to add/change password protection.  Make the procedure intuitive and direct.

(2)	Control, programming, maintenance, and inquiry (view and adjust) including but not limited to:

Monitor:

(a)	Time,

(b)	Date,

(c)	Current battery charge status,

(d)	Input/output voltages,

(e)	Power output,

(f)	Battery temperature,

(g)	Field programmable relay settings

Current status shall be indicated by LED lights:

(a)	Green – Flashing for battery back-up mode

(b)	Green – Steady ON for normal line mode operation

(c)	Red – Flashing for ALARM conditions

(d)	Red – Steady ON for FAULT conditions

Maintenance Controls - password protect:

(a)	UPS Inverter ON/OF,

(b)	Battery Test,

(c)	Event Log (Retrieving, viewing and printing in plain English),

(d)	Changing Default Settings

Other Settings:

(a)	Temperature Settings,

(b)	Re-Settable Inverter Event Counter,

(c)	Cumulative Inverter Timer,

(d)	Self-Test,

(e)	Low Battery Alarm

(3)	Upload firmware software updates of the non-volatile, read-only memory type.

h.	Specifications.

(1)	Environmental:

The operating temperature for the (UPS), (PTS) and (MBPS) shall be -34.6 °F to 165.2 °F

(-37 °C to +74 °C).

(2)	UPS Input/Output:

TABLE 662-2.01-2

UPS SPECIFICATIONS

| Input Specifications |  |
| --- | --- |
| Nominal Input Voltage | 120 VAC, Single Phase |
| Input Voltage Range | 120 VAC ± 25% |
| Input Frequency | 60 Hz ± 5% |
| Output Specifications |  |
| Nominal Output Voltage | 120 VAC, Single Phase |
| Power Rating* | 2000 VA, (1500 Watts) |
| Output Frequency | 69 Hz ± 5% |
| Voltage Wave Form | Sine Wave, THD < 3% |
| Efficiency (nominal) | 95 – 97% |

*The UPS power rating of 2000 VA / 1500 Watts shall be with a minimum inverter efficiency of 80%.

(3)	Loss/Restoration of Utility Power:

When the utility line voltage is outside the High and Low Limits (100 & 130 VAC respectively set as defaults), the UPS shall transfer the load to battery power. The UPS shall return to line mode when the utility power has been restored to above 105 VAC or below 125 VAC; or the UPS shall return to line mode when the utility power is back to nominal for more than 30 seconds (the line qualification time).  The line qualification time shall be adjustable to 3, 10 or 30 seconds.

The maximum transfer time allowed, from disruption of normal utility line voltage to stabilized UPS line voltage from batteries, shall be 65 milliseconds. The same maximum allowable transfer time shall also apply when switching from UPS line voltage to utility line voltage.

(4)	Battery(s):

(a)	Batteries as part of the UPS provide the power.

Individual batteries shall be rated at 105 Amp-Hour minimum. Batteries shall be 12 VDC type and shall be easily replaced and commercially available off the shelf. The battery system used in the UPS shall consist of 4 batteries and shall be of a voltage not to exceed 60 VDC. Batteries shall be provided with quick disconnect terminals and a polarized - keyed battery cable for easy field installation.

Batteries shall be deep cycle, sealed prismatic lead-calcium based AGM/VRLA (Absorbed Glass Mat/Valve Regulated Lead Acid) batteries - able to withstand extreme temperature. Batteries shall be certified to operate over a temperature range of -4 °F to 165.2 °F (-20 °C to +74 °C).  The batteries shall be provided with appropriate interconnect wiring and a corrosion-resistant stationary or swing-out mounting tray and/or brackets appropriate for the cabinet into which they will be installed as specified in “Design of LC/UPS”.

Batteries shall indicate maximum recharge data and recharging cycles. Recharge time for the battery from protective low cutoff to 80% or more of full battery charge capacity, shall not exceed twenty (20) hours.

(b)	Battery Compartment:

The battery cabinet shall be vented through the use of louvered vents, filter, and one thermostatically controlled fan operated from the UPS. The fan will automatically turn ON at the temperature programmed into the UPS.

External battery compartments may be used to satisfy environmental and physical requirements.  When submitting shop drawings, material and equipment submittals, request in writing and demonstrate graphically the need for an external compartment(s).

(c)	Back-Feed and Other Protections:

The UPS shall be equipped to prevent a malfunction feedback to the cabinet or from feeding back to the utility service per UL 1778, Section 48 "Back-Feed Protection Test". The upstream back-feed voltage from the UPS shall be less than 1 VAC for the protection of persons accessing the equipment.

The UPS shall have lightning surge protection compliant with IEEE/ANSI C.62.41 for 2000 VAC.

(5)	Relay Contacts:

The UPS shall provide the user with 6 sets of fully programmable, relay contacts of type NO/NC, panel-mounted, potential free and rated 1 Amp, 120 VAC and labeled C1 through C6. Each relay's setting shall be programmable to activate under conditions through local access or remote access.  The minimum number of relay settings is outlined below.

Independently configure relay contacts C1 through C6 to activate under the following conditions:

(a)	ON BATTERY - relay activates when BBS switches to battery power.

(b)	LOW BATTERY - relay activates when batteries have reached a specified level of remaining useful capacity while on battery power. The specified level shall be adjustable from 0 to 100%.

(c)	TIMER- relay activates after being on battery power for a specified amount of time. The specified time shall be adjustable from 0 to 8 hours.

(d)	ALARM - relay activates after a specific or general alarm is detected. These alarm conditions include:

	Line frequency

	Low output voltage

	No temperature probe

	Overload

	Batteries not connected

	High temperature

	Low temperature

The relay shall be programmed to activate when any of these alarm conditions occur, or when a specified condition occurs.

(e)	FAULT- relay activates after a specific or general fault is detected. These fault conditions include:

	Short circuit

	Low battery voltage

	High battery voltage

	High internal temperature

	Overload

The relay shall be programmed to activate when any of these fault conditions occur, or when a specific condition occurs.

(f)	OFF- relay is disabled and shall not activate under any condition.

(6)	Default Relay Settings:

(a)	Relay C1 and C2 shall be set to activate whenever the UPS transfers to battery power and shall be labeled "ON BATT."

(b).	Relays C3 and C4 shall be set to activate whenever the batteries reach 40% of remaining useful capacity and shall be labeled "LOW BATT."

(c)	Relays C5 and C6 shall be set to activate whenever the UPS has been on battery power for 2 hours and shall be labeled "TIMER."

Terminal block position 19 & 20 shall be set to activate a self-test. This test confirms that a unit can transfer into and out of battery mode while supporting the output load.

(7)	Load Center for Temporary Power:

Use the following load centers for distribution of power for temporary lighting and signals including the control systems.  Provide work needed to modify load centers to provide functional temporary lighting and signal systems according to the NEC.

(a)	Permanent load centers installed in their plan location.

(b)	Existing load centers scheduled to remain intact until completion of the project.  Relocate and reuse existing load centers only if approved.

(c)	Approved temporary load centers with photoelectrical controlled lighting circuits.  Provide a temporary load center when retiring an existing load center that is not approved, and when approved load centers are unavailable.

Approved load centers include load centers UL labeled as Service Equipment, or UL labeled as Industrial Control Equipment and marked “Suitable for use as service equipment.”

661-5.01 BASIS OF PAYMENT.

Add the following Pay Item:

| PAY ITEM |  |  |
| --- | --- | --- |
| Item Number | Item Description | Unit |
| 661.2001.____ | Load Center, Type 1A with UPS (LC/UPS) | Each |

C661.2-20.0101