Special Provisions

Add the following Section:

SECTION 662
SIGNAL INTERCONNECT

662-1.01 DESCRIPTION.  This item consists of the work required to furnish and install signal interconnect in conduit between the controller assemblies shown on the Plans along the route indicated or on a route as directed by the Engineer.

Sect 662: C662	Related Sect/Sp:  550/C550.1; 660/C660.1; 661/C661.1.2; 667/C667; 669/; 740/C740, 740.1.2.3

Include C550.1 any time C662 is used.

662-1.02 REGULATIONS AND CODE.  Complete the work according to these Specifications and Section 660, Signals and Lighting.  The Department requires third party certification for high density polyethylene conduit.  Equal to or exceeding UL 651 B and NEMA TC-7.

662-2.01 MATERIALS.

Precast Concrete Products	Subsection 550-2.03

Submit the materials for review and approval according to the requirements of No 1. Equipment List and Drawings. of Subsection 660-2.01, Materials.

Furnish a 25 pair #19 telephone cable conforming to REA Specification PE-39 for the interconnect cable.  Install the interconnect cable in a 2 inch polyethylene conduit.

Encapsulate completed splices in waterproof reenterable type splice kits of the same type used for loop lead-in cable splices.  REA Bulletin 344-2 entitled "Lists of Materials Acceptable for use on Telephone Systems of REA Borrowers" provides a list of acceptable splice materials.

662-2.02 POLYETHYLENE DUCT SYSTEM.  Install a polyethylene duct system in which to pull the interconnect cable.  The Department will not permit the installation of the polyethylene conduit in a plowed trench.

Furnish a Type III polyethylene duct made from extra high molecular weight, high density, polyethylene (PE) pipe, with a cell classification equal to or exceeding 335444C when tested according to ASTM D 3350.

Furnish fittings used in the duct system, such as elbows, made from the same type polyethylene as the duct.  Fuse connections using the manufacturer’s recommended procedure and equipment.  Except elbows weeping into junction boxes shall be rigid metal conduit.  Join the rigid metal conduit to the HDPE with Electrofusion Type Coupler.

Keep junction boxes and ends of conduit covered unless pulling conductors.

Mark underground conduits with a continuous strip of polyethylene marker taped.  Furnish marker tape with a black legend on a red background that is 4 mil thick and 6 inches wide.  Install the tape 6 inches below finished grade.

Use care during compaction operations to prevent damage to the junction boxes and conduits.  Remove and replace items damaged during the backfill and compaction operations at no additional cost to the Department.

After testing and installing the conductors, plug conduit openings with duct seal to prevent water from entering the duct system.

662-2.03 JUNCTION BOX.  Furnish precast, reinforced concrete junction boxes conforming to the sizes and details shown on the Plans.  Install junction box lids made of cast iron.

662-3.01 CONSTRUCTION REQUIREMENTS.  The signal interconnect consists of cable, conduit, junction boxes, other necessary hardware required to complete the item, cable splicing, and the termination of conductors on terminal blocks.

Install the polyethylene conduits at least 30 inches below finished grade.

Install junction boxes at abrupt changes in conduit alignment and on 300 foot maximum centers.  Angle points and curves with delta angles greater than 45 degrees constitute an abrupt change.  Install Type 1A junction boxes, except when splicing interconnect cables together.  Complete the interconnect cable splices in Type II or III junction boxes.  Complete the splices according to Rural Electrification Administration (REA) Specification PC-2 for splicing telephone cables.  The Contractor shall determine the locations for making signal interconnect splices.  The Engineer, however, will not allow splices to be made at low points in the terrain or the bottom of sag vertical curves.  Keep splices in the interconnect cable to an absolute minimum and get the splice locations approved by the Engineer beforehand.

Furnish the controller cabinets with terminal blocks for the interconnect cable.

662-3.02 EXCAVATING AND BACKFILLING.  Backfill the excavations according to Section 204.

The Engineer will not allow ripping or plowing for installation of conduit.  Backfill around the polyethylene conduit with a 6 inch lift of material free of rocks exceeding a 1 inch maximum dimension.

662-4.01 METHOD OF MEASUREMENT.  The Engineer will measure signal interconnect by the linear foot from the center of junction box to center of the next junction box, following the slopes of the existing ground.

662-5.01 BASIS OF PAYMENT.  The contract unit price paid per linear foot for signal interconnect constitutes full compensation for furnishing work required to complete the work specified.  Terminal blocks for the interconnect cable shall be paid under Item 660.0001.____ Traffic Signal System Complete.

Payment will be made under:

| PAY ITEM |  |  |
| --- | --- | --- |
| Item Number | Item Description | Unit |
| 662.2000.____ | Signal Interconnect | LF |

C662-21.0601