SECTION 740
SIGNALS AND LIGHTING MATERIALS

Sect 740: CR740.1.2.3.4.5

Related Sect/Sp:  660/CR660.1; 661/CR66.2.1, 662/CR662; 667/CR667; 668/CR668HTWR; 669/CR669ATR

Related Sect/Sp:

CR740.3. Primary CR special, edit to project.

Special Provisions

Replace Subsection 740-2.02 SIGNAL AND LIGHTING STRUCTURES with the following:

740-2.02 SIGNAL AND LIGHTING POLES.

1.	Design.  Design and fabricate highway lighting structures to conform to the 1994 Edition of AASHTO Standard Specifications for Structural Supports for Highway Signs, Luminaires and Traffic Signals with interim revisions and the highway lighting sheets in the Plans.  Use a wind speed of 100 mph with a gust factor of 1.3.  Design each electrolier to support a sign with an area of 16 square feet with its centroid located 14 ft above the pole base.

Design and fabricate traffic signal structures to the 2001 Edition of AASHTO Standard Specifications for Structural Supports for Highway Signs, Luminaires, and Traffic Signals with interim revisions and Central Region Traffic Signal Details.  Design must meet Fatigue Category III, with galloping using a basic wind speed of 100 mph and Central Region standard loads.

A registered professional engineer shall design the structures and provide stamped shop drawings and calculations.  Submit the stamped drawings and calculations for each pole to the Engineer for approval.  Design for the complete-in-place structure including the supported hardware.

a.	In the stamped calculations, indicate the edition of Standard Specifications to which the poles are being designed and provide the input data used to design each pole and mast arm, including:  design wind speed, cross section shape, yield strengths of the component materials, dimensions of the pole components, and a summary of the loads used.

b.	On the stamped shop drawings, provide design wind speed and the details for building the poles and mast arms, including:  materials specifications, slip fit joint dimensions, pole component dimensions, welds that will be made, and the welding inspection that will be done.

Submit the mill certifications for the steel items (piles, plates, bolts, and other related items) to the Engineer for approval.

2.	Fabrication.  Fabricate signal and lighting structures from tapered steel tubes with a round or 16 sided cross section.  Orient handholes located near the base of poles to face downstream of traffic flow.

Provide traffic signal poles, lighting poles, and signal mast arms in lengths evenly divisible by 5 feet.

Furnish poles and mast arms up to 40 feet long in one piece.  Poles and mast arms longer than 40 feet may be furnished in one piece or in two segments with a slip type field splice.  For slip type joints, provide a minimum overlap of two and one half (2.5) feet or the overlap specified in the Plans, whichever is greater.  In mast arms, locate these splices at least one foot away from the Plan location of signal heads and signs.  In signal poles, locate the edge of the female section at least 6 inches above the top of the signal mast arm connection.

Fabricate tubes with walls up to 1/2 inch thick from the prequalified base metals listed in AWS D1.1.  Fabricate elements greater than 1/2 inch thick from steel that conforms to AASHTO M270 and meets the Fracture Critical Impact Test requirements for Zone 3.  The Department will not accept structures that use laminated steel elements.

Fabricate the cross section of each tube from no more than 2 pieces of steel.  When using 2 pieces, place the longitudinal welded seams directly opposite one another.  Place the welded seams on adjacent sections to form continuous straight seams from the base to the top of the pole.

When tenons are needed to install traffic signals and luminaires, make them from two inch nominal schedule 40 pipe that conform to ASTM A 53 Grade B.

Fabricate breakaway signal poles in accordance with the Pole Sheet in the Plans. Fabricate signal poles 10 to 15 feet long from 7 gage (US Standard) sheet steel.  Fabricate each post with a minimum inside diameter at the base plate as shown in the Plans.  Use 4 inch diameter by 4 inch Schedule 40, ASTM A53, Grade B pipe as a post-top adapter.

The Department does not allow holes made for lifting purposes in the ends of tubular segments, except in the free ends of luminaire mast arms.  To add lift points, weld them to the tube opposite the longitudinal seam weld on the outside of female segments and on the inside of male segments.  Before shipment, remove lift points added to the outside of the tubes, grind the area smooth with the base metal, and hot stick repair the finish according to Subsection 660-3.01.8.a.  Lift points added to the inside of tubes in place may be left in place.

Hot-dip galvanize lighting and signal structures to meet AASHTO M 111 and these specifications. Galvanizing kettles will be large enough to completely submerge each element, the mast arm, and the pole.  Submerge the complete/whole element in the galvanizing process.  An element galvanized in sections will not be accepted.  Galvanize bolts and fasteners to meet AASHTO M 232.

After the poles and mast arms are galvanized, remove all excess zinc from all drip lines and points and the surfaces of all tube ends that form slip type joints to provide a smooth finish.

The Department will reject poles and mast arms that are:

(1).	Not fabricated according to these specifications or the approved shop drawings,

(2)	Bowed with sweeps exceeding 3/4 inch throughout the length of the pole, mast arm, or segment, if furnishing a 2 piece pole or mast arm,

(3)	Out of round.  Sections are out of round when the diameters of round members or the dimension across the flats of multisided members exceed 2 percent of the dimension specified on the shop drawings.

Fabricate pile cap adapters from Grade X42 steel line pipe that conforms to API 5L and from steel plate that conforms to ASTM A 709 Grade 50.  Attach the anchor plate to the pile section with a complete joint penetration (CJP) weld.  Fabricate the anchor plate to match the base plate of the lighting standard.

3.	Welding.  Perform welding to conform to Subsection 504-3.01.8. Welding and the 2001 Edition of AASHTO Standard Specifications for Structural Supports for Highway Signs, Luminaires, and Traffic Signals with interim revisions, the Central Region Traffic Signal Details, and the following:

a.	Make welds continuous.  Grind exposed welds flush with the base metal at slip fit joints for the length of the slip fit joint plus one half the diameter of the female section.

b.	On steels 5/16 of an inch thick and thicker, inspect 100 Percent of CJP welds by either radiography (RT) or ultrasound (UT).

c.	Inspect a random 25 percent of PJP and fillet welds by magnetic particle (MT).  If a defect is found, inspect 100% of the PJP and fillet welds made to fill the order.  In steels less than 1/8 inch thick, complete the tests according to AWS D1.1.

d.	Only visually inspect welds made on luminaire mast arms.

4.	Anchor Rods & Bolts.  Furnish 2 inch diameter (nominal) anchor rods for signal poles that meet ASTM F1554 Grade 105, are 96 inch minimum length and conform to Supplemental Requirements; S2, Permanent Manufacturer’s Identification, S3, Permanent Grade Identification and S-5 Charpy Impact Requirements.  Hot dip galvanize according to AASHTO M232.  Use nuts that conform to AASHTO Specification M292 of the grade, surface finish, and style for 2 inch diameter anchor rods.  Washers shall conform to AASHTO M293.

5.	Miscellaneous.  Finish the edges of poles and mast arms to conform to the following requirements.  Before hot dip galvanizing, neatly round the following features to the radius specified.

a.	On holes through which electrical conductors pass, provide a 1/16 inch radius on both the entrance and exit edges,

b.	On pole base plates, provide a 1/8 inch radius on edges along which plate thickness is measured and a smooth finish on all other exposed edges,

c.	On the ends of tubes that form slip type joints, complete the following tasks on the two surfaces that contact one another.  First, provide 1/16 inch radii on the inside and outside edges of the female and male segments, respectively.  Then for the length of the joint plus one half the diameter of the female section grind down welds until they feature a radius concentric with the mating surface and remove material protruding from the two surfaces.

Provide caps to cover the free ends of poles and mast arms.

Identify critical information for poles and arms with visible permanent aluminum tags that contain the information shown in Table 740-1.  The measurements shown are for illustration purposes only.  Use tags large enough to include required information using 1/4 inch high text, 3/8 inch of space between successive lines of text, and at least 3/8 inch of space between the edges of the tag and the text.  Secure the tags with two 1/8 inch blind rivets at the base of poles and the underside of mast arms.  If furnishing a two piece signal mast arm with slip type joint, mark both pieces with the same message.  Provide the holes for the blind rivets before galvanizing.

TABLE 740-1

POLE MARKINGS

Note:

Italic type indicates additional Tag Markings if poles have 2 luminaire or 2 signal mast arms.

| POLES (Including Mast Arms ) | MEASUREMENTS | TAG MARKINGS |
| --- | --- | --- |
| Signal Poles |  |  |
| a) Signal mast arm length | 45 ft./55 ft. | SMA 45/SMA 55 |
| b) Luminaire mast arm length | 22 ft./18 ft. | LMA 22/LMA 18 |
| c) Pole height | 36 ft. | PH 36 |
| d) Intersection number (if more than one) -pole number |  | 1 - P 4 |
| e) Sum of signal mast arm moments about centerline of signal pole |  | SM 4000/SM 3200 |
| f) Design wind speed | 100 mph | DWS 100 |
| Light Poles |  |  |
| a) Luminaire mast arm length | 15 ft./15 ft. | LMA 15/LMA 15 |
| b) Pole height | 37 ft. | PH 37 |
| Signal Mast Arm |  |  |
| a) Mast arm length | 40 ft. | SMA 40 |
| b) Intersection number (if more than one) -pole number |  | 1 - P 4 |
| c) Sum of signal mast arm moments about centerline of signal pole |  | SM 3740 |
| d) Design wind speed | 100 mph | DWS 100 |
| Luminaire Mast Arm |  |  |
| a) Mast arm length | 18 ft. | LMA 18 |
| b) Pole number (if unique arm design) |  | P 4 |

.

740-2.05 CONDUCTORS.  Replace Table 740-2 with the following:

TABLE 740-2

CONDUCTOR TERMINATION TABLE

| CONDUCTORS PER CABLE | CIRCUIT | WIRE COLOR | AWG. NO. | BAND LEGEND |
| --- | --- | --- | --- | --- |
| 7 | Vehicle Red | Red | 14 | Head No. |
|  | Vehicle Yellow | Orange |  |  |
|  | Vehicle Green | Green |  |  |
|  | Common Neutral | White |  |  |
|  | Spare | White/Black |  |  |
|  | Spare | Black |  |  |
|  | Spare | Blue |  |  |
| 7 | Vehicle Red Arrow | Red | 14 | Head No. |
|  | Vehicle Yellow Arrow | Orange |  |  |
|  | Vehicle Green Arrow | Green |  |  |
|  | Common Neutral | White |  |  |
|  | Spare | White/Black |  |  |
|  | Spare | Black |  |  |
|  | Spare | Blue |  |  |
| 7 | Vehicle Red | Red | 14 | Head No. |
|  | Vehicle Yellow | Orange |  |  |
|  | Vehicle Green | Green |  |  |
|  | Common Neutral | White |  |  |
|  | Spare | White/Black |  |  |
|  | Vehicle Yellow Arrow | Black |  |  |
|  | Vehicle Green Arrow | Blue |  |  |
| 4 | Pedestrian Don’t Walk | Red | 14 | Head No. |
|  | Pedestrian Walk | Green |  |  |
|  | Common Neutral | White |  |  |
|  | Spare | Black |  |  |
| 4 | Pedestrian Pushbutton | Black | 14 | Head No. |
|  | Neutral | White |  |  |
|  | Spare | Red |  |  |
|  | Spare | Green |  |  |
| 5 | Photo Electric Control | Black | 14 | PEC |
|  | Load to Contactor | Red |  |  |
|  | Neutral | White |  |  |
|  | Spare | Orange |  |  |
|  | Spare | Green |  |  |

TABLE 740-2

CONDUCTOR TERMINATION TABLE

(Continued)

| CONDUCTORS PER CABLE | CIRCUIT | WIRE COLOR | AWG NO. | BAND LEGEND |
| --- | --- | --- | --- | --- |
| 3 | Flashing Beacon | Black | 14 | Head No. |
|  | Neutral | White |  |  |
|  | Spare | Red |  |  |
| 3 | Preemption | Orange | 20 | "PRE" |
|  | Neutral | Blue |  |  |
|  | Spare | Yellow |  |  |
| 3 | Preemption Confirmation | Black | 14 | "PRECON" |
|  | Neutral | White |  |  |
|  | Spare | Red |  |  |
| 3 | Highway Luminaire | Black | 8 or 6 | Circuit No. |
|  | Highway Luminaire | Red |  | Circuit No. |
|  | Highway Luminaire Spare | White |  |  |
| 3 | Service to Controller | Black | 6 or 4 | "SIG" |
|  | Neutral | White |  | No Band |
|  | Spare | Red |  | No Band |
| 3 | Sign Luminaire | Black | 8 | SIGN |
|  | Sign Luminaire | Red |  | SIGN |
|  | Sign Spare | White |  |  |

Replace No. 5. with the following:

5.	Detector Loops.  Use No. 14 AWG conductors for detector inductive loops that meet IMSA Specification 51-3, Type RHW/USE, or IMSA Specification 51-5, when called for on the Plans or specified in the Special Provisions.

Replace "6 twisted pairs" in the second sentence of the 4th subparagraph of No. 6. with the following:

"7 twisted pairs"

Replace TABLE 740-3 with the following:

TABLE 740-3

INTERCONNECT TERMINATION TABLE

| TELEMETRY CABLE: Type PE-39, No. 19 AWG, Solid Copper, as noted on the Plans or in the Special Provisions |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Pair No. | Tip | Ring | Pair No. | Tip | Ring |
| 1 | White | Blue | 14 | Black | Brown |
| 2 | White | Orange | 15 | Black | Slate |
| 3 | White | Green | 16 | Yellow | Blue |
| 4 | White | Brown | 17 | Yellow | Orange |
| 5 | White | Slate | 18 | Yellow | Green |
| 6 | Red | Blue | 19 | Yellow | Brown |
| 7 | Red | Orange | 20 | Yellow | Slate |
| 8 | Red | Green | 21 | Violet | Blue |
| 9 | Red | Brown | 22 | Violet | Orange |
| 10 | Red | Slate | 23 | Violet | Green |
| 11 | Black | Blue | 24 | Violet | Brown |
| 12 | Black | Orange | 25 | Violet | Slate |
| 13 | Black | Green |  |  |  |

Replace Subsection 740-2.06 ELECTRICAL CONDUIT with the following:

740-2.06 ELECTRICAL CONDUIT AND FITTINGS.  Unless specified otherwise, use rigid metal conduit and fittings for raceways.  Furnish galvanized rigid type conduit and elbows conforming to UL Standard 6 and are manufactured of mild steel according to ANSI C80.1.  Furnish third party certified fittings designed for rigid metal conduit.

For loop detectors, use Schedule 80 polyvinyl chloride (PVC) conduit that conforms to UL Standard 651.  Use PVC fittings meeting NEMA TC 3.

When polyethylene conduits are specified in the Plans, use a smooth wall, schedule 40, high-density polyethylene (HDPE) pipe that conforms to UL Standard 651 B and NEMA TC-7-2000.

Furnish insulated throat grounding bushings made of malleable iron or steel with a mechanically galvanized or zinc plated finish.  Grounding lugs shall either be an integral part of the bushing or consist of an attached tin plated copper saddle.  Grounding lugs shall feature a stainless steel screw, the centerline of which falls within 20 degrees of conduit centerline.  The bushings furnished shall also feature a stainless steel or brass mounting screw that locks the bushing onto the conduit end.

Furnish conduit outlet bodies and their covers with a hot dip galvanized finish and stainless steel screws.  For loop detectors, furnish Type X bodies and, for photoelectric control installation, furnish Types C and LB conduit bodies.

When Myers hubs are specified, furnish rain tight, grounding type hubs made of malleable iron with a hot dip or mechanically galvanized finish.

At expansion joints, provide watertight expansion fittings capable of the following movements without damaging the conduits attached to it or the conductors that pass through it.  The movements include:  axial expansion or contraction to 3/4 inch, angular misalignments in any direction to 30 degrees, and parallel misalignment of the conduits to 3/4 inch.  The fittings shall also include a braided copper bonding jumper equal to an 8 AWG conductor, bushings to prevent scraping the conductors, and a smooth inner sleeve that maintains a constant diameter regardless of conduit alignment.

Replace Subsection 740-2.09 CONTROLLER ASSEMBLIES with the following:

740-2.09 CONTROLLER ASSEMBLIES. Provide solid state, traffic controller assemblies having level 2 conformance to NEMA Standard Publication TS 2-2003 V02.06, Traffic Controller Assemblies with NTCIP Requirements as defined in NTCIP1202.  Traffic Controller Assemblies must meet or exceed the Environmental Requirements of Section 2 of the NEMA TS2-2003 V02.06 document. The Original Equipment Manufacturer (OEM) and its manufacturing and testing facilities shall be ISO 9001:2000 certified for processes involving the Traffic Controller Assemblies.

Use traffic control equipment that is compatible with the existing traffic signal monitoring system.  Compatibility must be 100% at the cabinet level to include inputs, outputs, telemetry protocol, and block upload and download of RAM data.

In addition, features of the existing local controllers and controller modules must be functionally duplicated to meet or exceed the performance of the existing equipment.

The existing local controller cabinets at other intersections include the following equipment:

(1)	Econolite ASC/3-2100

(2)	Econolite Cobalt 2100

	Use LED indicators for all electronic devices covered under Subsections 740-2.09 through 740-2.13.

Replace Subsection 740-2.10 CONTROLLER UNIT with the following:

740-2.10 CONTROLLER UNIT.

Actuated Controller Unit (CU).

Provide solid state, Type A2N Actuated Controller Units (CU) meeting the requirements of Section 3 of the NEMA Standard Publication TS 2-2003 V02.06, Traffic Controller Assemblies with NTCIP Requirements.

	The CU must meet the referenced National Transportation Communications for ITS Protocol (NTCIP) and comply with publication TS 3.2 the Simple Transportation Management Framework, and shall meet the requirements for Conformance Level 2

	The software shall comply with NEMA TS 3.3, the Class B Profile, and shall include both an EIA/TIA 232-E and an FSK modem interface for NTCIP based communications.

	The CU shall implement conformance groups and optional object groups as defined in NEMA TS 3.4 and TS 3.5 for A2N level 2.

	Provide controllers with display heaters or enhancements to improve viewing in temperatures below 0 F.

	Provide controllers having an interface compatible with SYNCRO-7 traffic modeling software.

Furnish Econolite Cobalt 2100 controller unit with the following optional features:

	User interface Advanced Display with graphics and touch-screen

	TS2 Type I connector

	Data Key 3.3V, 32MB

Replace Subsection 740-2.11 CONTROLLER CABINET with the following:

740-2.11 CONTROLLER CABINET. Provide a controller cabinet that meets the requirements of NEMA Standard TS 2-2003 V02.06 Traffic Controller Assemblies with NTCIP Requirements (NEMA TS-2), Section 5 Terminals and Facilities and Section 7 Cabinets.

1.	Standard Features. Supply the following standard features:

a.	Materials

Unless otherwise designated in the Plans, provide cabinets constructed of sheet Aluminum.

b.	Cabinet Dimensions

Unless otherwise designated in the Plans, provide a size 6 cabinet as defined in NEMA TS-2 Table 7-1.

c.	Doors

(1)	Provide doors meeting the requirements of NEMA TS-2 Section 7.5.  The lock must accept a Best CX series core that will be installed by the Department after the Contract is complete.

(2)	Provide a Police Compartment meeting the requirements of NEMA TS-2 Section 7.5.7.  The Police Compartment shall house the following switches:

(a)	"flash/automatic" switches that when placed in the "flash" position causes the intersection displays to go into the flashing mode.  When placed in the "automatic" position, the signal system must resume normal operation.

(b)	"signals on/off" switch that when placed in the "off" position removes power from the signal bus.  Do not allow power on the bus when either "automatic" or "flash" operation is selected by any means.

(3)	Permanently label switches in the Police Compartment.

d.	Shelves

Provide shelves meeting the requirements of NEMA TS-2 Section 7.6. Provide additional laptop computer shelf mounted approximately 42" above ground level.  The laptop shelf must accommodate a standard 17" computer and be retractable below one of the cabinets’ shelves.

e.	Finish and Preparation

Unless otherwise designated in the Plans, provide unpainted Aluminum Cabinets with a "natural" brushed appearance.

f.	Cabinet Mounting

(1)	Provide cabinet mounting features as defined NEMA TS-2 Section 7.8.

(2)	The cabinet manufacturer is responsible for providing a cabinet that will mount without modification on the foundation detailed in Alaska Department of Transportation Central Region, Regional Detail, Controller Cabinet Foundation.

g.	Cabinet Ventilation

Furnish a cabinet that fully meets the requirements of NEMA TS-2 Section 7.9 and the following:

(1)	Furnish the fan and cabinet vent with internally mounted metal covers that are fabricated to close off the flow of air during winter operation.

(2)	Equip the cabinet with a selectable, 600/900/1500 watt cabinet heating device.  The heating device must have a remote air sensing thermostat. The contacts must be rated 20 amps, 120 volts, 60 hertz.

(a)	Construct the thermostat so that contacts close on descending temperature and are adjustable between 0 and 30 °F ±5 °F. The contacts must open on rising temperatures of 15 °F above the closing temperature.  The adjustment must have an indicating pointer.

(b)	Connect the thermostat in series with an electrical resistance heater and blower fan.  The blower fan must be rated for continuous duty.  The heater and fan must be connected in parallel and rated 120 volts, 60 Hertz.  Mount the unit in the vertical position on the cabinet door beneath the auxiliary "goose neck" cabinet light.  The thermostat shall be mounted immediately to the left of the heating device on the cabinet door.

(c)	Do not block the air intake or outlet.  Provide the unit with a SPST manual override switch that bypasses the thermostat to enable the fan and heater to operate at warmer temperatures.

h.	Auxiliary Cabinet Equipment

(1)	Mount a hooded incandescent light fixture with a 15 inch flexible "goose neck" from the cabinet door.  Use a fixture UL rated to accommodate a 25 watt lamp with an integral "ON-OFF" rotary switch mounted on the lamp hood.  Mount a fluorescent lighting fixture on the inside of the cabinet near the front edge.  Use a fixture rated to accommodate an F15T8 lamp operated from a high power factor UL or ETL listed ballast.  The lamp must be included.  The lighting fixture "ON-Off" switch must be a toggle switch mounted on an inside control panel.  Include in the circuit a door actuated switch that turns the light ON when the door is open and OFF when the door is closed.

(2)	Provide three (3) paper sets of complete and accurate cabinet drawings with each cabinet.  Make cabinet drawings available electronically in AutoCAD v2004 or later format and deliver with paper set.

(3)	Provide one paper set of manuals for the controller, Malfunction Management Unit and vehicle detector amplifiers with each cabinet. Make said manuals available in electronic Adobe "pdf" format and deliver with paper set.

i.	Cabinet Wiring

Neatly arrange the wiring within controller cabinets to conform to the requirements of Subsections 660-3.05 and 740-2.05.  Furnish controller cabinets wired to accommodate

(1)	Configuration #4 in Table 5-2 of the NEMA Standards Publications No. TS 2-2003 V02.06, Traffic Controller Assemblies with NTCIP requirements with two each Type 2 detector racks.

(a)	Equip the cabinet with required control and auxiliary equipment connecting cables to operate the phases and detection indicated on the Plans, including future use.

(b)	Size wiring, switches, surge protectors, flash relays, and flashers to handle the necessary amperage required under full cabinet use.  Use orange colored wires to run from the flash transfer relay used for emergency flash programming.

(c)	Wire the cabinet to accommodate 6 unique preempt sequences as defined by NEMA TS-2 Section 3.7 and 2 auxiliary preempt sequences.  Configure each detector rack to accommodate 4 unique sequences.

j.	Field Terminal Blocks

Provide Terminals and Facilities meeting the requirements of NEMA TS-2 Section 5, Configuration #4 (Table 5-2) and the following:

(1)	Provide 2 or more insulated terminal blocks to terminate field conductors.  Provide each block with 12 poles with 10-32 screw type terminals.  Use a terminal block that is a barrier type with removable shorting bars in each of the 12 positions and with integral type marking strips.  Terminate conductors to a terminal block.

(2)	Terminate conductors from the controller unit in ring type terminal lugs or solder them to a through panel solder lug on the rear side of the terminal.  Terminate other conductors in spade type terminal lugs.

(3)	Do not bring more than 3 conductors to any one terminal.  Two flat metal jumpers, straight or U shaped, may also be placed under a terminal screw.  Fully engage at least 2 full threads of terminal screws when the screw is tightened.  Do not extend live parts beyond the barrier.

(4)	Terminals must be provided to terminate a future 25 pair interconnect cable with each conductor terminated on individual terminals.  Terminate interconnect cable conductors on individual terminals.

(5)	On the right side of controller cabinets, install two 16 position bus bars, for terminating the equipment grounding and neutral conductors used inside the cabinets.  On the left side of the controller cabinets, install two 32 position bus bars, for terminating the equipment grounding and neutral conductors from field wiring.

k.	Cabinet Accessories

See NEMA Standard TS 2-2003 V02.06, Section 5 Terminals and Facilities, Figure 5-4 Cabinet Power Distribution Schematic for Items (1) through (6).

(1)	Disconnecting Means

(a)	Main circuit breaker must be a single pole, 30 ampere, 10,000 amperes interrupting capacity for each cabinet.

(b)	Auxiliary circuit breaker(s) must be single pole, 20 ampere, 10,000 amperes interrupting capacity to protect fan, heater, light, and convenience outlet(s).

The rating of the main disconnect means with overcurrent protection must be not less than 125% of the maximum anticipated continuous load.  When using disconnecting circuit breakers, use "trip indicating trip free," Type.

(2)	Signal Bus.  Connect the signal bus to the incoming AC line through a signal bus mercury contactor and an overcurrent protection device.  Energize the signal bus mercury contactor to provide power to the signal bus.  The current rating of the signal bus mercury contactor must be at least the current rating of the main overcurrent protection device.

(3)	AC Service Transient Suppression.  Connect the transient suppression device for the primary feed of the cabinet on the load side of the cabinet overcurrent protection device.  The transient voltage suppression device connected to the controller power circuit must provide protection against voltage abnormalities of 1 cycle or less duration.

(a)	The suppressor must be solid state high energy circuit containing no spark gap, gas tube, or crow bar component.  The current rating of the device must be 15 amps minimum.  The device must provide transient protection between neutral and ground, line and ground, as well as line and neutral.  If the protection circuits fail, they must fail to an open circuit condition.  The device must meet requirements of UL Standard 1449.

(b)	The suppressed voltage rating must be 600 volts or less when subject to an impulse of 6,000 volt, 3,000 amp source impedance, 8.0/20 microsecond waveform as described in UL Standard 1449.  In addition, the device must withstand, without failure or permanent damage, one full cycle at 264 volts RMS.

(c)	The device must contain circuitry to prevent self induced regenerative ringing.  There must be a failure warning indicator light that must illuminate when the device has failed and is no longer operable.  The transient suppression device must withstand a 20,000 ampere surge current with an 8x20 microsecond (time to crest x time to second halfcrest) waveform 20 times at 3 minute intervals between surges without damage or degradation to the suppressor.  Output voltage must not exceed 500 volts at any time during the test.  Use a device that is a solid state, high energy circuit with no spark gap, gas tube, or bar component.

(4)	Radio Interference Suppression.  Equip each traffic cabinet, flasher, and other current interrupting device with a suitable radio interference suppressor installed at the input power point.  Install the radio interference suppressor after the AC service transient suppression unit described in Subsection 740-2.11.1.k (3).  It must provide a minimum attenuation of 50 decibels over a frequency range from 200 kilohertz to 75 megahertz, when used with normal installations.

(a)	The interference suppressor must be hermetically sealed in a substantial metal case filled with suitable insulating compound. Terminals must be nickel plated, 10-24 brass studs of sufficient external length to provide space for connecting two No. 8 conductors and must be so mounted that the terminals cannot be turned in the case.  Ungrounded terminals must be properly insulated from each other and must maintain a surface leakage distance of not less than 1/4 inch between any exposed current conductor and any other metallic part, with an insulation factor of 100 to 200 megohms dependent on external circuit conditions.

(b)	The radio interference suppressor must have a minimum current rating equal to the rating of the main disconnect means as specified in Subsection 740-2.11.1.k (1) (a).  It must be designed for operation on 120 volts, 60 hertz, single phase circuits and be UL and EIA compliant.

(c)	Connect the ground connection of the radio interference suppressor only to AC neutral.  Do not connect to Earth Ground directly.

(5)	Communications Transient Suppression.  Provide a transient suppressor for the system interface communications lines when used.  This suppressor must withstand a 100 ampere 10 x 700 microsecond waveform 20 times at 30 second intervals between surges without damage or degradation to the suppressor.  Apply the transient surge both line to line and line to ground. Output voltage must not exceed 8 volts line to line and line to ground.  Output voltage must not exceed 8 volts line to line or 250 volts line to ground at any time during the test.

(6)	Control Panel.  Provide and label a control panel assembly that is readily accessible from the front of the cabinet. The control panel assembly must consist of:

(a)	"controller power" switch to energize the controller while the signal lights are off or are being operated by the flasher.  Label and rate the switch for load current.

(b)	An electrical outlet.  It must be a duplex, 3 prong, NEMA Type 5-20R grounding type outlet with independent ground fault circuit protection.

(c)	"auto/flash" switch that when placed in the "flash" position provides flashing operation without interrupting the controller unit power. When the switch is placed in the "auto" position the controller unit must provide normal operation.

(d)	"stop time/off/on" switch that when placed in the "stop time" position causes the controller unit to stop time.  In the "off" position, the controller unit must be active regardless of external commands.  In the "on" position, the timing must be normal but subject to external command interruptions.

(e)	"heater by-pass" switch to bypass the remote heater thermostat.

(f)	momentary contact test switches to place calls on each vehicle and pedestrian phase.  Switches must provide tactile feedback and be rated at 1 ampere, minimum, for a resistive load at 120 VAC and at 28 VDC.  Contacts must be coin silver or gold plated and be enclosed and labeled as to their function.

2.	Special Features. Provide special features if called for in the Plans or as specified in the Special Provisions.

Coordination "Remote/Time of Day/Free" Switch.  When the switch is in the "Remote" position, supervisory functions performed on the controller unit from a master coordinator or central computer must operate normally.

When the switch is in the "Time of Day" position, the local controller must use the local coordinators time of day plan.  When the switch is in the "Free" position, it must be possible to remove any or all coordination devices and maintain normal, non-coordinated controller operation without wire jumpers, jumper plugs or other special devices.  Provide this switch if a local coordination or system modem/interface unit is shown on the Plans.

Replace Subsection 740-2.12 STANDARD AUXILIARY EQUIPMENT with the following:

740-2.12 STANDARD AUXILIARY EQUIPMENT.

Provide equipment meeting the requirements of Section 6 of the NEMA Standard Publication TS 2-2003 V02.06, Traffic Controller Assemblies with NTCIP Requirements (NEMA TS-2).

1.	Three Circuit Solid State Load Switches.  Use load switches conforming to NEMA TS-2, Section 6.2 Three Circuit Solid State Load Switches and as a minimum include Light Emitting Diode indicators on the DC input circuitry.  The load switch must have three independent switching circuits, each being an individually replaceable solid state module.

2.	Solid State Flasher.  Use a NEMA Type III flasher unit that conforms to NEMA TS-2, Section 6.3 Solid State Flashers.

3.	Malfunction Management Unit (MMU).  Provide Type 16 MMU to be fully compliant with the requirements of NEMA TS-2, Section 4.  In addition, the MMU shall have a full intersection LCD back lighted signal on the front panel and shall be downward compatible with TS-1 CMUs.

4.	Flash Transfer Relay.  Use flash transfer relays that meet the requirements of NEMA TS-2, Section 6.4 Flash Transfer Relays.

Replace Subsection 740-2.13 SPECIAL AUXILIARY EQUIPMENT with the following:

740-2.13 SPECIAL AUXILIARY EQUIPMENT. Use the following special auxiliary equipment when called for on the Plans and/or Special Provisions:

Provide equipment meeting the requirements of the cited Sections of the NEMA Standard Publication TS 2-2003 V02.06, Traffic Controller Assemblies with NTCIP Requirements (NEMA TS-2).

1.	Inductive Loop Detectors Units. Provide inductive loop detectors that conform to the requirements of NEMA TS-2, Section 6.5 Inductive Loop Detector Units.  Unless otherwise called for in the Plans provide 2 Channel Inductive Loop Detectors with audible feedback of detection events.  The audible feature must be manually switchable between audible "on" and silent "off."

2.	Local Coordination Units. Provide actuated coordination that conforms to the requirements of NEMA TS-2, Section 3.6 Actuated Coordination.

3.	System Modem/Interface Unit.  Supply a system modem/interface unit assembly that is compatible with the existing computerized traffic control system.

4.	Preemption Units. Provide preemption that conforms to the requirements of NEMA TS-2, Section 3.7 Preemption and the following:

Install the following components of the GTT Company’s Opticom Priority Control System according to GTT’s written installation instructions at the signalized intersections listed on the Plans.

a.	The system must be capable of sending a signal to the controller when an Opticom signal from a vehicle-mounted "GTT OPTICOM Emitter" has been received and maintained for a period of 1.7 seconds.

b.	Use Opticom Priority Control System Model 792H emitters.

c.	Unless otherwise shown on the Plan use Opticom Traffic Control Systems Opticom Detector Model 721 preemption detectors.

d.	Furnish the number of Opticom Traffic Control Systems 764 Phase Selectors to meet the number of channels of detection for each intersection, or as specified in the Plans. For each controller cabinet scheduled to receive a 764 Phase Selector provide, for each Phase Selector, a Model 768 Opticom Interface Panel.

e.	When more than one detector is required per phase, furnish the required number of harnesses for the 764 Phase Selectors to handle the auxiliary detection.

f.	Install Model 138 Optical detector lead in cable between the end of each signal mast arm and the controller cabinet.  Furnish enough slack in these cables for them to extend 2 feet beyond the end of each signal mast arm and to leave 10 feet of slack in the controller cabinet.  Seal both ends of each lead in cable with mastic lined, heat shrink tubing end caps.

g.	The controller, rather than the phase selector or auxiliary logic, must perform interval timing, signal sequences, and phase skips.

h.	Mount detectors according to manufacturer recommendations or as approved by the Engineer.  Mount and aim detectors to provide maximum emergency vehicle recognition.  Detector locations shown on the Plans are approximate and subject to change as directed by the Engineer.

i.	When emitters are required, provide GTT Opticom Priority Control System, Model 792H Emitter with 793 in vehicle switch.  The Emitter shall be factory programmed to the class and vehicle identification numbers assigned by jurisdiction as shown in the Plans and the following:

(1)	Class 0 and Vehicle ID. Number 0 (Zero) shall be disabled for Emitters.

(2)	Vehicle Id. Numbers shall be sequential, beginning with the lowest number in the EVP Emitter table for the appropriate class.

(3)	Provide one copy of 790IS Emitter Software Kit including "Y" cable.

(4)	One GTT Opticom Portable Emitter Kit with 792R emitter on a magnetic base, 793R switch and cigarette lighter adapter power cord in a "Camera Bag" case.

5.	Bus Interface Unit (BIU).  Provide BIU’s that fully meet the requirements of NEMA TS-2 Section 8.  Unless otherwise called for in the Plans provide BIU’s that meet the NEMA designation BIU2.

6.	Traffic Logging System.  If called for in the Plans, furnish, and install in the controller cabinet, a stand-alone unit that collects, time stamps, and stores data in an unattended manner.

7.	Video Detection System.

a.	General.

(1)	System Hardware. Use machine vision system hardware consisting of the following components:

(a)	Color Machine Vision Processor (MVP) sensors as shown in the Plans

(b)	Terra Access Point (TAP)

(c)	Communication interface panel

(d)	Personal computer (PC)

The PC shall host the server and client applications that are used to program and monitor the other system components.  The MVP sensor shall be an integrated color zoom camera and processor that perform real-time traffic detection. Each MVP sensor shall be programmable with a minimum of twenty detection zones to satisfy the traffic detection needs of a variety of simple to complex traffic applications.  The detection zones shall be user-defined though interactive graphics software running on a PC.  The detection zones and the associated traffic functions and alarms shall be downloaded to the MVP for operation.  The real-time performance shall be observed by viewing the video output from the sensor with overlaid flashing detector’s to indicate the current detection state (on/off).  Subsequent redefinition of detection zones shall be permitted for rapid reconfiguration of fine-tuning detection performance.  The MVP sensor shall calculate detector states in real-time and communicate the detection information to the TAP that subsequently translates the detection state directly to a traffic signal controller in real time.  The MVP sensor shall optionally store cumulative traffic statistics, internally in non-volatile memory, for later retrieval and analysis.

The MVP shall communicate to the Terra access Point, communications panel and the software applications using the industry standard TCP/IP network protocol.  The MVP shall have a built in Internet Protocol (IP) address and shall be addressable with no plug in devices or converters required.

The Terra Access Point shall communicate directly with up to eight (8) MVP sensors and shall comply with the form factor and electrical characteristics to plug directly into a NEMA Type C or D detector rack providing up to thirty-two (32) inputs and sixty-four (64) outputs directly with a TS2 Type traffic signal controller.

The communication interface panel shall be hardwired into a traffic signal cabinet or junction box.  The communication interface panel shall be a Eight-sensor model and provide the electrical termination of wiring for video, data, and power for the MVP.

The communication interface panel shall provide high-energy transient protection to electrically protect the Terra Access Point and connected MVP sensors.

(2)	System Software. The MVP sensor embedded software suite shall incorporate multiple applications that perform a variety of diagnostic processing.  Its primary function is to detect vehicular traffic approaching or departing the MVP sensor in multiple traffic lanes.  The detection shall be reliable, consistent, and perform under all weather, lighting, and traffic congestion levels.

There shall be a suite of client applications that reside on the host client/server PC.  The applications shall execute under Microsoft Windows 98, 2000, Windows NT, and XP. Available client applications shall include:

(a)	Network Browser:  Learn a network of connected Terra Access Pints and MVP’s then show the topology in a logical hierarchical relationship

(b)	Detector Editor: Create and modify detector configurations to be executed on the MVP sensor

(c)	Operation Log: Extract the MVP run-time operation log of special events that have occurred.

(d)	Data Archive: Extract time interval cumulative traffic statistics in real time (on the same time interval spacing) or after long periods of data accumulation (for instance, once a day or once a week, etc.)

(e)	Software Installer: Reconfigure one or more MVP sensors with a newer release of embedded system software.

b.	Functional Capabilities

(1)	MVP Image Sensor. The MVP image sensor shall be an integrated imaging color CCD array with optics, high-speed image processing hardware and a general purpose CPU bundled into a sealed enclosure.  The MVP Sensor shall be equipped with a sunshield to reflect solar heat and to shield the CCD array from direct exposure to the sun.  The CCD array shall be directly controlled by the general purpose CPU, thus providing high video quality for detection that has virtually no noise to degrade detection performance.  The optics and camera electronics shall be directly controlled for optimal illumination for traffic detection.  The lens shall be pre-focused at the factory, as required for operation.  It shall be possible for the user to zoom the lens, as required for operation.  The MVP sensor shall operate at a maximum rate of 30 frames per second when configured for the NTSC (US) video standard.  The MVP shall process a minimum of twenty detector zones simultaneously placed anywhere in the field of view of the sensor.  The video output shall have the ability to selectively show overlaid graphics indicating the current real-time detection state of each individual detector defined in the video.  The sensor output NTSC video shall be viewed with any compatible video-display device.

(2)	Differential Video. The MVP sensor shall output full motion color video through the means of a differential video port in NTSC format.  The differential video is transmitted over a single twisted pair.

(3)	Power. The MVP sensor shall operate on 24 VAC, 50/60Hz at a maximum of 25 watts.  The camera and the processor electronics shall consume a maximum of 10 watts and the remaining 15 watts shall support an enclosure heater.

(4)	MVP Operations Log. The MVP shall maintain a non-volatile operations log, which minimally contains:

(a)	Revision numbers for the current MVP sensor hardware and software components in operation.

(b)	Title and comments for the specific detector configuration file downloaded to the MVP.

(c)	Date and time the Operations Log was last cleared.

(d)	Date and time communications were opened or closed with the MVP.

(e)	Date and time of last power-up.

(f)	Time stamped MVP self-diagnosed hardware and software error to aid in system maintenance and troubleshooting.

(5)	MVP Vehicle Detection. The real time detection performance of the MVP shall be optimized by following the set of guidelines for:

(a)	The traffic application to perform,

(b)	MVP sensor mounting location,

(c)	The number of traffic lanes to monitor,

(d)	The sizing, placement, and orientation of Count and Presence detectors,

(e)	Traffic approaching and/or receding from the sensor’s field of view,

(f)	Minimizing the effects of lane changing maneuvers.

(6)	Detection Zone Placement. The video detection system shall provide flexible detection zone placement anywhere and at any orientation within the field of view of the MVP sensor.  Preferred detector configurations shall be:

(a)	Detection zones placed across lanes of traffic for optimal count accuracy or

(b)	Detection zones placed parallel to lanes of traffic for optimal presence detection accuracy of moving or stopped vehicles.

A single detection zone shall be able to replace one or more conventional detector loops connected in series.  Detection zones shall be able to be overlapped for optimal road coverage.  In addition, selective groups of detectors can be logically combined into a single output by using optional delay and extend timing and signal state information.  Optimal detection shall be achieved when the MVP sensor placement provides an unobstructed view of each traffic lane where vehicle detection is required.  Examples of obstructions are not limited to fixed objects.  Obstruction of the view can also occur when vehicles from a lane nearer to the sensor obscure the view of the roadway of a lane farther away from the sensor.

(7)	Detection Zone Programming. Placement of detection zones shall be by means of a supervisor computer (PC) operating in the Windows 98, 2000 or Windows NT graphical environments, a keyboard, and a mouse.  The monitor shall be able to show the detection zones superimposed on images of traffic scenes.

The detection zones shall be created by using a mouse to draw detection zones on the supervisor computer’s monitor.  Using a mouse and the keyboard it shall be possible to place, size, and orient detection zones to provide optimal road coverage for vehicle detection.  It shall be possible to download detector configurations from the supervisor computer to the MVP, to retrieve the detector configuration that is currently running in the MVP, and to back up detector configurations by saving them to the supervisor computer’s removable or fixed disks.

The supervisor computer’s mouse and keyboard shall be used to edit previously defined detector configurations to permit adjustment of the detection zone size and placement, to add detectors for additional traffic applications, or to reprogram the sensor for different traffic applications or changes in installation site geometry or traffic rerouting.

(8)	Detection Zone Operation. The MVP real time detection operation shall be verifiable through several means.  The primary method shall be to view the video output of the sensor with any standard video display device (monitor).  The video with overlaid detection zones shall display each detector as white, when the state of the detector is ON, or as black, when the state of the detector is OFF.  Each detector shall be selectively assignable to be visible or hidden in the detector flashing video display when the detector configuration file is programmed.

Additional verification of detector operation includes visual observation of the LED’s on the front of the TAP and/or confirmation of detection as recognized by the traffic controller.

(9)	Optimal Detection. The video detection system shall optimally detect vehicle passage and presence when the MVP sensor is mounted 30 ft. or higher above the roadway, when the image sensor is adjacent to the desired coverage area, and when the distance to the farthest detection zone locations are not greater than ten (10) times the mounting heights of the MVP.  The recommended deployment geometry for optimal detection also requires that there be an unobstructed view of each traveled lane where detection is required.  Although optimal detection may be obtained when the MVP is mounted directly above the traveled lanes, the MVP shall not be required to be directly over the roadway.  The MVP shall be able to view either approaching or receding traffic or both in the same field of view.  The preferred image sensor orientation shall be to view approaching traffic since there are high contrast features on vehicles as viewed from the front rather than the rear. The MVP sensor placed at a mounting height that minimizes vehicles image occlusion shall be able to monitor a maximum of six (6) to eight (8) traffic lanes simultaneously.

(10)	Terra Access Point Detector Port Master. The Terra Access Point card shall provide the hardware and software means for up to eight (8) MVP sensors to communicate real time detection states and alarms to a local traffic signal controller.  It shall comply with the electrical and protocol specifications of the detector rack standards.  The card shall have 1500 Vrms isolation between rack logic ground and street wiring.

The Terra Access Point card shall be a simple interface card that plugs directly into a NEMA TS2 Type C or D detector rack.  The TAP TS2 card shall provide 32 phase inputs and 64 detector outputs.

(11)	MVP Input and Output Assignments. Input and Output assignments are programmed into the MVP through the local "Supervisor" port on the detector rack interface card.  The MVP declares which input and output pins are utilized during operation, the card requires no software configuration or setup.  Detector outputs shall be assigned to any detector type that changes on/off state and consecutive pairs of outputs shall emulate the output of two (closely spaced) detectors to report speed of individual vehicles.

(12)	Jumper Configurable TS1 I/O. Two jumpers shall permit the card to be configured so that all inputs and outputs go either to the rear edge connector or the front panel DB 15 connector.

(13)	Terra Interface Panel. The Terra communications interface panel supports one to Eight MVPs.  The communications interface panel consists of a predefined wire termination block for MVP power, data, and video connections, a power transformer for the MVP, electrical surge protectors to isolate the TAP and MVP, and an interface connector to cable directly to the TAP.

(14)	MVP Sensor Power. The interface panel shall provide power for one (1) MVP through a step-down transformer, taking local line voltage and producing 28 VAC, 50/60 Hz, at about 30 watts.  A 1/2 amp slow-blow fuse shall individually protect the step-down transformers.

(15)	High Energy Transient Suppression. The interface panel shall provide termination points for all street wiring of the MVP and high-energy transient protection.  The interface panel shall provide high energy crowbar transient protection, to NEMA TS2 standards.  The transient suppression shall protect all of the interconnected hardware.

(16)	Interface Panel I/O Terminations. The Terra interface panel terminal block includes terminations for one (1) to eight (8) MVPs.  This shall include terminations for:

(a)	3 termination points for power, Communications and Video to and from the MVP sensor

(17)	Supervisor Software Suite. The system software shall support either small or large networks of field hardware of MVP sensors, TAPs, and commercial telecommunications equipment.  The communication of traffic data, alarms, video snapshots, etc. across the network shall use the client server relationship model.  The central communications server, the ComServer, provides local or remote access to all networked field hardware to a variety of client applications that can execute simultaneously on the same host computer as the ComServer or across a local area network.  Local access shall provide direct hook-up/link to field hardware (for field installation and maintenance) even though the field hardware may be communicating to remote client applications.  Remote access shall provide connection to specific field hardware over long distances as part of a larger interconnected network.  The Supervisor Software Suite shall consist of the ComServer and all of the supplied client applications.

The Supervisor Software Suite shall provide an easy to use graphical user interface and support all models/versions of the supplied MVP and Mini–Hub.  The software shall support both still image and real-time viewing of video images within in Windows.  Programming the MVPs and designating inputs and outputs from/to the TAPs shall be performed with detectors overlaid on still images and monitoring the detection performance of the MVPs shall be displayed with "live" video.

The Supervisor Software Suite consists of the:

(a)	ComServer, to provide the network communications services of deployed field hardware to client applications

(b)	Network Browser, to activate selected client applications with associated field hardware in the network

(c)	Detector Editor, to create and modify detector configurations to be executed on the MVPs and TAPs in the field

(d)	Operation Log, to extract the MVP run-time operation log of special vents that have occurred

(e)	Data Archive, to extract time interval cumulative traffic statistics in real time (on the same time interval spacing) or after long periods of data accumulation (for instance, once a day or once a week, etc.) and stored locally to the Supervisor PC

(f)	Installer, to reconfigure one or more MVPs with a newer release of embedded system software.

(18)	Supervisor Computer System. A supervisor computer system is not required.

c.	MVP Hardware

(1)	MVP Image Sensor. The MVP video detection system shall use medium resolution, color image sensor as the video source for real-time vehicle detection.

As a minimum, each image sensor shall provide the following capabilities:

(a)	Images shall be produced with a color CCD sensing element with horizontal resolution of at least 500 lines and vertical resolution of at least 350 lines.

(b)	Images shall be output as a video signal conforming to NTSC specifications.

(c)	Provide software JPEG video compression.

(d)	Useable video and resolvable features in the video image shall be produced when those features have luminance levels as high 10,000 lux during the day.

(e)	Useable video and resolvable features in the video image shall be produced when the ratio of the luminance of the resolved features in any single video frame is 300:1.

(f)	Provide direct real-time iris and shutter speed control.

(g)	Be usable for video surveillance.

(h)	An optical filter and appropriate electronic circuitry shall be included in the image sensor to suppress "blooming" effects at night.

(i)	Gamma for the image sensor shall be preset at the factory to a value of 1.0.

(2)	MVP Optics. The MVP image sensor shall be equipped with an integrated zoom lens that can be changed using either configuration computer software or a hand-held controller.

(3)	MVP Enclosure. The image sensor and lens assembly shall be housed in an environmental enclosure that provides the following capabilities:

(a)	The enclosure shall be waterproof and dust-tight to NEMA-4 specifications, and shall have the option to be pressurized with dry nitrogen to 5  1 psi.

(b)	The enclosure shall allow the MVP image sensor to operate satisfactorily over an ambient temperature range from –29° F to 140° F while exposed to precipitation as well as direct sunlight.

(c)	The enclosure shall allow the image sensor horizon to be rotated during field installation.

(d)	The enclosure shall include a provision at the rear of the enclosure for connection of the factory-fabricated power, communications, and video signal cable.  Input power to the environmental enclosure shall be 110 VAC and either 50 or 60 Hz as an option.

(e)	A heater shall be at the front of the enclosure to prevent the formation of ice and condensation in cold weather, as well as to assure proper operation of the lens’ iris mechanism.  The heater shall not interfere with the operation of the image sensor electronics, and it shall not cause interference with the video signal.

(f)	The enclosure shall be light-colored and shall include a sun shield to minimize solar heating and glare.

(g)	The front edge of the sunshield shall protrude beyond the front edge of the environmental enclosure and shall include provision to divert water flow to the sides of the sunshield.

(h)	The amount of overhang of the sunshield shall be adjustable to prevent direct sunlight from entering the lens or hitting the faceplate.

(i)	The total weight of the image sensor in the environmental enclosure with sunshield shall be less than 6 pounds.

(j)	When operating in the environmental enclosure with the power, communication and video signal cable connected, the image sensor shall meet FCC class B and CE requirement for electromagnetic interference emissions.

(4)	MVP Electrical. Connections for video, communications and power shall be made to the image sensor using a single connector (Easy Lock). The Contractor shall supply the 3 conductor (1175-006) 18 AWG Carolprene flexible cable, which will run from the back of the camera to the signal controller cabinet.

(5)	MVP Field Interface Equipment. An MVP communication interface panel shall be available for installation inside the traffic cabinet.  The panel shall provide twisted-pair connection points with approved transient protection.  Transient protection shall be included for each MVP image sensor.  Additionally, the communication interface panel shall provide 110 VAC for each sensor using transformers that step down the voltage from the existing 110 or higher AC power available in the cabinet.  The interface panel 3-wire input power shall be connected to the transient protected side of the AC power distribution system in the traffic control cabinet in which the panel is installed.

d.	System Installation. The supplier of the video detection system shall supervise the installation and testing of the video detection system and computer equipment.  A factory certified representative from the supplier shall be on-site during installation.  Install all video detection equipment in accordance with the manufacturer’s recommendations.

e.	System Training. Provide a four-hour session of training by a certified instructor to State personnel in the operation, setup and maintenance of the video detection system.  Provide instruction and materials for a maximum of 10 persons and conduct the training at a location determined by the Engineer.

f.	Service, and Support. Supplier, for the term of the Contract, from initial equipment installation through final acceptance Subsection 105-1.16, provide continuous software support, including updates of the MVP sensor, Terra Access Point, and supervisor computer applications.  Provide this same service to the Department after acceptance under a separate Contract.

Replace Subsection 740-2.16 PEDESTRIAN PUSH BUTTONS with the following:

740-2.16 PEDESTRIAN PUSH BUTTONS.  Push buttons shall be Tamper proof with a 2 inch minimum diameter convex 316 stainless steel actuator button.

Construct a weatherproof assembly designed to prevent an electrical shock under any weather condition and grounded per the NEC.

Push Button Switch. Furnish Polara model RBDLM2-B-4H or approved equal with the following features.  Provide a solid state electronic piezo type, switching unit, with screw type terminals, rated 15 amperes at 125 VAC.  Must have the following characteristics:

1.	Switching unit that is solid state electronic piezo rated for 100 million cycles.

2.	Sealed to prevent ice from impeding function.

3.	Must hold the call for a minimum of 5 seconds.

4.	Switch operating force of 3 pounds or less with no moving plunger or moving electrical contacts.

5.	Provide an LED indication and an audible tone or beep within the button when pushed.

6.	Must have a raised rim or ridges to protect the button from side impacts.

7.	Powder coated cast switch housing of dark olive green or black.

Where a pedestrian push button is to be mounted on top of a 2-1/2 inch diameter post, provide the housing with a slip-fitter with screws for securing to the post.

Factory finish pedestrian push button housings, mountings, brackets, and fittings with 2 coats of dull black enamel or powder coat.  Painting/powder coating is not required where the color is an integral part of the component material.

Replace Subsection 740-2.17 with the following:

740-2.17 FLASHING BEACONS.  Furnish beacons that consist of one or more traffic signal sections meeting the requirements of Subsection 740-2.14 Vehicular Signal Heads. See the Plans for the number, size and color of the signal sections required for each beacon.

Use the flasher in signal controller cabinets to energize beacons that flash continuously and are installed near traffic signals.  Otherwise, each flashing beacon controller assembly consists of the following 120 VAC equipment housed in a NEMA 3R enclosure:  a circuit breaker, a radio interference suppressor, a transient voltage suppressor, a NEMA Type 3 flasher, neutral and ground busses, and terminal blocks.

Controller assemblies for school zone speed limit sign beacons shall also include a time switch and a second 120 VAC circuit breaker that protects a thermostat and heater.

The NEMA 3R enclosure shall feature a single shelf and a hinged door with a hasp and staple for sealing and locking the cabinet door.

The radio interference and transient voltage suppressors shall meet the requirements of Subsections 740-2.11.1.k.(3) and (4), respectively.

Use a solid state NEMA Type 3 flasher meeting the requirements of NEMA Standard TS 1-1989, Traffic Control Systems.

Use 20 ampere, 600 volt barrier type phenolic terminal blocks with plated brass screw type terminals and integral strips can be marked with a pen or pencil.

Furnish an RTC Manufacturing model AP41-L time switch complete with wiring harness, or an approved, calendar programmable, solid state time switch with liquid crystal display, keyboard, input/output port, and wiring harness.  The approved time switch shall:

1.	Operate on line voltages from 95 to 135 VAC, operate in temperatures from -22 F to 165 F, and include a capacitor that provides 48 hours of backup power to retain programming and time when the unit is disconnected from AC voltage.

2.	Include a backlit display and provide 2 lines of alphanumeric legend with 16 characters per line.  The display shall automatically prompt the operator while programming the device through the keyboard for ease of use.

3.	Include an input/output port and keyboard activated special functions that transfer the program to other units and download the program to a printer for a hard copy record of the program.

4.	Automatically compensate for changes in Daylight Savings Time and leap years and include a keyboard activated special function to quickly change the dates for the begin and end of Daylight Savings Time.

5.	Provide at least 10 basic plans for daily and/or weekly use and at least 200 program steps that are equally divided amongst the actual number of basic plans.  Each program step shall be assignable to a single day, weekend, weekday, or every day.  The time switch shall also include 20 plans that activate the basic plans to provide one year of time based control.

6.	Include at least 4 single pole double throw, relay controlled outputs rated for 15 amperes of resistive load at 115 VAC.  Each pole shall be independently activated for steady on or momentary on and be manually switched on through the keyboard.

When a signal controller cabinet flasher is used to energize a beacon, furnish a two pole, fused block with built in fuse pullers to protect the flasher.  Furnish third party certified blocks that hold 13/32" x 1-1/2" midget ferrule fuses, are rated for 30 amperes, and feature tubular screw terminals that accommodate conductors to 8 AWG.  Furnish blocks with two fast acting, 3 ampere (BAF-3) fuses, and flat bases that can be directly mounted on a dead panel.

Replace Subsection 740-2.18 LUMINAIRES with the following:

740-2.18 ROADWAY LUMINAIRES.  Furnish luminaires that conform to the following specifications and provide the light distributions specified.  When luminaire performance criteria are specified, luminaires shall also:

	Meet or exceed the minimum initial light levels indicated.

	Provide light distribution uniformity ratios and veiling luminance ratios equal to or less than the maximums indicated.

When luminaire performance criteria are specified, submit the following information for each luminaire type and light distribution type specified:  luminaire specifications, the lumen output of the lamps that will be furnished, and current electronic photometric data to the Engineer for approval.  Furnish the photometric data in Illuminating Engineering Society (I.E.S.) format.  The Engineer will use software that calculates light levels and uniformity ratios according to the American National Standard Practice for Roadway Lighting, A.N.S.I./I.E.S. RP-8 to verify each luminaire provides the light levels, uniformities, and veiling luminance ratios specified.

When cut off distributions are specified, furnish luminaires with flat glass lenses and a full cutoff light distribution as defined in the American National Standard Practice for Roadway Lighting, A.N.S.I./I.E.S. RP-8, dated 2000.

Furnish each luminaire with a high pressure sodium lamp of the wattage specified and matching ballast with an input voltage equal to circuit voltage.  Furnish lamps that feature a rated life of 40,000 hours based on 10 hours per start and ballasts that conform to Subsection 740-2.21.

1.	Luminaries General

Install luminaires that feature:

a.	Corrosion resistant enclosures with gray paint finish and space for the ballast.

b.	Third party certification for use in wet locations.

c.	Glass lenses, unless polycarbonate resin refractors are specified.

d.	Terminal blocks for attaching the illumination tap conductors.

e.	Aluminum reflectors with an ALZAK or ALGLAS finish.

f.	Optical components free of substances that affect photometric performance, paint.

g.	Housings cast with no provision for a photoelectric control receptacle.

h.	Airtight reflector and lens units that breathe through activated charcoal filters and include elastomer gaskets to seal the gap between the two components.  Gasket material must withstand the temperatures involved and be securely held in place.

i.	Plug in starting aids in fixtures with lamps through 400 watts.

2.	Luminaries – Cobrahead and Offset

Each cobrahead or offset luminaire shall also include:

a.	An easily removed hinged door used exclusively for mounting the ballast.

b.	A second door that frames the lens, hinges on the house side, and fastens on the street side with an automatic type latch.

c.	A four bolt mounting brackets that fit 2 inch nominal diameter standard pipe and feature a center pivot for leveling the luminaire.

Offset luminaires shall also include knuckle style pole top adapters that are sized to fit 2 inch nominal diameter standard pipe and feature a wire way meeting NEC requirements for installing three size 10 AWG conductors between the pole and the terminal block located in the luminaire.

3.	LED Luminaire

LED Luminaires shall be UL listed for wet locations and enclosure classified IP66 per IEC 529.  The fixture shall be resistant to corrosion, ultraviolet degradation and abrasion.  Nickel-chrome plated wire guard shall be used for providing anti-fouling protection from leaf/debris and animals nesting to assure cool LED operation.

Average delivered lumens over 50,000 hours should be a minimum of 85% of initial delivered lumens.

The LEDs shall operate over the temperature range of -40 °F to +165 °F.  The LEDs shall be wired in series parallel strings.  The failure of many one LED, and its associated string of LEDs, shall not cause the loss of more than 20% of the light output of the complete LED module.

The luminaire and all of its components, for the term of the Contract, from initial installation through final acceptance 105-1.16, when directed, promptly replace failed equipment and repair failed workmanship.

4.	Lenses

When polycarbonate resin lenses are specified, the fabricator shall furnish certified lenses conforming to the following criteria:

a.	The lenses are molded in a single piece from virgin polycarbonate resin.

b.	The lenses are free from cracks, blisters, burns, and flow lines, and furnished with the natural molded surface.

c.	The lenses are of uniform density throughout and free from air, gas, or moisture pockets, and uncured areas.

d.	The lenses are transparent with a clear bluish tint, produced from ultraviolet stabilized resin to reduce the effects of ultraviolet radiation on their color properties.

e.	The resins used meet the requirements for the self extinguishing classification of ASTM D 635 and feature a minimum impact strength, Izod notched of 12 foot pounds per inch when tested according to ASTM D 256, Method A, using a 1/8 inch by 1/2 inch bar molded according to ASTM recommended practice.

Delete Subsection 740-2.20 ILLUMINATION CONTROL in its entirety.

Add Subsection 740-2.24 TRAFFIC SIGNAL COMMUNICATIONS SYSTEM:

740-2.24 TRAFFIC SIGNAL COMMUNICATIONS SYSTEM. Furnish only fully functioning new equipment of the brand and type listed or approved equal. To be considered an approved equal equipment must meet or exceed the listed specifications.  The products listed in this subsection are subject to review and approval if they are included on the Materials Certification List (MCL).

MASTER RADIO

Furnish fixed frequency licensed radios in the number and location shown on the plans.  The radios must be fully compatible with Econolite ASC/3-2100 traffic signal controllers and Econolite ASC/2M-1000 on-street master controllers. Furnish Microwave Data Systems model MDS-4790A radio or approved equal meeting the following requirements:

1.	Frequency Range: 330 to 512 MHz

2.	Tx/Rx Split: Simplex to 132 MHz

3.	Data Interface: RS-232 Female Connector, Supports: TXD, RXD, RTS, CTS, DCD, RUS, AUX4 PWER, DSR, and GND

4.	Frequency programmability; 5 KHz increments, 6.25 KHz increments any MAS channel pair

5.	Operational Modes: Asynchronous – Simplex, half-duplex, full-duplex

6.	Frequency Stability; +/- 0.00015% 1.5 ppm

7.	Transmitter Carrier Power; 0.1 to 5 Watts Programmable

8.	Transmitter Carrier Power Accuracy; Normal +/- 1.5 dB

9.	Transmitter Output Impedance; 50 Ohms

10.	Duty Cycle; Continuous

11.	Receiver Type; Double Conversion Superheterodyne

12.	Adjacent Channel (EIA): 60 dB nominal

13.	Primary Power; 100-240 VAC (50/60 Hz)

14.	Power Required: <60 Watts nominal

15.	Modem Modulation; Digital/CPFSK

16.	Latency (Rx-Tx-Rx): <10 ms including RTS/CTS delay

17.	Modem CTS Delay; 0-255 msec programmable in 1 msec increments

18.	Modem PTT Delay; 0-255 msec programmable in 1 msec increments

19.	Data Rate (rf): 9,600 bps

20.	Data Rate (data): 110 bps -38.4 kbps

21.	Bit Error Rate: BER 1X10^-6@-110 dBm typical

22.	Local Diagnostics: Included

23.	Dimensions; approximately (3.5" H x 14.3" W x 14.3" D) inches

24.	Maximum Weight; 19.8 lbs

25.	Front Panel: Detachable

26.	Mounting: Shelf or under shelf

27.	Temperature Range; -22 ˚F to +140 ˚F

28.	Agency Approvals; FCC Part 90 (150-174 MHz bands)

29.	Case; Die Steel

REMOTE RADIO (TRANSCEIVER)

Furnish fixed-frequency licensed radios in the number and location shown on the plans.  The radios must be fully compatible with Econolite ASC/3-2100 traffic signal controllers and Econolite ASC/2M-1000 on street master controllers. Furnish Microwave Data Systems model MDS-4710A radios or approved equal meeting the following requirements;

1.	Banding; 10 MHz blocks

2.	Frequency programmability; 5 KHz increments, 6.25 KHz increments any MAS channel pair

3.	Agency Approvals; FCC Part 90 (150-174 MHz bands)

4.	4 Wire Analog; Yes

5.	Date Rate: 9,600 bps

6.	Channel Spacing 25, 30 KHz

7.	Bit Error Rate; 1X10^-6@-110 dBm typical

8.	Diagnostics; Network Wide Diagnostic Option

9.	Operational Modes; Async –Simplex, half-duplex

10.	Data Interface; Rs-232, DB-25 female connector

11.	Supports; TXD, RXD, RTS, CTS, DCD, RUS, AUX POWER, DSR and GND

12.	Transmitter Carrier Power; 0.1 to 5 Watts Programmable

13.	Transmitter Duty Cycle; Continuous

14.	Transmitter Output Impedance; 50 Ohms

15.	Transmitter Frequency Stability; +/- 0.00015% 1.5 ppm

16.	Transmitter Carrier Power Accuracy; Normal +/- 1.5 dB

17.	Receiver Type; Double Conversion Superheterodyne

18.	Receiver Frequency Stability; +/- 0.00015% 1.5 ppm

19.	Primary Power; Voltage 13.8 Vdc nominal

20.	Tx Current; 2A Typical at 5 Watts

21.	Rx Current; less than 125 mA

22.	Modem Modulation; Digital/CPFSK

23.	Modem CTS Delay; 0-255 msec programmable in 1 msec increments

24.	Modem PTT Delay; 0-255 msec programmable in 1 msec increments

25.	Temperature Range; -22 ˚F to +140 ˚F

26.	Case; Die Cast Aluminum

27.	Dimensions; approximately 2 x 6 x 7.5 inches

28.	Weight; maximum 2.5 lbs

ANTENNAS & CABLE

OMNI Antenna: Furnish Radio Frequency Systems model 458-2N Storm Chief, OMNI antenna or approved equal meeting the following requirements:

1.	Frequency Range: 450-470 MHz

2.	Gain: 8 dBd gain

3.	Vertical Beam Width: 12 degrees

4.	Height: 13.3 feet

5.	Weight: 10 pounds maximum

6.	Power Rating: 250 Watts

7.	Lightening Protection: Included

8.	Wind Loading: 100 mph

9.	Construction: White fiberglass

YAGI Antenna: Furnish antenna model 4506 YAGI or approved equal meeting the following requirements:

1.	Frequency Range: 450-470 MHz

2.	Bandwidth VSWR 1.5 400 MHz: >38 MHz

3.	Gain: 10.2 dBd minimum

4.	Front to Back Ratio: >15 dB

5.	Elements: 6 minimum

6.	Power Rating: 150 Watts

7.	Lightening Protection: Included

8.	Wind Loading: 200 mph, 110 mph with 0.5" radial ice

9.	Construction: Gold anodized aluminum

Antenna Cable: Furnish coaxial antenna cable Andrew LDF4-50A or approved equal meeting the following requirements:

1.	Jacket Material: PE

2.	Dielectric Material Foam PE

3.	Inner Conductor Material: Copper-clad aluminum wire

4.	Jacket Color: Black

5.	Outer Conductor Material: Corrugated copper

6.	Nominal Diameter: 0.5"

7.	Cable Weight: 0.15 lb/ft

8.	Diameter Over Dielectric: 0.510

9.	Diameter Over Jacket: 0.630"

10.	Inner Conductor OD: 0.190"

11.	Outer Conductor OD: 0.550"

12.	Cable Impedance: 50 ohm +/- 1 ohm

13.	Capacitance: 23 pF/ft

14.	DC Resistance, Inner Conductor: 1.480 ohms/kft

15.	DC Resistance, Outer Conductor: 0.580 ohms/kft

16.	DC Test Voltage: 4000 V

17.	Inductance: 0.058 uH/ft

18.	Insulation Resistance: 100000 MOhm

19.	Jacket Spark Test Voltage (rms): 8000 V

20.	Operating Frequency Band: 1-8800 MHz

21.	Peak Power: 40.0 kW

22.	Pulse Reflection: 0.5%

23.	Velocity 88%

24.	Operating Temperature: -67 to +185 degrees Fahrenheit

25.	Attenuation at 450 MHz: 1.447 dB/100 ft

26.	Average Power at 450 MHz: 1.61 kW

27.	Bending Moment: 2.8 ft lb

28.	Flat Plate Crush Strength: 110.0 lb/in

29.	Minimum Bend Radius, Multiple Bends: 5.00"

30.	Minimum Bend Radius, Single Bend: 2.00"

31.	Number of Bends, Minimum: 15

32.	Number of Bends, Typical: 50

33.	Tensile Strength: 250 lb

ON-STREET MASTER CONTROLLER

Furnish Econolite ASC/2M-1000 on street master controller unit or approved equal meeting the following requirements:

1.	Enclosure

a.	The system master shall be compact so as to fit in limited cabinet space. It shall be installable on a shelf that is not more than 7" deep.  External dimensions shall not be larger than 9" x 15" x 9-1/2" (H x W x D).

b.	The enclosure shall be constructed of sheet aluminum and shall be finished with an attractive and durable protective coating.  Model, serial number, and program information shall be permanently displayed on the top surface.

c.	The enclosure shall open along a vertical stainless steel hinge so as to provide ready access to the electronics in case of need for service.

2.	Electronics

a.	The electronics shall be modular and shall consist of vertical circuit boards.  Horizontal circuit cards shall not be acceptable.

b.	A microprocessor shall be used for timing and control functions. Continuing operation of the microprocessor shall be verified by an independent monitor circuit, which shall set an output to FALSE and indicate an error message if a pulse is not received from the microprocessor within a selectable period.

c.	In the interest of reliability, sockets shall only be used for components with 20 pins or more.

d.	A built in, high efficiency switching power supply shall generate required internal voltages as well as 24 VDC output.  Voltages regulated and monitored with control signals.  Fuses mounted on the front of the system master for 120 VAC input and 24 VDC output.

e.	Timing of the system master shall be derived from the 120 VAC power line.  A 5 year lithium battery shall maintain the time of day clock and digital data during a power outage lasting up to 30 days. Lead acid, nickel-cadmium, or alkaline batteries shall not be acceptable.

f.	User programmed settings shall be stored in an electrically erasable programmable read-only memory (EEPROM).  Designs using a battery to maintain user data shall not be acceptable.

g.	To facilitate the transfer of data from one system master to another, the EEPROM shall be mounted on an easily removable submodule that is to connected to the processor module via a DIN printed circuit board connector.

h.	Printed circuit boards meet the requirements of the NEMA Standard plus the following requirements to enhance reliability:

(1)	Plated through holes and exposed circuit traces plated with solder.

(2)	Both sides of the printed circuit board covered with a solder mask material.

(3)	The circuit reference designation for components and the polarity of capacitors and diodes clearly marked adjacent to the component.  Pin 1 for integrated circuit packages designated on both sides of printed circuit boards.

(4)	Electrical mating surfaces gold plated.

(5)	Printed circuit board assemblies, except power supplies, coated on both sides with a clear moisture proof and fungus proof sealant.

3.	Front Panel and Connectors

a.	The front of the system master consists of a panel for the display and keyboard plus a separate panel for the connectors.

b.	A 16 line by 40 character/line alphanumeric liquid crystal display (LCD) shall show program and status information.  The display area having nominal measurements of 2 1/2" x 4 1/2" (H x W) or larger.  For ease of viewing, provide backlighting by light emitting diodes and multiple levels of contrast adjustment.

c.	Front panel operator inputs clearly labeled and environmentally sealed elastomeric keys.  These shall include a 10 digit numeric keypad, ten function keys, an oversize ENTER key, and an oversize four-arrow cursor control key.

d.	Eight of the function keys shall be labeled F1 through F8 and provide the following functions:

F1 -	Main Menu-Pressing the F1 key shall display the main menu.

F2 -	Next Screen-Pressing the F2 key shall display the next screen, thus allowing rapid advancement from screen to screen.

F3 -	Sub Menu-Pressing the F3 key from any data screen shall display the current sub-menu.

F4 -	Next Data-Pressing the F4 key shall search for the first non-zero data field, thus allowing rapid search for valid entries.

F5 -	Display Adjust-Pressing the F5 key shall adjust the contrast of the display.

F6 -	Next Page-Pressing the F6 key shall advance to the previous or next group of data entry screens in a submenu.

F7 -	Status Display-Pressing the F7 key shall present the status display.

F8 -	Help-Pressing the F8 key at any data entry field shall display a help screen about that field.

Special Function. A key marked "special function" shall be provided to lock out data changes if an access code is present and to enter hexadecimal characters.

Clear. A key marked "clear" shall be provided to abort a data entry and restore the current value.

4.	Telemetry

a.	Up to two channels of telemetry, utilizing time division multiplex/frequency shift keying (TDM/FSK) techniques shall be provided depending on system requirements.

b.	The modems for each channel shall provide full duplex communications over four wire Type 3002 telephone lines between the system master and local controllers.

c.	The transmitter digital to FSK modulator.  A digital HIGH resulting in a frequency of 2200 Hz, and a digital LOW shall result in a frequency of 1200 Hz.  At the point of frequency shift, the signal phased coherent. The nominal output level shall be 0 dBm into a 600 ohm load.

d.	The receiver - an FSK to digital demodulator.  The receiver will receive a frequency of 2200 Hz resulting in a digital HIGH, and a frequency of 1200 Hz resulting in a digital LOW.  The receiver sensitivity will be set at -34 dBm and adjustable from -40 to +6 dBm.

5.	Serviceability

a.	Electronic modules other than the power supply easily removable from the front of the system master using a standard screwdriver as the only tool. Power and signal connections to the circuit boards though plug in connectors.

b.	The system master layout allows the removal and replacement of any circuit board without unplugging or removing other circuit boards.  Boards keyed to prevent improper installation.  No more than two boards attached together to form a circuit assembly.  Attaching hardware uses captive screws or 1/4 turn fasteners to secure circuit assemblies to the enclosure.

c.	The system master enclosure allows complete disassembly using a standard screwdriver.  Design the enclosure so that one side of any circuit board is completely accessible for troubleshooting and testing while the unit is still in operation.  This capability accomplished without the use of extender cards or card pullers.

6.	Functional Operation

a.	The system master controls the operation of a traffic system or zone containing up to 24 intersections by specifying the operation of the intersection controllers based on processed detector data, time of day/day of week/ week of year scheduling, manual operator selection, or external commands.

b.	The control signals consists of traffic plans that specify a coordination program that commands one of six cycle lengths, one of five offsets, one of four splits; system free; or zone plan, and up to four special functions.

c.	The system master shall provide for a communication link to a monitor computer to upload/download controller data bases, to transfer events and detector data for storage, and to provide data on a one second basis for real time displays.

d.	There are optional capabilities for telemetry interconnect and for a remote or local data terminal.

7.	Program Selection

a.	The default program in effect selected on a priority basis.  Priorities as follows:

(1)	Manual entry from keyboard

(2)	External command from a master

(3)	Time-of-day/day-of-week schedule

(4)	Traffic responsive

b.	Manual entry from the keyboard shall override programs from other sources.  Used as the default when automatic selection fails and time of day/day of week backup is not enabled.

c.	Provision made for program commands from an external master.  The external command inputs usable for crossing artery synchronization.

8.	Time-of-day/day-of-week programming

a.	Up to 150 program steps shall be available for time of day/day of week (TOD) scheduling.  Up to 16 TOD programs possible.  The TOD programs scheduled to repeat by assignment to the week of year and day of week and special TOD programs assignable by month and day on a one time or repeating basis for implementing holiday programs or special events.

b.	TOD program selection or special function scheduling enabled separately for override of traffic responsive commands.  Program makes it possible to enable a traffic responsive default function that allows TOD operation to take effect only if the traffic responsive operation fails.

c.	TOD operation controlled by a calendar and clock that compensates automatically for leap year and daylight savings time (if enabled).  Each TOD program step shall consist of the following:

(1)	Program number.

(2)	Begin time (hour and minute).

(3)	Traffic plan consisting of cycle, offset and split; system free; or zone plan command (see 5.9).

(4)	Enable special functions.

(5)	Enable maintenance call operation.

(6)	Enable traffic responsive operation.

(7)	Auto program override (if cycle length is higher).

(8)	Command non-interconnected coordination operation.

(9)	Enable crossing artery synchronization.

(10)	Specify sample period for traffic responsive plan.

(11)	System detector log interval.

(12)	Sample period log interval.

d.	Power OFF for longer than the capability of the power down timer inhibits TOD operation.  TOD operation enabled when time is updated.

9.	Traffic Responsive Programming

a.	Traffic plan selection in the traffic responsive mode performed at user specified intervals.  The plan selection interval specified in minutes or cycles.

b.	Raw sensor data consisting of volume counts and presence measurement from up to 32 detectors processed into scaled volume and scaled occupancy traffic parameter values for use in traffic responsive plan selection.  The volume and occupancy scale factors specified for each detector and also for the system.  If individual values are not specified, use the system value.

c.	The sensors assignable to eight detector groups, each of which shall contain up to four detectors.  A minimum number of operable detectors required for valid operation user specified.  Each group of detectors assignable to any combination of the following functions:

(1)	Level selection

(2)	Direction 1 traffic

(3)	Direction 2 traffic

(4)	Split demand A

(5)	Split demand B

(6)	Arterial demand

(7)	Nonarterial demand

d.	For each detector group assignment, the user is able to specify that the highest, second highest or average of scaled sensor data is used as the detector group output.  The output parameter of each detector group includes volume, occupancy, or concentration (which is the higher of volume or occupancy).

e.	The data processing of the detector group outputs assigned to each function specified as follows:

(1)	Parameter (volume, occupancy, or concentration).

(2)	Highest, second highest, or average output of the detector groups assigned to the function.

(3)	Factor used in a first order smoothing algorithm.

(4)	Update predictor value that will bypass data smoothing for a predetermined increase.

f.	Computed level determined by comparing the processed level selection detector group outputs to user specified threshold values.  Provision made for determining up to five computed levels.  The threshold values between adjacent levels overlap to provide a hysteresis effect to minimize oscillation.  It is possible to inhibit access to higher levels by entering an out of range threshold value.

g.	Arterial directional preference determined by computing the difference between the processed direction 1 data and direction 2 data.  Computed offset determined by comparing the arterial directional values to user specified threshold values.  The computed offset either the direction 1 preference, direction 2 preference, or average.  The threshold values between adjacent computed offsets shall overlap to provide a hysteresis effect to minimize oscillation.

h.	Based on computed level and computed offset, one of fifteen traffic plans selected.  Traffic plans provided for one of the following:

A coordination plan consisting of:

(1)	One of six cycle lengths

(2)	One of five offsets

(3)	One of four splits or four computed split/special function programs

(4)	System free

(5)	Zone plan command

(6)	Up to four special functions shall be available for each traffic plan.

i.	Zone plan commands 1 through 32 from the master selecting command programs 1 through 32 at each intersection controller.  Make it possible to group intersections as necessary for traffic patterns providing multiple subzone coordination or independent operation within a zone.  As an example, zone plan command 1 able to specify the following zone operation:

(1)	Intersection 1 through 8, command program 1 calling for cycle 2, offset 3, and split 1.

(2)	Intersection 9 through 16, command program 1 calling for cycle 3, offset 2, and split 2.

(3)	Intersection 17 through 20, command program 1 calling for free mode.

j.	If, due to failed detectors or improper data entries, the computed level or computed offset cannot be determined, the previously selected traffic responsive plan shall be retained for a period specified by the operator.  A default traffic plan will be available for use if valid computed level and offset have not been determined before the expiration of the retention period.

k.	The default plan selected from one of three sources as determined by operator entries.

(1)	TOD scheduling used if traffic responsive backup is enabled.

(2)	Manual plan.

(3)	System free.

l.	Computed split/special function program determined by computing the difference between the processed split demand B data and split demand A data.  One of four programs consisting of one of four splits and any special function selected by comparing the difference to user specified values.  The threshold values between adjacent splits overlaps to provide a hysteresis effect.

m.	Five additional traffic plans shall be selectable based on computed level and nonarterial preference.  A nonarterial preference ratio determined by computing the difference between the processed nonarterial demand data and arterial demand data.  Either arterial or nonarterial preference selected by comparing the difference to user specified threshold values.  The threshold values overlap to provide a hysteresis effect.  It is possible to specify that any of the nonarterial traffic plans defer to the arterial plans at the same computed level.

10.	Crossing Arterial Synchronization

a.	Provision made for crossing arterial synchronization in two independent system masters. Synchronization established through the common intersection of both systems in order to maintain simultaneous, coordinated traffic flow along each of the arterials.

b.	Crossing arterial synchronization enabled by the time of day scheduler and occur when the traffic pattern commanded by each of the system masters has the same cycle information.

c.	Crossing arterial synchronization enabled as long as both system master cycle commands are the same and remain in effect for as long as traffic demand warrants this mode.  To prevent oscillation, it is possible to "lock in" this mode for a user programmable period from 0-30 cycles.

11.	Power Fail Restart

A second set to provide for diagnostic values specified for each system detector individually.  The individual value used if it is longer than the system diagnostic interval. When no individual value is specified for a system detector test, use the system diagnostic value.

a.	The system detector diagnostic tests shall be as follows:

(1)	No Activity.  Two intervals from 0 to 255 minutes between vehicle counts settable by time of day for no-activity diagnostics on a system basis.  A diagnostic interval begins each time a vehicle count occurs.  If a vehicle count is not received during the diagnostic interval, the detector fails.  No activity diagnostics is inhibited if the volume from a majority of unfailed system detectors is below a system specified threshold value from 0 to 255 counts per minute.

(2)	Maximum Presence.  An interval from 0 to 30 minutes specified for maximum presence diagnostics.  Continuous detectors call for the diagnostic interval causing the detector to be failed.

(3)	Minimum Presence.  An interval from 0 to 15 minutes and a minimum average presence time from 0 to 30 occupancy counts, where each count is 16 2/3 milliseconds, is specified for minimum presence diagnostics.  A detector fails if the occupancy per vehicle count averaged over a one minute period is less than the specified average presence time for the diagnostic interval.

(4)	Excessive Counts.  A diagnostic count from 0 to 180 counts per minute and diagnostic interval from 0 to 30 consecutive minutes specified.  If the detector count is equal to or greater than the diagnostic count for the diagnostic interval the detector shall be failed.

b.	Speed trap detector status tested for no activity.  If a speed trap readback does not contain a speed for the current no activity period, the speed trap fails.

c.	Failed detectors automatically return to service if no failure condition exists for a 0 to 15 minute detector recovery interval.

d.	Provide a display showing diagnostic status for system detectors.  The diagnostic status of four system detectors displayed simultaneously. Displayed information for each system detector includes: enable, telemetry, no activity, max presence, min presence, and excessive counts.

12.	Telemetry Diagnostics

a.	Diagnostics required for systems having optional telemetry interconnect. The diagnostics shall monitor readback for no response conditions. Includes channel diagnostics and local telemetry.

(1)	Channel.  A transceiver failure detected if a telemetry channel is enabled, but no telemetry module is present.  A loop failure detected when no readback is received on a telemetry channel for 3 seconds. The telemetry channel automatically returned to service and the status of devices connected to the channel cleared when readback are received for 3 consecutive seconds following either failure.

(2)	Local Telemetry.  A local telemetry failure detected when a device has not responded with a valid readback for 5 consecutive seconds.  This failure identified with controllers and system detectors only.  The device automatically returned to service and the device status cleared when valid readback have been received for 5 consecutive seconds following a local telemetry failure.

b.	A diagnostic display showing enable status, loop error and transceiver error for two channels simultaneously provided.

13.	Intersection Diagnostics

Diagnostics provided for intersections with telemetry interconnect.  Intersection status conditions available for diagnostic display and logging.

a.	Controller readback provided data for determining the following intersection conditions:

(1)	Conflict Flash.  A minimum flash interval from 0 to 30 seconds specified.  If an intersection readback indicates a CMU flash for a period in excess of the minimum flash interval, the intersection fails and the intersection status indicates a conflict flash condition.

(2)	Local Flash.  If an intersection readback indicates flash, CMU flash is OFF, and flash is not commanded from the master, the intersection status indicates a local flash condition and the intersection considered off line.

(3)	Commanded Flash.  If an intersection readback indicates flash, CMU flash is OFF, and flash is commanded from the master, the intersection status shall indicates a commanded flash condition and the intersection considered off-line.

(4)	Maintenance Required.  If an intersection readback indicates a maintenance required condition, the intersection fails and the intersection's status indicates a maintenance required condition.

(5)	Cycle Fail.  If the readback from a coordinated intersection indicates that a sum check is present and there has not been a phase change for two cycles if coordinated or three minutes if noncoordinated, the intersection fails and the intersection status indicates a cycle fail condition.

(6)	Coordination Alarm.  If an intersection readback indicates a coordination alarm, the intersection fails and the intersection status indicates a coordination alarm condition.

(7)	Local Free, Commanded Free, Coordination Error, or Preempt.  If an intersection readback indicates any of these conditions, the intersection status indicates the condition and the intersection considered off-line.

(8)	On-line.  When a failure or off-line condition is removed, the indication removes from the intersection status, and the intersection is recorded on-line if no other failure or off-line condition is present.

b.	Supplemental status readback provides data for determining the following local vehicle detector conditions:

(1)	No Activity. - Same as for the system detector, except that no individual detector value is specified.

(2)	Max Presence. - Same as for the system detector.

c.	Supplemental status readback indicates when a minimum of two user-defined alarms go On or OFF.  The alarm condition indicated in the intersection status.

d.	Provides a display showing diagnostic status for intersections.  The diagnostic status for a minimum of four intersections displayed simultaneously.  Displayed information for each intersection includes: enable, telemetry, cycle fail, CMU flash, maintenance required, coordination alarm, alarm 1, and alarm 2.

14.	System Management

a.	Provision made for keyboard control of the following system management functions that deal with system configuration, operational status, and status monitoring:

(1)	Add/delete telemetry connected controllers

(2)	Add/delete telemetry connected system detectors

(3)	Alter telemetry channel command sequence

(4)	Enable/disable telemetry channel

(5)	Enable/disable controller

(6)	Enable/disable system detector

b.	Provision made for status displays of the following categories:

(1)	General status.  Displaying master number, time of day, date, day of week, program in effect, cycle countdown, special function, time of day interval and plan, and overall diagnostic status.  In addition, displays plan and selected cycle length of manual, external, time of day, and traffic responsive plans.

(2)	System detector current.  Displays actual and scaled volume and occupancy for system detectors in groups of eight.

(3)	Sample period results.  Displays current plan selected by traffic responsive calculations.

Intermediate results also displayed including the eight detector group computed values.

(4)	Controller status.  Shall display information retrieved from intersection controllers through telemetry channels.  Current phase 1 - 8 green, vehicle detector 1 - 8 status, overlap A-D green, and alarm status shall be displayed on one screen.

(5)	Detector presence and speed traps.  Display system detectors 1 - 32 actuation status and speed traps 1 - 8 speed on one screen.

15.	Event Recording

a.	An event recording function provided for the occurrence of events relating to system operation.  Events include the following:

(1)	Program and mode changes

(2)	Device diagnostics

(3)	System events

b.	Events recorded as occurred.  It shall be possible to enable/disable any event and to assign event priorities to control automatic reporting to a monitor computer on the following basis:

(1)	Priority 1.  Reports immediately

(2)	Priority 2.  Reports after 0 - 255 minute delay

(3)	Priority 3.  Reports with higher-priority reports

c.	An event buffer provided for 250 events.  Include provision for the event buffer to be printed out on command and for the event buffer to be cleared.

d.	Event messages include the master number, event priority, date and time, a brief description of the event, and identification of the system device if applicable.

e.	Information recorded as follows for program or mode change events that may occur automatically as a result of traffic computations, on a TOD scheduled basis, or due to a manual or external command:

(1)	In-effect program change Program source

(2)	Program cycle, offset, split and cycle length

(3)	Traffic responsive program change Computed selection parameters level, offset, split

(4)	Nonarterial preference

(5)	Program cycle, offset, and split

(6)	Special function change source

(7)	Special function number with ON/OFF status

(8)	Time of day program step change TOD program step number

(9)	Intersection mode change Intersection no. Change source Intersection mode number with ON/OFF status

f.	Device diagnostics previously defined shall be continuously executed and be recorded as events occur.

g.	System events include the following:

(1)	Power Off.  A power OFF event recorded when power is removed. The event message shall be printed out when power is restored.  Date, time, and traffic responsive program is preserved in memory for a minimum of 30 days during power OFF.  A 72 hour power down timer enabled when loss of power is detected so that the day and time may be corrected when power is restored.

(2)	Power On.  A power ON message indicates the time power was restored.  The date and time corrected if power has been off less than 72 hours.

(3)	Power Interrupt.  A power interrupt event indicates that power was off for less than 0.75 seconds.

(4)	Clock Error.  A clock error message indicates the date and time is incorrect.  This event occurs at initial power ON before the date and time is set and if power has been OFF in excess of 72 hours.  A clock error shall inhibit TOD operation.

h.	Telephone number entry programmable to allow event reporting to a monitor computer and another telephone number programmable to report device failures or optionally priority 1 events to a separate maintenance computer or to a terminal.  Event reports to a maintenance computer or terminal done only when scheduled by a TOD entry.  If the monitor computer, maintenance computer or terminal is busy or off line, a reporting system master repeatedly attempts to call at a user programmable retry interval.

16.	Logs and Reports

a.	Logs and reports generated in response to operator requests.  The reports consist of the following:

(1)	Current status

(2)	System detector log

(3)	Speed log

(4)	Sample period log

(5)	Detector buffer data

b.	Current status reports available for request by the operator on a one time basis. The following status reports shall be provided:

(1)	Zone status consisting of:

(a)	Program in effect and source

(b)	Auto program (if not program in effect)

(c)	Special function status

(d)	Intersection mode

(2)	Telemetry channel status:

(a)	On line/Off line/Failed

(3)	Controller status:

(a)	On line/Off line/Failed

(4)	System detector status:

(a)	On line/Off line/Failed

(5)	Local detector status:

(a)	Failed

(b)	Summary of currently failed controllers and failure cause

(c)	Summary of currently failed system detectors and failure cause

(d)	Current 15 minute system detector log

(e)	Contents of event buffer

c.	System detector logs available for system detectors.  The logs present actual volume, actual occupancy and computed speed.  The logging interval selectable options 15, 30, or 60 minutes as scheduled by the TOD entries.  The operator is able to enable or disable the log without affecting the previous selections.  Possible to specify that speed be computed in miles per hour or kilometers per hour.  The log reported to the monitor computer on a real time basis.

d.	A speed log tabulated in three speed bands the number of vehicles detected by each speed trap assigned to log.  Up to 8 speed traps independently specified as a measure of effectiveness (using nominal progression speed for each active cycle and offset program as a reference) or as a programmable speed band.  The measure of effectiveness method providing a speed offset below and a speed offset above the nominal speed for establishing speed bands, whereas the programmable speed band method provide two independent speeds to define three speed bands.  The logging interval the same as for system detector logs and shall report to the monitor computer on a real time basis.

e.	A sample period log available to allow the user to evaluate traffic responsive system control.  Make it possible for the operator to adjust detector scale factors, computational parameters, smoothing factors and thresholds, and to monitor the resultant effect on program selection.  Possible for the operator to specify the log printout on a multiple of sample periods from 1 to 15 as scheduled by TOD entries; or, alternatively to print out the sample period log when a change occurs to computed level, offset, split or nonarterial preference.  The operator is able to enable or disable the log without affecting previous selections.  The sample period log consists of the following parameters:

(1)	Scaled volume and occupancy from enabled system detectors

(2)	Volume for each detector group

(3)	Occupancy for each detector group

(4)	Concentration for each detector group

(5)	Current value of each program selection function

(6)	Smoothed value of each program selection function

(7)	Computed program selection parameters

(8)	Selected auto program

(9)	In effect program and cycle length

f.	The sample period log reported to the monitor computer on a real time basis.

g.	A user enabled log buffer shall accumulate data from enabled system detectors and speed traps for each logging interval.  Contents of the log buffer shall be transferred at 6, 12 or 24 hour intervals to the monitor computer for storage.  A separate telephone number provided for calling the monitor computer via an external modem using the dial up telephone network.  This telephone number shall also be used for real time log.

GPS TIME REFERENCE

1.	GPS

Furnish Econolite model GPS-100.

a.	Requirements

GPS time reference or approved equal meeting the following requirements:

(1)	Operating temperature range: TS2 temperature range

(2)	LED indication: 4 satellite lock

(3)	LED indication: synchronization fault when no satellites have been detected for 12-hours

(4)	Pinout: Pin 5 = Ground, Pin 7 = Voltage in, Pin 8 = IPPD (Pulse per Day), Pin 9 = Isolated ground

(5)	Sync Pulse Duration: 1000 ms

(6)	Sync Pulse Amplitude: Source Voltage

(7)	Serial Interface: DB 9 @ 9600-8-N-1

(8)	Embedded menu program: access via Hyperterminal

(9)	Displays: for current status of GPS data and satellites

(10)	Firmware Updates: Available through software interface

(11)	Time Reset Signal: User variable, Default = 03:30:00

(12)	Antenna Gain: 27 dB

(13)	Operating Voltage: 3 - 5 V

(14)	Antenna mounting: cabinet top (hardware included)

(15)	Antenna Dimensions: 2.2 inch diameter x 0.5 inches H

(16)	Data Updates: GPS data sent once per second via serial port

b.	Additional Features

(1)	Ability to act as stand-alone unit or integrate to traffic cabinet controls

(2)	Automatic adjustments for DST and time zone

(3)	DIP switch selectable settings stored in nonvolatile memory

(4)	DIP switch selectable settings stored in nonvolatile memory

CR740.3-050118