SECTION 707

METAL PIPE

Special Provisions

707-2.03 CORRUGATED ALUMINUM ALLOY CULVERT PIPE AND UNDERDRAINS. Add the following:

The Corrugated Aluminum Pipe Arch shall have 3” x 1” corrugations.

707-2.05 DUCTILE IRON PIPE FOR WATER AND SANITARY SEWER.  Delete this Subsection in its entirety and substitute the following:

- Ductile iron pipe (DIP)	Class 52 rubber gasketed bell-and-spigot joint pipe per AWWA C151, with cement mortar lining per AWWA C104.

DIP mechanical joint fittings	350 psi pressure rating per AWWA C153, with cement mortar lining per AWWA C104.

DIP restraining mechanical joint	350 psi pressure rating, UL listed, ASTM

retainer glands 	A536-80, multiple thrust-restraint wedge design with twist-off nuts for correct torquing, “EBAA MegaLug”, “Romac Roma-Grip” or Engineer accepted equal.

DIP mechanical joint bolt-through	350 psi pressure rating, ASTM 536-80,

positive restraint mechanism	“Foster Adapter” or Engineer accepted equal.

DIP standard rubber gaskets	AWWA C111

DIP field lock gaskets	350 psi pressure rating per AWWA C111, meeting the requirements of NSF Standard 61, UL listed, rubber with multiple vulcanized stainless steel locking segments, all subject to Engineer’s acceptance.

Polyethylene encasement material	8 mils thick, conforming to AWWA C105.

- 707-2.06 SERVICE PIPE.  Delete Item 2, Steel Pipe in its entirety.

707-2.07 GALVANIZED STEEL WATER CONDUIT.  Delete this Subsection in its entirety.