Add the following Section:

- SECTION 681

- ELECTRICAL POWER RELOCATION

Special Provisions

    - DESCRIPTION.  The Contractor shall be responsible for furnishing all labor, equipment, and materials (other than listed on the Owner Furnished Materials Listing) necessary to construct electrical duct banks (both concrete encased and direct buried), junction boxes, switching cabinet pads, fiberglass pedestals, transformer pads and associated electrical grounding for Homer Electric Association (HEA).  The electrical duct banks will consist of multiple conduits of the number and size shown on the staking sheets and plans.  Upon completion and acceptance of the duct system, HEA will provide and install the electrical power cable, switching cabinets transformers, and other electrical equipment.  HEA will remove the existing aerial facilities including the existing poles. The utility staking sheets and details are included for the Contractor’s information.

The Contractor shall also provide as-built drawings in accordance with the conditions prescribed herein.

The Contractor doing this work shall be a licensed electrical contractor licensed by the State of Alaska, must be approved by HEA, and must have an employee on staff who possesses an Electrical Administrators license in the Outside Linework category. The Contractor shall also be on HEA’s pre-qualified Contractor list at the time of bidding.  The Contractor’s work will be closely inspected by HEA with their instructions relayed to the Contractor through the Engineer.  The HEA representative will be assigned for the entire underground installation, and no work shall proceed without him on site.  The Contractor shall advise HEA in writing at least 24 hours in advance of his actual duct system work indicating both location and time.

    - MATERIALS.  Owner furnished materials (all conduit, PVC and RMC sweeps, conduit plugs, concrete pads, fiberglass pedestals, ground rods, and misc. materials shown on the material issue ticket) will be available for the Contractor to pick up during regular HEA working hours, at the HEA yard located at 3977 Lake Drive in Homer, Alaska.  The Contractor shall be responsible for all handling, loading, and transportation to the jobsite.

Within five (5) days of receipt of Notice-to-Proceed, the Contractor shall determine his material take-off requirements and shall prepare a complete itemized list of materials for submittal to HEA.  The materials will be staged for pickup at the agreed upon time, based on submittal of a material list four (4) calendar days prior.  Materials shall be picked up for the complete project and not on an as needed basis.  Materials will be loaded on the Contractor’s vehicle by others at no cost to the Contractor.  The Contractor shall sign for materials at the time of receipt.

HEA’s warehouse foreman will be available for material issuance between the hours of 9:00 AM to 11:30 AM and 1:00 PM to 3:30 PM daily except Saturdays, Sundays, and legal holidays.  HEA will require a minimum of 24 hours notice prior to pickup; the Contractor should contact HEA at (907) 235-8551.  Where it is necessary to open the warehouse for the Contractor’s convenience and to procure special issuing of material other than during these normal working periods, the Contractor will be billed for the loaded labor rate time involved plus 25 percent handling overhead.  Storage and safekeeping of all materials after pickup from HEA shall be the Contractor’s responsibility.  All unused materials will be returned to the warehouse upon completion of the project.

The duct banks will consist of rigid steel conduit (RSC) and/or Schedule 40 rigid polyvinyl chloride (PVC) conduit.  RSC or Schedule 40 PVC conduit shall be used for all duct banks.  RSC conduit shall be manufactured of mild steel with a galvanized coating.  Conduit locator plates shall be supplied by the Contractor and be standard materials for locating the ends of buried conduits when not brought above ground.  All conduits shall have a pull line installed. All open conduit ends shall be plugged with blank duct plugs equipped with means of securing pull line to the back plate of the plug.

Concrete encased duct bank shall be installed where so dictated in the plans.  For all concrete encased duct bank sections the cement shall be a recognized standard brand Portland Cement contained in 42.6-kg sacks or 170.4-kg barrels bearing the manufacturers name.  The cement shall conform to the AASHTO M-85. The concrete mix shall be designed to produce a plastic and workable mixture, and a compressive strength at 28 days of at least 17237 kPa.  Only pre-mix concrete will be allowed.

    - APPLICABLE STANDARDS AND CODES.  In order to resolve any questions on safety regulations, installation practices, and testing procedures, the Contractor shall consult and make himself familiar with the applicable parts of the current editions of the following standards and codes:

- Alaska State Safety Code

- Homer Electric Association Safety Code

- Arctic and Sub Arctic Construction - Utilities, US Army Corps of Engineers

- Alaska State Safety Code

- National Electrical Code

- National Electrical Safety Code

- National Electrical Manufacturers Association

- Occupational Safety Health Act

- Underwriters Laboratories

All equipment and material furnished under this Section shall conform to the latest applicable specifications and rules of the National Electrical Manufacturers Association, American Standards Association, Institute of Electrical and Electronic Engineers and the Federal Specifications cited hereinafter.  As appropriate, all materials used shall be listed on the latest "List of Material Acceptable for Use on Systems of RUS Electrification Borrowers", and approved for this electrical system by HEA.

All materials furnished shall be standard equipment and be of the manufacturer’s latest design.  These materials shall be new, and not used, manufacturer’s seconds or rejects.  Where two or more units of the same class of material are required, they shall be like products of the same manufacturer.

    - VERIFICATION OF DIMENSIONS.  The exactness of dimensions given on any HEA drawing is not guaranteed, and therefore the Contractor shall field verify the accuracy of all dimensions.  In all cases of interrelation with other work, he shall verify in the field all the dimensions relating to the contiguous work.  Any errors due to the Contractor’s failure to verify shall be rectified promptly at the Contractor’s cost.

    - GENERAL CONSTRUCTION REQUIREMENTS.  HEA, through the Engineer, reserves the right to suspend the electrical duct bank installation at any time that the Contractor fails to meet the requirements set forth herein until such time as the Contractor makes the necessary corrections.  Suspension of work will not entitle the Contractor to an extension of time for the completion of the project and will not entitle him to extra payment for costs incurred.

The Contractor shall work continuously a minimum of six (6), 10-hour days per week to accomplish the work in a timely manner to allow road work contingent upon the electrical relocation to be performed.  The Contractor shall complete the relocation in three segments, beginning only one segment and completing that segment before beginning another.  The segments will be completed in the order listed unless otherwise approved in writing by HEA.  The electrical relocation segments will be as follows:

Segment 1:  Equipment # S3/20/5300 to # S3/16/3053

Segment 2:  Equipment # S3/16/2954 to # S3/16/6721A

Segment 3:  Equipment # S3/16/6721 to # S3/11/6148

Close coordination with HEA will be necessary to assure the operation of the electric distribution system is not impacted.

The electrical duct banks shall be installed to result in the maximum degree of reliability and maintenance-free operation.  Kinked ducts, inadequately supported, protected or swabbed ducts, and ducts that are carelessly jointed are not reliable and therefore unacceptable.  Any section of this electrical duct system that is not acceptable will be removed and replaced in accordance with these Special Provisions.

All conduit shall be stored to prevent damage or contamination prior to installation.  Conduit shall not be laid directly on the ground or floor.  It is preferable to store the conduit in a vertical position.  They shall be kept clean and dry as possible and free from damaging or deteriorating elements.  Temporary storage and installation of electrical duct banks shall be in accordance with NEMA Bulletin TCB-2 (1976), "Users Manual for the Installation of Underground Plastic Duct".

The existing electrical and/or public easements restrict the area available for the Contractor’s construction activities.  Throughout the project, the Contractor shall take all necessary precautions to insure the construction activities do not impact areas outside the existing electrical and/or public easements.  Existing HEA facilities also restrict construction areas.  The Contractor shall protect HEA facilities and at all times maintain them in good operational condition.  Shoring of trenches, existing power poles, and existing pad mounted equipment shall be completed by Contractor with all associated costs covered in the trenching unit bid price.

If construction or excavation require the removal of any existing privately owned facilities on the provided electrical easements, the Contractor shall be responsible for coordinating with the owner and for restoring lawns, driveways, parking lots, etc., to their original condition.  Any restorative work will be completed as soon as practicable after the installation, but in no case shall the period of time exceed two (2) weeks.  All restorative work shall be inclusive to the trench unit bid price.

A program of cleanup operations shall be carried out on a continuous basis throughout the progress of construction and the site shall be left neat and clean.  All equipment, devices, and structures shall be inspected after installation has been completed and any damage shall be repaired or replaced as directed.

One (1) week prior to the pre-construction meeting the Contractor shall submit a written work plan for approval.  This work plan shall detail equipment, manpower, and schedule Contractor will use to complete the project.  Shoring techniques to maintain existing facilities during adjacent excavation shall also be stated in this work plan.  Once work commences, the Contractor, the Engineer, and HEA’s Inspector will meet at the end of each week to review the work to date and plan the following week’s work.  The Contractor shall submit in writing his anticipated hourly work shift schedule by noon on the Wednesday prior to the next work week.

    - SURVEYING AND STAKING.  Conduit alignments shall be per the plans and any changes to the alignment will be subject to the approval of the Engineer. All vaults and electrical conduit shall be located and staked at the alignment and elevations indicated on the plans.  If elevations are not provided on the plans, the conduits shall be installed at the depth specified on the plan set.

All vaults, pads, and electrical duct systems shall be located and staked by the Contractor at the elevations indicated on the plans.  It shall be the Contractor’s responsibility to schedule a physical inspection of all line and grade prior to placing any vaults, pads, or ducts.  These elevation checks shall include top of pad elevations to assure adequate clearance for the pads from final grade.

All duct systems shall be constructed to within an allowable vertical tolerance of 30.5mm, and a horizontal tolerance of 61.0mm from the indicated plan location.

    - TRENCH AND PAD EXCAVATION AND BACKFILL.  Excavation work shall be accomplished in accordance with these Special Provisions and Section 204, Structure Excavation for Conduits and Minor Structures.

All existing underground utilities shall be identified and located and proper care taken not to damage them.  It shall be the Contractor’s responsibility to establish the location of all existing underground facilities by calling for a field locate in accordance with Subsection 105-1.06, Cooperation with Utilities.

The excavation shall be dug in such a manner as to provide a foundation of non-frost susceptible material on which to install the vaults, pads, or electrical duct banks as shown in the plans.  Trench and equipment foundation depth shall be as shown on the plans.  Trenches shall be of the necessary width that will allow compaction equipment to be utilized and for proper installation of structures or conduit.  The trench unit shall include all labor and equipment necessary to construct the facility in accordance with the plans and specifications.  Extra compensation shall not be granted for hand digging and/or utilization of an “air knife”.  The banks of the excavation shall be sloped/shored so as to conform to the prevailing safety requirements.

The trenches shall be maintained in a safe manner at all times to protect workers from cave-ins.  Appropriate shoring shall be employed to assure safety of workers while working in trenches.  Barriers and warning signs shall be employed to protect the public and employees from falling into trenches where such trenches are in areas vulnerable to these accidents.  Vehicles and excavation equipment must not cross over or run near trenches that could cause potential cave-ins.

Construction shall be arranged so the trenches will be left open for the shortest practical time to avoid creating a hazard and to minimize the likelihood of trench collapse due to other construction activity, rain, and accumulation of water in the trench, etc.  All temporary bridging utilized by the Contractor will be inspected and approved by the Engineer prior to installation.  This does not relieve the Contractor of responsibility for providing bridging of sufficient size and strength.  Any bridging open to public traffic will provide a smooth driving surface.

The Contractor shall not begin excavation of the trench until all personnel, materials, and equipment are present to complete the work in the most expedient manner.  Not more than 122 meters of trench shall be open in advance of the installation unless authorized in writing by the Engineer.  The Contractor shall backfill all pad and trench excavations within 48-hours.  There shall be no more than 30 meters of open trench at the end of the work day, unless approved by the Engineer.

The routing of the duct banks shall be as shown on the plans and staking sheets unless the conditions encountered are such that changes are necessary to accomplish the work.  In the event that rock or other obstructions are encountered during the trenching operation such that the ducts or pads cannot be installed, the Contractor shall inform the Engineer on the nature and extent of the difficulty encountered for his review and verification.  The Engineer, with the approval of HEA, will determine whether the duct is to be rerouted, trenched through the obstructed area, or advise another suitable change.

All excavation shall be inspected and approved by the Engineer before duct bank installation is started.  After the ducts are installed, the Engineer shall approve their line and grade prior to concrete encasement or sand backfill.  Trench, conduit installation, and concrete placement acceptance forms shall be filled out by HEA and signed by the electrical subcontractor after approval of each stage.  Failure to complete these forms will result in the rejection of the work.  The Contractor shall provide 24-hour written notification to HEA when a section of the duct system is ready for an acceptance inspection and a time for this inspection shall be mutually agreed upon.  Failure by HEA to attend the prearranged inspection shall not relieve the Contractor of the requirement to have the section accepted by HEA.  However, any additional costs involved will be in accordance with Section 104, Scope of Work.

All material below the specified trench depth shall be removed to a depth of 0.6 meters below specified trench depth.  Backfill shall be composed of materials meeting the requirements as specified on the plan drawings.  All materials shall be deposited in layers not exceeding 200mm and each lift (excluding sand) shall be compacted to 95 percent of the maximum density in accordance with Subsection 203-3.03, Construction of Embankments with Moisture and Density Control.  Note the final 50mm of over excavation fill shall be sand as shown in the plans.

All costs associated with the excavation, backfill importation, and excavation disposal shall be included in the trench unit bid price.  Disposal of waste excavation shall meet the requirements of subsection 681-3.07, Disposal of Waste Excavation.

All material below the specified equipment pads shall be removed to a depth of 0.6 meters below specified trench depth.  As shown in the plans, separation geotextile will be placed below the equipment pad at the over excavation elevation.  Backfill to the equipment pad grade will be with material meeting the requirements of Selected Material, Type A for Utilities, and deposited in layers not exceeding 200mm.  Each lift shall be compacted to 95 percent of the maximum density in accordance with Subsection 203-3.03, Construction of Embankments with Moisture and Density Control.  All cost associated with the excavation, backfill importation, separation geotextile, and excavation disposal shall be included in the equipment pad assembly unit bid price.  The separation geotextile shall meet the requirements of subsections 630-1.01 to 630-3.01.

All trench transition areas shall be gradual in terms of depth.  Offset conduit bends shall not be permitted.  At all transition locations, the “shallow” trench transition to meet the “deep” trench at a slope not to exceed 10:1.  Work associated with the trench transitions shall be incidental to the construction of the trench unit and not be considered a separate pay item.

The bottom of the trench must be transversely level to provide a uniform support for ducts.  Care shall be exercised to minimize the likelihood of water flow since this may cause trench damage and reduction in trench depth.  When this occurs, the trench must be cleared to the required depth before installing the ducts.

If large quantities of water are evident, the Contractor may elect to backfill with 50mm to 150mm coarse rock overlaid with a separation geotextile fabric.  All costs associated with this or any other option shall be included in the trenching unit bid prices.

When the duct bank passes below the structural section of the roadway, Selected Material, Type A Trench Backfill, shall be utilized for backfill to 200mm above the sand bedding over the duct.  The balance of the trench above the electrical duct banks shall be backfilled and compacted in 200mm lifts with material meeting the requirements of Selected Material,  Type C, to 95 percent of the maximum density in accordance with Subsection 203-3.03, Construction of Embankments with Moisture and Density Control, up to the bottom of the roadway structural section.  The desired compaction shall be obtained with mechanical tamping machines.  No construction or other activity shall be permitted across any trench until a depth of 1 meter of fill above the duct banks has been placed and compacted in accordance with these Special Provisions.

    - CONDUITS.  Schedule 40 PVC and the Galvanized Rigid Steel conduit shall be provided by HEA.  Defective conduit shall not be installed and shall be removed immediately from the worksite.

The Contractor shall install the conduit in open trench as to the manufacturer’s recommendations and as depicted in the plans, with no more than 5 degrees deflection per 3.05 meters of run.

All conduit sweeps and conduit entrances into pads/pedestals shall be installed within the pad window area or pedestal to allow for future installation of conductors without removal or adjustment of the pad or pedestal.

All terminating of conduit ends shall be secured with temporary end caps, and buried terminations shall be marked with a UM-47 above them as shown on the plans, at the time the conduit termination is backfilled.

PVC Fittings - Conduits and fittings shall be jointed by means of a primer solvent and welding cement (Contractor furnished) to provide a watertight and root-proof joint.  All conduits shall be cut off square with a hacksaw.  The cut end shall be face flat and properly reamed with a reamer designed for the purpose of removing the sharp edge.

Plastic spacers (Contractor furnished) with a maximum horizontal spacing of 2.44 meters are to be used to maintain conduit placement and separation for concrete encased ducts.

Only tools and equipment designed for the particular use and operation shall be used.  Tools and equipment shall be kept in good condition.  Worn or broken tools shall be removed from the job immediately.

Bending - All bending of conduit will be by means of infrared heating and bending equipment, such as a Carlon "Hotbox Bender" or equivalent.  No cold bending of conduit will be accepted.  Any bent conduit that is deformed will be unacceptable and will be removed and replaced at the Contractor’s expense.  The cost of field bending the conduit shall be subsidiary to the appropriate Conduit Item.

All conduit shall be field bent to follow the trench line and grade with a minimum radius of 7.62-meters.  All bends will be per the manufacturer’s recommendations.  The minimum allowable bending radius for equipment entrances is 1200mm.  Preformed sweeps and preformed elbows with bending radii less than 1200mm will not be allowed.  The material for all 4 and 6 inch conduit preformed elbows of 90 degrees will be RSC conduit.  All bends will be approved by the Engineer.

Duct Finishing - After completion of backfilling and compaction, the electrical duct systems will be mandreled, brushed, and swabbed to confirm the integrity of the duct run.  All bell ends shall be beveled.  The steel mandrel and steel brush shall be 1-3/4 inches in diameter for the 2-inch conduit, 3-3/4 inches in diameter for the 4-inch conduit, and 5-3/4 inches in diameter for the 6-inch conduit.  If the duct will not accept the mandrel, the duct will be removed and replaced at no additional expense.  All mandreling must be done in the presence of the Engineer and HEA representative.  All conduit entrances and exits into the vaults shall then be sealed and plugged.  The cost of mandreling and installing the jet line shall be considered subsidiary to the appropriate conduit item.

A 5-mm diameter polyethylene or polypropylene pull rope, with a minimum breaking strength of 3114N, shall be left in each conduit.  A conduit plug shall be furnished by the Contractor and placed on each conduit end with the pull rope securely tied to internal portion of the plug.  The conduit plugs shall be water, airtight, removable, and reusable, Manufacture: JACKMOON USA, INC or equivalent.  All pull ropes shall be new and continuous with no spliced sections.

Each conduit run destination shall be identified by 18.75-mm letters on 75 x 125-mm metal or plastic tag secured to the conduit, identifying the terminus of the conduit run, for example: "To SC 000".

    - ELECTRICAL DUCT BANK INSTALLATION.  All electrical duct banks on this project will be comprised of multiple PVC or RSC conduits of the configuration shown on the plans.  The conduits for the primary distribution circuit will be concrete encased or direct bury as noted on the plans.

It shall be the Contractor’s responsibility, with the Engineer’s approval, to determine the most expedient method to complete the required electrical duct bank installation.  All work across the roadway shall be accomplished in accordance with Section 643, Traffic Maintenance.

Concrete Encased Duct Banks - Concrete forms, when required by the Contractor’s operation, shall be secured and braced to resist all deformation or displacement while under load, and shall be constructed to line, grade, and dimensions shown on the plans.  The forms shall be installed in such a manner as to be easily removed without hammering or prying against green concrete.  Reinforcing bars shall be provided at all locations detailed on the plans.

The Contractor shall tie down the conduit prior to placement of concrete to avoid conduit flotation.  All concrete shall be placed by means of a concrete vibrator and in such a manner as to prevent damage or displacement to forms, ducts, spacers, steel reinforcing, or other insert accessories.  If flotation or misalignment of the conduit(s) occurs the Contractor shall make all the necessary repairs at Contractor expense.

Concrete shall not be placed if there is standing water in the forms or if the subgrade is saturated.  Placing of concrete may be initiated when the temperature is not less than 4.44 C and rising, and the soil temperature is greater that 1.11 C.  The concrete shall have a minimum temperature of 10 C and the addition of anti-freeze salts or solutions will not be allowed.  At temperatures of 4.44 C and below, the Contractor shall keep the concrete covered and apply heat to maintain a minimum temperature of 5 C during the total curing period.

All concrete forms shall be left in place for a minimum of 24 hours until the concrete becomes firmly set.

    - SWITCHING CABINET PADS, PRIMARY J-BOX PADS, AND TRANSFORMER PADS.  The switch cabinet pads, primary J-box pads, and transformer pads shall be placed to the dimensions detailed in the plans.

Before installation the Contractor shall verify the orientation of the pads with the Engineer.  The Contractor shall install grounding rods in all equipment pads in accordance with the UM6-6L or UM6-6 specification shown on the drawings.  The Contractor shall install grounding bushings on all GRSC elbows, which terminate inside equipment pads, in accordance with the UM6-6L or UM6-6 specification.

The Contractor shall assume all responsibility of the cost of transportation, installation, repair, and maintenance of HEA pads until the pads are accepted by HEA.  During the placement of a pad, if the gravel foundation proves to be inadequate to support the pad to designed line or grade (elevation), the Contractor shall remove the pad and re-compact to meet the requirements shown on the plans and specifications.

The pads shall conform to the final grade after completion of the entire road project.

681-3.07  DISPOSAL OF WASTE EXCAVATION.  Waste excavation shall be disposed of by the Contractor outside the project limits at locations approved by the Engineer.  All waste excavation shall be considered subsidiary to the trench unit bid item.

680-3.08  BEDDING MATERIAL.  All conduits installed for HEA shall be bedded with sand or with ¾ inch minus rock material.  If native material meets the following requirements it may be used as bedding material, with prior approval by the Engineer.  Sand bedding shall meeting the following:

Sieve Size	Present Passing by Weight

6.25 mm or ¼ -inch	100 %

0.075 mm or No. 200	0-6%

681-3.09  CABLE PULLING.  HEA shall install and splice the electric power cable.

681-3.10  AS-BUILT DRAWINGS.  An as-built survey, by a land surveyor registered in the State of Alaska, will be completed by the Contractor.  All electrical duct banks and pads, including the locations, alignment and installed depth shall be included.  The information will be referenced to established survey monuments.

The HEA as-built prints shall include all references to the road centerline at 30.48-meter intervals, alignment changes, deviations and exact locations of all vaults and pads.  The Contractor’s as-built plans shall note all obstructions i.e. existing utilities, culverts, and line grade and elevation changes.  On the HEA as-built plans in the joint trench locations the Contractor shall note and reference the orientation of HEA facilities.  When the HEA conduit system is completed, the Contractor shall certify the accuracy of the construction survey notes and each revision on the plans by written signature endorsement, by a registered land surveyor and deliver them to the Engineer prior to final acceptance of the system by HEA.  In addition the Contractor shall provide two (2) CDs with the as-built information in Auto Cad R14 files in the layering pattern provided by the Department on the read only CD and deliver them to the Engineer.  Delivery shall be to the Engineer prior to acceptance of the electrical duct system by HEA.

680-3.11  INSPECTION.  The HEA Inspector may at any time have access to the project site for the purpose of inspection.  The Contractor agrees to notify the HEA inspector at least seven (7) calendar days prior to the start of this project.  The manner of installation of the conduit, materials, and equipment used therein, shall be subject to the inspection of HEA Inspector.  Prior to backfilling any of the trenches for the HEA, the HEA Inspector will measure the conduit installed.  HEA will conduct a final inspection within ten (10) calendar days of the Contractor’s informing the HEA Inspector, in writing, that the HEA conduit system is complete.  Incomplete items (punch list) as noted in the final inspection report, shall be completed by the Contractor within ten (10) calendar days of the final inspection.

    - METHOD OF MEASUREMENT.  Concrete encased conduit, RSC, and Schedule 40 PVC conduit will be measured by the meter along the horizontal length of the installed construction unit.  Trench and concrete encased duct bank will be measured by the meter, at the required width and depths as specified on the plans.

The ground rod, ground rod assembly, sweep conduit, electrical switching cabinet pads, transformer pads, transformer pad assemblies, primary J-box pads shall be measured by the unit, complete and accepted in the final position.

Bedding material shall not be measured for payment but will be subsidiary to the conduit items.

Separation geotextile shall not be measured for payment but will be subsidiary to the equipment pad assembly items.

    - BASIS OF PAYMENT.  Payment will be full compensation for all labor, equipment, and materials necessary to complete this work.

Payment for a concrete encased duct bank and electrical conduit system will be the length of the construction unit conduits installed times the unit bid price per meter for each construction unit.  The price paid for the electrical duct system shall include all necessary fittings.  Splice kits shall be subsidiary to the duct bank installation.

Junction and pull box installations will be paid per each, as an electrical transformer pad.

The unit bid prices will include all necessary excavation to plan grade, backfill of native materials outside the normal lines of the roadway structural section. Borrow materials to elevate equipment pads and to replace unsuitable material will be paid under Item 203(6A), Selected Material, Type A.

Payment will be made under:

| Pay Item No. | Pay Item | - Pay Unit |
| --- | --- | --- |
| 681 (1-2 PVC) | UM6P920, Conduit, 1-2” Schedule 40 PVC | Meter |
| 681 (1-4 PVC) | UM6P940, Conduit, 1-4” Schedule 40 PVC | Meter |
| 681 (1-6 PVC) | UM6P960, Conduit, 1-6” Schedule 40 PVC | Meter |
| 681 (1-2, 90 PVC) | UM6PE20, Sweep Conduit, 1-2”, 90 Schedule 40 PVC, 48” | Each |
| 681 (1-4, 90 PVC) | UM6PE40, Sweep Conduit, 1-4”, 90 Schedule 40 PVC, 48” | Each |
| 681 (1-2, 90S) | UM6SE20, Sweep Conduit, 1-2”, 90 Rigid Steel | Each |
| 681 (1-4, 90S) | UM6SE40, Sweep Conduit, 1-4”, 90 Rigid Steel | Each |
| 681 (1-6, 90S) | UM6SE60, Sweep Conduit, 1-6”, 90 Rigid Steel | Each |
| 681 (1-4, 45S) | UM6SF40, Sweep Conduit, 1-4”, 45 Rigid Steel | Each |
| 681 (1-6, 45S) | UM6SF60, Sweep Conduit, 1-6”, 45 Rigid Steel | Each |
| 681 (1-2S) | UM6S920, Conduit, 1-2” Rigid Steel | Meter |
| 681 (1-4S) | UM6S940, Conduit, 1-4” Rigid Steel | Meter |
| 681 (2-6S) | UM6S960, Conduit, 1-6” Rigid Steel | Meter |
| 681 (XUR4) | XUR4, Concrete Encased Duct Bank | Meter |
| 681 (UR4) | Trench Excavation and Backfill | Meter |
| 681 (UM1-4) | UM1-4, Transformer Pad Assembly, Poly | Each |
| 681 (UM1-4L) | UM1-4L, Transformer Pad Lid Assembly | Each |
| 681 (UM1-PC) | UM1-PC, Transformer Pad Assembly, Concrete | Each |
| 681 (UM1-PCL) | UM1-PCL, Transformer Pad Lid Assembly | Each |
| 681 (UM1-FG) | UM1-FG, Fiberglass Pad Assembly | Each |
| 681 (UM1-FGL) | UM1-FGL, Fiberglass Pad Lid Assembly | Each |
| 681 (UM3-14) | UG Enclosure Assembly, 1 Phase | Each |
| 681 (1UM33) | UG Enclosure Assembly, 3 Phase | Each |
| 681 (UM6-6) | Ground Rod | Each |
| 681 (UM6-6L) | Ground Rod Assembly | Each |
| 681 (UK5) | Secondary Pedestal | Each |
| 681 (UM-47) | Underground Locate Target | Each |
| 681(15) | Electric As-Builts | - Lump Sum |