## ITEM F-171	POWER GATE OPERATORS

DESCRIPTION

171-1.1 Provide a complete and operational power gate operating system, with controls, designed and manufactured to operate as an integral system with the cantilever gate as located and shown on the plans.

MATERIALS

171-2.1 APPROVALS. Obtain approval of all materials or equipment proposed to use or incorporate in the work. Submit to the Engineer five (5) complete listings of materials and equipment specified herein and on the plans. Prepare the list to clearly identify the material or equipment by item, name, or designation used and indicate where specified. Provide submittals neatly bound, clearly indexed, and include applicable catalog numbers, cuts, wiring diagrams, performance data, operation and maintenance manuals, etc., for all material or equipment specified. In addition, whenever called for elsewhere in these Specifications include in the submittal certificates of compliance, manufacturer's instructions and/or shop drawings, or proposed construction or installation procedures.

171-2.2 COMPONENTS. Provide major components to include a new load center, gate operator, radio control and keypad system, cable, conduit, circuit breakers, and connectors. Provide NEMA approved electrical components. Provide testing of the gate operators and control systems before shipment from the factory.

a.	Gate Operator. 1 horsepower minimum, 240 Volts (V), single phase, capable of instant reversing, and adjustable time delay relay from 1/2 to 180 seconds for closing, UL 325 listed, mechanical braking within NEMA 3R enclosure. Chamberlain Group, Inc. Model SL595 Heavy Duty, Harsh Environment, or approved equal.

b.	Key-Pad System. Provide complete keypad systems designed to be impervious to the local environmental conditions. Install at each automated gate. Include any required power supplies and interfaces for a self-contained remote unit capable of handling at least two keypads.

Provide for each gate, 2 each keypads and terminal or interface to be controlled by either the radio or keypad systems. Digital Key Model 1050 Industrial Access or approved equal.

Include time delay relays, adjustable from 1/2 to 180 seconds for each system.

c.	Radio-Control System. Provide complete radio-control system. Include any required power supplies and interfaces for self-contained remote units.

Provide radio-receiver system designed to be impervious to local environmental conditions.

Provide system that interfaces with the keypad system and designed to be controlled by either method.

Provide for each gate operator, 12 each adjustable frequency transmitters, Pulsar Control or approved equal.

d.	Load Center. Provide enclosure for housing equipment, NEMA 12 lockable type, including an interior panel. Minimum size 36 inches x 24 inches x 10 inches. Hoffman or approved equal. Provide enclosure sized large enough to house panel, radio, keypad interface, power supply, and relays. Size distribution center to accommodate the equipment indicated in the load center wiring diagram on the plans.

Provide panel board rated as shown on the plans, single phase, 3- wire, and sized to provide all circuits and spares indicated. Provide branch breakers of bolt in type. Install panel board in the enclosure.

- Conductors for secondary systems in conduits. Provide copper, 600 volt-Volt Type XHHW, (X = Cross-Linked Polyethylene, HH = High Heat-Resistance, W = Water Resistance, Temperature Rating: 194° F in dry locations and 167° F in wet locations), black (phase conductors) and, white or yellow (neutral), and green (equipment grounding conductor).

f.	Rigid steel conduit. Provide standard weight (schedule 40) steel pipe, galvanized on the outside and finished with 40 mil (thousandth of an inch) Polyvinyl Chloride (PVC) exterior coating and with interior finished with a coating of urethane, Robroy Industries or approved equal. Provide fittings that meet the same specifications as the conduit.

g.	Flexible metal conduit. Provide liquid tight Anaconda Type 'EF' or approved equal.

h.	Marker tape. Provide yellow polyethylene plastic, printed "Caution Buried Electric Line Below", Allen System or approved equal.

i.	Tapes.

(1)	Pipe Sealing Tape: Scotch No. 48, Teflon pipe sealing tape or approved equal.

(2)	Corrosion Preventive Tape: Scotch No. 43 or approved equal.

(3)	Electrical Insulating Tape: Scotch No. 88 or approved equal.

j.	Ground conductor. Provide stranded bare copper, No. 6 AWG.

k.	Ground rods. Provide 3/4-inch diameter by 10 feet length copper clad steel.

- Concrete. Provide commercial grade concrete with a minimum 28-day compressive strength of 2,500 psi or an approved, pre-mixed, sacked concrete.

m.	Trench Backfill. Use material of the type shown on the plans.

CONSTRUCTION REQUIREMENTS

171-3.1 GENERAL. Install gate operator and control systems as shown on the plans and in accordance with the manufacturer’s instructions. Perform work in conformance with applicable National Fire Protection Association (NFPA) codes and standards, including NFPA 70 National Electrical Code (NEC), and all State and local codes. Locate new gate operators, fixtures, conduit, cables, etc., as shown on the plans and/or as directed by the Engineer.

171-3.2 TRENCHING, EXCAVATION, AND BACKFILLING.

- Trenching and Excavation. Trenches or excavations may be excavated manually or with mechanical equipment of standard manufacture specifically designed for excavating or trenching. Do not use blades of road patrols or graders to excavate the trenches.

Ensure that excavations for the placement or construction of items associated with the electrical work are of sufficient size to permit the placement or construction of the full width, length, and depth of the structure or object and the layer of bedding material, whenever bedding is required. Such items include, but are not limited to, foundations, footings, slabs, pads, manholes, handholes, ducts and/or duct banks, light base assemblies or outing stakes. Use the specified backfill material as shown on the plans.

Excavate the walls of trenches as near vertical as practical with smooth bottom, and free of frost susceptible material, pools of water, trash or debris. Control drainage in the vicinity of the trenches to prevent the runoff of surface water in the trenches. Promptly pump to remove any water accumulated in the trenches.

Provide trenches for burial of cable or conduit of sufficient width to provide a minimum 3 inches of lateral clearance between the conduit and trench walls on both sides or provide the lateral clearance as shown on the plans. Provide sufficient depth so that the top of the cable or conduit is a minimum of 18 inches below finish grade or to the depth indicated on the plans, when installed; and graded to slope as required.

Before placing any conduit in the trenches, remove all rocks or stones larger than 2 inches in diameter from the bottom of the trench. Tamp the trench bottom by filling or cutting away as required, to provide uniform conduit grades, sloping towards outlets, as shown on the plans. Call for inspection of the trenches by the Engineer before placing conduit.

- Backfilling. Before backfilling, cover the conduit with a 3 to 6 inch layer of approved backfill or bedding material as shown on the plans. Begin backfilling of the trenches after the conduit is installed and inspected and approved for backfilling by the Engineer. Thoroughly tamp the initial cover layer. Backfill the remainder of the trench with approved materials as shown on the plans, placed in 6-inch layers. Compact each layer to the density of the adjacent undisturbed ground and/or to the satisfaction of the Engineer. Backfill completely to the level of the adjacent surface. For trenches and excavations in areas where a surface layer of gravel, rock, or other material differing from subgrade has previously been placed, fill the upper part of the trench with the same material salvaged from the excavating or scripted from the adjoining surface. Provide at least 6 inches of surfacing material in the trench. For trenches in existing asphalt concrete, resurface the trench with a minimum 3-inch depth of an approved, pre-mixed, sacked concrete.

Restore all surface areas disturbed and/or damaged by trenching, excavation, sorting of materials, or any other construction related activities to their original condition except as stated above. Replace surfacing or cover material with new material of the same type of material removed. Accomplish restoration and/or removal and replacement of surfacing as required under this item at no additional cost to the State.

171-3.3 GROUNDING. Install grounding electrodes and grounding conductors as shown on the plans.

171-3.4 TESTING. Furnish all necessary labor, materials, equipment, appliances and power for conducting and performing tests of materials, equipment and/or systems. Begin tests after the work has been inspected and approved by the Engineer. Tabulate, sign, and date all test results on reproducible test sheets. No work will be accepted until all the applicable tests are performed successfully with satisfactory results and test sheets delivered to the Engineer.

Repair and/or remove and replace materials, equipment and/or systems that do not test satisfactorily.

Retest after repair or replacement.

Test and demonstrate to the Engineer the following:

a.	Circuits are properly connected in accordance with applicable wiring diagrams.

b.	Power and control circuits are continuous and free from short circuits.

c.	Circuits are free from unspecified grounds.

d.	Resistance to ground of all ungrounded 600-Volt multiple circuit conductors is not less than ten megohms when tested with a 1,000-Volt insulation resistance tester.

e.	Circuits are operable. Demonstration to include operation of each control and switch 10 times.

171-3.5 INSPECTION. Notify the Engineer and request inspection at least 48 hours prior to installing cables, conduit, concrete or lighting fixtures, making any splices, or covering any buried or concealed work. Immediately correct any deficiencies found during the inspection.

171-3.6 RECORD DOCUMENTS. Maintain at the project site a complete set of contract plans, Specifications, and approved changes to the contract documents. In addition to the above, maintain a separate complete set of electrical drawings for as-built purposes. Note all changes upon these as-builts along with the date and authority approving the change.

On the as-built drawings, show locations of all items such as lights, conduit, handholes, etc., including any existing active lines encountered. Show dimensions from roadway and taxiway centerlines or other permanent objects. Include complete wiring diagrams, (both power and control), identifying terminals, cables, and connections.

171-3.7 GUARANTEE. Guarantee that all materials or workmanship found defective within one year of final acceptance will be replaced at the Contractor’s expense, promptly upon notification and to the satisfaction of the Department.

METHOD OF MEASUREMENT

171-4.1 Measured as a complete unit to include radio and keypad system, gate operator, poles, load center with panel, relays, all wire and conduit, grounding rods, ground conductors, concrete footings, excavation, bedding, backfill, marker tape, concrete bases, all testing and all other incidentals necessary for an approved and operational power gate operator system installation.

BASIS OF PAYMENT

171-5.1 At the contract unit price per each for the completed and accepted system.

Payment will be made under:

Item F171.010.0000      Power Gate Operator System – per each