## ITEM L-101 AIRPORT ROTATING BEACONS

DESCRIPTION

101-1.1 This item shall consist of removal and disposal of existing beacons and furnishing and installing new airport rotating beacons. The work shall include mounting, leveling, wiring, conduit, painting, maintaining, and testing of the beacon. In addition, this item also includes all materials and incidentals necessary to place the beacon in a serviceable condition, as a completed unit, to the satisfaction of the Engineer. This item shall include a mounting platform if specified on the Plans.

EQUIPMENT AND MATERIALS

101-2.1 GENERAL.

Airport lighting equipment and materials covered by advisory circulars (ACs) shall be certified in AC 150/5345-53, Airport Lighting Equipment Certification Program (ALECP) and listed in the ALECP Addendum. The AC 150/5345-53, the latest certified equipment list, and the address list of certified airport lighting equipment manufacturers are available on the FAA Airport Engineering, Design, & Construction web page: https://www.faa.gov/airports/engineering/.

101-2.2 BEACON. The beacon shall be type L-801A, or L-802A, Class II, with metal-halide lamp(s), meeting the requirements of AC 150/5345-12, Specification for Airport and Heliport Beacons.

- The beacon shall be supplied with an arctic kit to provide supplemental heating to the beacon mechanisms and bearings for operations in extreme weather. If the manufacturer does not offer an optional arctic kit, the beacon shall be modified as specified in this subsection. The beacon shall, at a minimum, be equipped with a 400 watts (W) strip heater installed to keep the motor and beacon housing warm during extreme cold weather conditions. An air-sensing thermostat shall be supplied with contacts rated for 16 amperes (A), 120 volts (V). The thermostat shall be constructed so that contacts close on descending temperatures adjustable between 0 °F and 30 °F, +/- 4 °F. The contacts shall open on rising temperatures at 15 °F above closing temperature.

- The internal heater and internal thermostatic control kit shall be field wired separate from the beacon lights and motor, as shown in the beacon wiring diagram on the Plans.

- The beacon contactor shall be 2-pole, 30 A, with an operating coil designed for 120 V, 60 Hz., and  shall be mounted in the control panel with its operating coil circuit connected through an on-off-auto switch as shown on the Plans.

101-2.3 BEACON INSTALLATION. Installation shall be as shown on the Plans and in compliance with AC 150/5340-30, Design and Installation Details for Airport Visual Aids.

101-2.4 PANEL BOARDS AND BREAKERS. Panel boards and breakers shall conform to the requirements of Federal Specification W-P-115, Panel, Power Distribution.

101-2.5 WEATHERPROOF CABINETS. The weatherproof cabinets shall conform to National Electrical Manufacturers Association Standards (NEMA) and shall be constructed of steel not less than No. 16 United States Standard (USS) gauge.

101-2.6 ELECTRICAL WIRE. For ratings up to 600 V, thermoset wire conforming to Commercial Item Description A-A-59544A, Type XHHW-2, shall be used.  The wires shall be the type, size, number of conductors, and voltage shown in the Plans or in these Specifications.

101-2.7 CONDUIT. Rigid steel conduit and fittings shall be per Underwriters Laboratories (UL) Standards 6 and 514B.

101-2.8 PAINT.

              - Priming paint for non-galvanized metal surfaces shall be a high solids alkyd primer compatible with the manufacturer’s recommendations for the intermediate or topcoat.

              - Priming paint for galvanized metal surfaces shall be a zinc-rich epoxy primer paint per MIL-DTL-24441C/19C, Formula 159, Type III.  Use MIL-24441 thinner per paint manufacturer’s recommendations.

              - Orange paint for the body and the finish coats on metal and wood surfaces shall consist of a ready-mixed non-fading paint meeting the requirements of Master Painter’s Institute (MPI) Reference #9 (gloss). The color shall be per Federal Standard 595, International Orange Number 12197.

              - White paint for body and finish coats on metal and wood surfaces shall be ready-mixed paint per the Master Painter’s Institute, Reference #9, Exterior Alkyd, Gloss, volatile organic content (VOC) Range E2.

              - Priming paint for wood surfaces shall be mixed on the job by thinning the above-specified orange or white paint with 1/2 pint of raw linseed oil to each gallon.

              - Factory-applied paint shall be manufacturer’s standard prime and finish coats or powder-coated finish.

101-2.9 DISCONNECT SWITCH.  Switch shall be a 600V AC, 30A minimum, heavy-duty motor-rated, multi-pole switch as indicated on the Plans.  Provide switch in a NEMA type 4X metal enclosure.

CONSTRUCTION METHODS

101-3.1. PLACING THE BEACON. The beacon shall be mounted as shown in the Plans.

101-3.2 HOISTING AND MOUNTING. The beacon shall be hoisted to the mounting platform by using suitable slings and hoisting tackle. Before fastening the beacon to the mounting platform, the mounting holes shall be checked for correct spacing. Beacon base or mounting legs shall not be strained or forced out of position to fit incorrect spacing of mounting holes. The beacon base shall be raised first, set in position, and bolted in place. The drum shall then be raised and assembled to the base.

101-3.3 LEVELING. After the beacon has been mounted, it shall be accurately leveled following the manufacturer’s instructions. The leveling shall be checked in the presence of the Engineer and shall be to the Engineer’s satisfaction.

101-3.4 SERVICING. Before placing the beacon in operation, the Contractor shall check the manufacturer’s manual for proper servicing requirements. Follow the manufacturer’s servicing instructions for each size of beacon.  If not included in the manufacturer’s instructions, the Contractor must also:

- Clean and polish all glassware, both inside and outside, using a type of cleaner which will not scratch the lens, and clean the interior of the beacon.

- Clean interior of beacon base and check for alignment of parts.

- Clean and lubricate all mechanical systems according to manufacturer’s recommendations. Assure that all sub-assemblies are properly aligned and working properly.

- Secure lamps properly in the sockets.

101-3.5 BEAM ADJUSTMENT. After the beacon has been mounted and leveled, the elevation of the beam shall be adjusted. The final beam adjustments shall be made at night so that results can be readily observed. The beams shall be adjusted to the elevation directed by the Engineer or as shown in the Plans.  See AC 150/5340-30 for additional information about airport beacon beam adjustment.

101-3.6 BEACON MOUNTING PLATFORM. Where the beacon is to be mounted at a location other than the beacon tower and where a special mounting platform is required, the construction of the mounting platform and any necessary lightning protection equipment shall be per the details shown in the Plans.

101-3.7 WIRING. The Contractor shall furnish all necessary labor and materials and shall make complete above ground electrical connections per the wiring diagram furnished with the project Plans. The electrical installation shall conform to the requirements of the latest edition of National Fire Protection Association, NFPA-70, National Electrical Code (NEC).

If underground cable for the power feed from the transformer vault to the beacon site and duct for this cable installation is required, the cable, ground rods and duct shall be installed as shown on the Plans.

If shown on the Plans, the Contractor shall connect the tell-tale relay mechanism in the beacon to energize the tower obstruction light circuit when failure of the beacon service (primary) lamp occurs.

If lightning protection is specified in the Plans, it shall be installed per L-103, Airport Beacon Towers, Subsection 103-2.3.

101-3.8 PANEL AND CABINET. If shown on the plans, the Contractor shall furnish and install at the top of the beacon tower or mounting platform a circuit-breaker panel consisting of four 15-ampere breakers mounted in a weather-proof cabinet to provide separate protection for the circuits to the beacon lamps, motor, obstruction lights, and other equipment. The cabinet shall be located on the side of the beacon platform as shown on the plans or as directed by the Engineer.

101-3.9 CONDUIT. All exposed wiring shall be run in not less than 3/4-inch galvanized rigid steel conduit. Outdoor rated, liquid-tight, flexible metal conduit may be used for final connection at the beacon equipment. No conduit shall be installed on top of a beacon platform floor. All conduits shall be installed to provide for drainage. If mounted on a fixed steel beacon tower, the conduit shall be fastened to the tower members with Wraplock® straps (or equivalent), clamps, or approved fasteners, spaced approximately 5 feet apart.

The conduit shall be fastened to wooden structures with galvanized pipe straps and with galvanized wood screws not less than No. 8 or less than 1-1/4 inches long. There shall be at least two fastenings for each 10 feet length.

101-3.10 BOOSTER TRANSFORMER. If shown on the Plans and described in these Specifications, a booster transformer, used to compensate for a voltage drop to the beacon, shall be installed in a suitable weatherproof housing under or on the tower platform, at the base of the tower, in the transformer vault, or at the power source.

Install booster transformer as shown on the Plans and as described in these Specifications. If the booster transformer is required for installation in the transformer vault, it shall be installed according to L-109 Airport Transformer Vault and Vault Equipment.

101-3.11 PHOTOELECTRIC CONTROL. If shown on the Plans or specified in these Specifications, the Contractor shall furnish and install an automatic control switch at the location indicated in the Plans. The switch shall be a photoelectric type, standard commercially available unit complying with UL 773, with supply voltage rating of 120-277V AC, integral surge protection, -40°F deg F to 140°F temperature range, and EEI-NEMA standard twist-lock mounting base with matching receptacle.  The photoelectric switch shall be installed, connected, and adjusted per the manufacturer’s instructions.

101-3.12 OBSTRUCTION LIGHTS. Unless otherwise specified, the Contractor shall install on the top of the beacon tower or mounting platform two L-810 obstruction lights on opposite corners. These lights shall be mounted on conduit extensions to a height of not less than 4 inches above the top of the beacon.

101-3.13 PAINTING. If construction of a wooden mounting platform is required as part of the Plans or these Specifications, all wooden parts of the platform shall be given one priming coat of white or international-orange paint after fabrication but before erection and one body and one finish coat of international-orange paint after erection. Steel mounting platforms shall be given one priming coat of corrosion-inhibiting primer before erection and one body and one finish coat of international-orange paint after erection. All equipment installed under this contract and exposed to the weather shall be given one body and one finish coat of international-orange (per Federal Standard 595, Number 12197) or white paint as required. This shall include the beacon (except glass surfaces), beacon base, breaker cabinet, all conduit, and transformer cases. It shall not include lightning protection system air terminals or obstruction light globes.

Apply the paint uniformly at the proper consistency. The finished paint shall be free from sags, holidays, and smears. Each coat of paint shall be given ample time to dry and harden before the next coat of paint is applied. A minimum of three (3) days shall be allowed for drying on wood surfaces, and a minimum of four (4) days shall be allowed for drying on metal surfaces. Painting shall not be performed in cold, damp, foggy, dusty, or frosty atmospheres, or when the air temperature is below 40°F, or started when the weather forecast indicates such conditions for the day.

All surfaces shall be cleaned before painting. The surfaces shall be dry and free from scale, grease, rust, dust, and dirt. All knots in wood surfaces shall be covered with shellac immediately before applying the priming coat of paint. Nail holes and permissible imperfections shall be filled with putty. The ready-mixed paint shall be thinned for the priming and body coats per the manufacturer’s recommendations. In the absence of such recommendations, the following shall apply:

              - Body coats (for both wood and steel surfaces) - add 1/2 pint of turpentine to each gallon of ready-mixed paint for body coats.

              - Finish coats (for both wood and steel surfaces) the ready-mixed paint shall be used as it comes from the container for finish coats.

101-3.14 TESTING. The beacon installation shall be fully tested for proper operation as a completed unit prior to acceptance. These tests shall include operation of the lamp-changer and performing insulation resistance and voltage readings. The insulation resistance to ground of the beacon power supply circuit shall be not less than 1,000 megohms when measured ungrounded. The Contractor must furnish testing equipment. Tests shall be conducted in the presence of the Engineer and shall be to the Engineer’s satisfaction.

101-3.15 SPARE PARTS. Provide a quantity of spare parts, according to subsection L-125-3.10, including two spare lamps. Deliver spare parts to airport maintenance as directed by the Engineer.

METHOD OF MEASUREMENT

101-4.1 The quantity to be paid for shall be the number of beacons installed as completed units in place, accepted, and ready for operation.

BASIS OF PAYMENT

101-5.1 Payment will be made at the contract unit price for each completed and accepted beacon. This price shall be full compensation for removal of existing beacon, furnishing all materials and for all preparation, assembly, and installation of these materials, and for all labor, equipment, tools, and incidentals necessary to complete this item.  Removal of existing rotating beacons shall be subsidiary to installation of new rotating beacons.

101-5.2 Spare parts are paid for under L125.170.0000 Spare Parts.  Spare parts to be paid by actual invoiced material and delivery cost, according to subsection L-125-4.4, plus 15% markup.

Payment will be made under:

Item L101.010.0000	Rotating Beacon, High Intensity, L-802A - per each

Item L101.020.0000	Rotating Beacon, Medium Intensity, L-801A - per each

References

The publications listed below form a part of this specification to the extent referenced. The publications are referred to within the text by the basic designation only.

Advisory Circulars (AC)

AC 150/5345-12	Specification for Airport and Heliport Beacons

AC 150/5340-30	Design and Installation Details for Airport Visual Aids

AC 150/5345-53	Airport Lighting Equipment Certification Program

Commercial Item Description

A-A-59544A	Cable and Wire, Electrical (Power, Fixed Installation)

Federal Specification (FED SPEC)

FED SPEC W-P-115	Panel, Power Distribution

Federal Standard (FED STD)

FED STD 595	Colors Used in Government Procurement

Master Painter Institute (MPI)

MPI Reference #9	Alkyd, Exterior, Gloss (MPI Gloss Level 6)

Mil Spec

MIL-DTL-24441C/19C	Paint, Epoxy-Polyamide, Zinc Primer, Formula 159, Type III

National Fire Protection Association (NFPA)

NFPA-70	National Electric Code (NEC)

Underwriters Laboratories (UL)

UL Standard 6	Electrical Rigid Metal Conduit – Steel

UL Standard 514B	Conduit, Tubing, and Cable Fittings

UL Standard 773	Plug-In Locking Type Photocontrols for Use with Area Lighting