## Item L-108 Underground Power Cable for Airports

DESCRIPTION

108-1.1 This item shall consist of furnishing and installing power cables that are direct buried and furnishing and/or installing power cables within conduit or duct banks per these Specifications at the locations shown on the Plans. It includes excavation and backfill of trench for direct-buried cables only.

Also included are the installation of counterpoise wires, ground wires, ground rods and connections, cable splicing, cable marking, cable testing, and all incidentals necessary to place the cable in operating condition as a completed unit to the satisfaction of the Engineer. This item shall not include the installation of duct banks or conduit, trenching and backfilling for duct banks or conduit, or furnishing or installation of cable for FAA owned/operated facilities. This item also includes removing underground cables as shown on the Plans and according to these Specifications.

EQUIPMENT AND MATERIALS

108-2.1 GENERAL.

- Airport lighting equipment and materials covered by advisory circulars (AC) shall be approved under AC 150/5345-53 Airport Lighting Equipment Certification Program (AC 150/5345-53), current version. AC 150/5345-53, the latest certified equipment list, and the address list of certified airport lighting equipment manufacturers are available on the FAA Airport Engineering, Design, & Construction web page: https://www.faa.gov/airports/engineering/.

- All other equipment and materials covered by other referenced specifications shall be subject to acceptance through manufacturer’s certification of compliance with the applicable specification, when requested by the Engineer.

108-2.2 CABLE.  Underground cable for airfield lighting facilities (runway and taxiway lights and signs) shall conform to the requirements of AC 150/5345-7 Specification for L-824 Underground Electrical Cable for Airport Lighting Circuits, latest edition.  Conductors for use on 6.6 and 20 ampere primary airfield lighting series circuits shall be single conductor, seven strand, L-824  either Type B with ethylene propylene insulation or Type C with cross-linked polyethylene insulation, 5,000 volts, non-shielded, and shall be sized as shown on the Plans.  L-824 conductors for use on the L-830 secondary of airfield lighting series circuits shall be sized in accordance with the manufacturer’s recommendations.  All other conductors shall comply with FAA and National Electrical Code (NEC) requirements.

Wire for electrical circuits up to 600 volts shall comply with Specification L-824 and/or Commercial Item Description A-A-59544A and shall be type XHHW-2, 90°C for installation in conduit and RHW-2, 90°C for direct burial installations. Conductors for parallel (voltage) circuits shall be of a type and size complying with, and installed in accordance with, NFPA 70, National Electrical Code.  The minimum power circuit wire size shall be #12 AWG.

Underground electrical cable used to extend isolation transformer secondary leads shall be #14 AWG, 2 conductor, copper, 600 V, Type SOOW-A/SOOW. Cable shall remain flexible down to -40°F. The cable connectors shall be secondary connector kits for the plug and the receptacle meeting AC 150/5345-26 L-823 Plug and Receptacle Cable Connectors (AC 150/5345-26).

If telephone control cable is specified, shielded, polyethylene insulated and jacketed, No. 19 AWG telephone cable conforming to ICEA-S-85-625, Standard, Aircore, Polyolefin, Copper Conductor Telecommunications Cable for direct burial, shall be used.

Conductor sizes may have been adjusted due to voltage drop or other engineering considerations. Equipment provided by the Contractor shall be capable of accepting the quantity and sizes of conductors shown in the Plans, or included in the Specifications. All conductors, pigtails, cable step-down adapters, cable step-up adapters, terminal blocks and splicing materials necessary to complete the cable termination/splice shall be considered incidental to the respective pay items provided.

Cable type, size, number of conductors, strand and service voltage will be as shown on the Plans, or included in the Specifications.

108-2.3 COPPER WIRE (COUNTERPOISE, BARE COPPER WIRE GROUND AND GROUND RODS). Wire for counterpoise or ground installations for airfield lighting systems shall be #6 AWG minimum bare solid copper wire for counterpoise and/or #6 AWG minimum bare stranded for grounding bond wire per ASTM B3 and ASTM B8. For voltage powered circuits, the equipment grounding conductor shall comply with NEC Article 250.

Where counterpoise conductors are to be installed and where soil conditions would adversely affect bare copper wire, the Contractor may use cross-lined polyethylene wire conforming to Commercial Item Description A-A-59544A, Type XHHW-2, 600 V.

Ground rods shall be copper-clad steel. The ground rods shall be of the length and diameter specified on the Plans, but in no case be less than 10 feet long by 3/4 inch in diameter.

108-2.4 CABLE CONNECTIONS. In-line connections or splices of underground primary cables shall be of the type called for on the Plans, or in these Specifications, and shall be one of the types listed in this subsection. When the Plans or these Specifications permit a choice of connection, the Contractor shall indicate in the bid the proposed type of connection to furnish.

- The Cast Splice. A cast splice, employing a plastic mold and using epoxy resin equivalent to that manufactured by 3MTM Company, “Scotchcast” Kit No. 82-B, or an approved equivalent, used for potting the splice is acceptable. Cast splicing is the only type of splicing approved for a telephone control cable.

- The Field-Attached Plug-In Splice. Field-attached plug-in splices shall be installed as shown on the Plans, or as indicated in these Specifications. The Contractor shall determine the outside diameter of the cable to be spliced and furnish appropriately sized connector kits and/or adapters. Tape or heat shrink tubing with integral sealant shall be in accordance with manufacturer’s requirements. Primary connectors shall include a strain relief and O-rings at the cable entry and a factory-molded sealing flap at the connector interface. Primary Connector Kits manufactured by Amerace, “Super Kit”, Integro “Complete Kit”, or approved equal is acceptable.

  - 600 V secondary receptacles shall be Type II, Class B, Style 11 or 12

  - 600 V plugs shall be Type II, Class B, Style 4 or 5

  - 5,000 V plugs shall be Type I, Class B, Style 3

  - 5,000 V receptacles shall be Type I, Class B, Style 10

- The Factory-Molded Plug-In Splice. AC 150/5345-26, Factory-Molded to Individual Conductors, is acceptable.

- The Taped or Heat-Shrink Splice. Taped splices employing field-applied rubber, or synthetic rubber tape covered with plastic tape is acceptable. The rubber tape should meet the requirements of ASTM D4388 and the plastic tape should comply with Military Specification MIL-I-24391 or Commercial Item Description A-A-55809. Heat shrinkable tubing shall be heavy-wall, self-sealing tubing rated for the voltage of the wire being spliced and suitable for direct-buried installations.

The tubing shall be factory coated with a thermoplastic adhesive-sealant that will adhere to the insulation of the wire being spliced forming a moisture- and dirt-proof seal. Additionally, heat shrinkable tubing for multi-conductor cables, shielded cables, and armored cables shall be factory kits that are designed for the application. Heat shrinkable tubing and tubing kits shall be manufactured by Tyco Electronics/ Raychem Corporation, Energy Division, or approved equivalent.

In all the above cases, connections of cable conductors shall be made using crimp connectors using a crimping tool designed to make a complete crimp before the tool can be removed. All L-823/L-824 splices and terminations shall be made per the manufacturer’s recommendations and listings.

All connections of counterpoise, grounding conductors and ground rods shall be made by the exothermic process or approved equivalent, except that a light base ground clamp connector shall be used for attachment to the light base. All exothermic connections shall be made per the manufacturer’s recommendations and listings.

108-2.5 SPLICER QUALIFICATIONS. Every airfield lighting cable splicer shall be qualified in making airport cable splices and terminations on cables rated at or above 5,000 volts AC. The Contractor shall submit to the Engineer proof of the qualifications of each proposed cable splicer for the airport cable type and voltage level to be worked on. Cable splicing/terminating personnel shall have a minimum of three (3) years continuous experience in terminating/splicing medium voltage cable.

108-2.6 CONCRETE. Concrete shall be proportioned, placed, and cured per P-610 Concrete for Miscellaneous Structures.

108-2.7 FLOWABLE BACKFILL. Flowable material used to backfill trenches for power cable trenches shall conform to the requirements of P-153 Controlled Low Strength Material.

108-2.8 CABLE IDENTIFICATION TAGS. Cable identification tags shall be made from a non-corrosive material with the circuit identification stamped or etched onto the tag. The tags shall be of the type as detailed on the Plans, or these Specifications.

108-2.9 TAPE. Electrical tapes shall be ScotchTM Electrical Tapes –ScotchTM 88 (1-1/2 inches wide) and ScotchTM 130C® linerless rubber splicing tape (2-inches wide), as manufactured by the Minnesota Mining and Manufacturing Company (3MTM), or an approved equal.

108-2.10 ELECTRICAL COATING. Electrical coating shall be Scotchkote™ as manufactured by 3MTM, or an approved equal.

108-2.11 EXISTING CIRCUITS. See subsection 108-3.10.

108-2.12 DETECTABLE WARNING TAPE. Plastic, detectable, American Public Works Association (APWA) Red (electrical power lines, cables, conduit and lighting cable) with continuous legend tape shall be polyethylene film with a metalized foil core and shall be 3-6 inches wide. Detectable tape is incidental to the respective bid item. Detectable warning tape for communication cables shall be orange.  Detectable warning tape color code shall comply with the APWA Uniform Color Code.

CONSTRUCTION METHODS

108-3.1 GENERAL. The Contractor shall install the specified cable at the approximate locations indicated on the plans. Unless otherwise shown on the Plans, all cable required to cross under pavements expected to carry aircraft loads shall be installed in concrete encased duct banks. Cable shall be run without splices, from fixture to fixture.

Notify the Engineer in writing and request inspection at least 48 hours prior to installing cables, making any splices, or covering any buried or concealed work. Immediately correct any deficiencies found during the inspection. Install cable in a manner to prevent harmful stretching of the conductors, injury to the insulation, damage to tapes and fillers or damage to the outer protective jacket or covering.

Cable connections between lights will be permitted only at the light locations for connecting the underground cable to the primary leads of the individual isolation transformers. The Contractor shall be responsible for providing cable in continuous lengths for home runs or other long cable runs without connections unless otherwise authorized in writing by the Engineer or shown on the Plans.

In addition to connectors being installed at individual isolation transformers, L-823 cable connectors for maintenance and test points shall be installed at locations shown on the Plans. Cable circuit identification markers shall be installed on both sides of the L-823 connectors installed and on both sides of slack loops where a future connector would be installed.

Provide not less than 3 feet of cable slack on each side of all connections, isolation transformers, light units, and at points where cable is connected to field equipment. At L-823 connectors and where provisions must be made for testing or for future above grade connections, provide enough slack to allow the cable to be extended at least two feet vertically above the top of the access structure. This requirement also applies where primary cable passes through empty light bases, junction boxes, and access structures to allow for future connections, or as designated by the Engineer.

Primary airfield lighting cables installed shall have cable circuit identification markers attached on both sides of each L-823 connector and on each airport lighting cable entering or leaving cable access points, such as manholes, hand holes, pull boxes, junction boxes, etc. Markers shall be heat stamped nylon identification tags bearing the circuit identification as indicated on the Plans. Markers shall be of sufficient length for imprinting the cable circuit identification legend on one line, using letters not less than 1/4-inch in size. The cable circuit identification shall match the circuits as shown on the Plans.

108-3.2 INSTALLATION IN DUCT BANKS OR CONDUITS. This item includes the installation of the cable in duct banks or conduit per this subsection. The maximum number and voltage ratings of cables installed in each single duct or conduit, and the current-carrying capacity of each cable shall be per the latest version of the National Electric Code, or the code of the local agency or authority having jurisdiction.

The Contractor shall make no connections or splices of any kind in cables installed in conduits or duct banks.

Unless otherwise shown in the Plans, where ducts are in tiers, use the lowest ducts to receive the cable first, with spare ducts left in the upper levels. Check duct routes prior to construction to obtain assurance that the shortest routes are selected and that any potential interference is avoided.

Duct banks or conduits shall be installed as a separate item per L-110 Airport Underground Electrical Duct Banks and Conduits. The Contractor shall run a mandrel through duct banks or conduit prior to installation of cable to ensure that the duct bank or conduit is open, continuous and clear of debris. The mandrel size shall be compatible with the conduit size. The Contractor shall swab out all conduits/ducts and clean light bases, manholes, etc., interiors immediately prior to pulling cable. Once cleaned and swabbed, the light bases and all accessible points of entry to the duct/conduit system shall be kept closed except when installing cables. Cleaning of ducts, light bases, manholes, etc., is incidental to the pay item of the item being cleaned. All raceway systems left open, after initial cleaning, for any reason shall be re-cleaned at the Contractor’s expense. The Contractor shall verify existing ducts proposed for use in this project as clear and open. The Contractor shall notify the Engineer of any blockage in the existing ducts.

The cable shall be installed in a manner that prevents harmful stretching of the conductor, damage to the insulation, or damage to the outer protective covering. The ends of all cables shall be sealed with moisture-seal tape providing moisture-tight mechanical protection with minimum bulk, or alternately, heat shrinkable tubing before pulling into the conduit and it shall be left sealed until connections are made. Where more than one cable is to be installed in a conduit, all cable shall be pulled in the conduit at the same time. The pulling of a cable through duct banks or conduits may be accomplished by hand winch or power winch with the use of cable grips or pulling eyes. Maximum pulling tensions shall not exceed the cable manufacturer’s recommendations. A non-hardening cable-pulling lubricant recommended for the type of cable being installed shall be used where required.

The Contractor shall submit the recommended pulling tension values to the Engineer prior to any cable installation. If required by the Engineer, pulling tension values for cable pulls shall be monitored by a dynamometer in the presence of the Engineer. Cable pull tensions shall be recorded by the Contractor and reviewed by the Engineer. Cables exceeding the maximum allowable pulling tension values shall be removed and replaced by the Contractor at the Contractor’s expense.

Assemble connections in the runway and taxiway series lighting cable at the light assemblies using approved L-823 connector kits. The male end shall be coated with silicone compound. Properly seat both plug and receptacle ends onto cable and check for proper connector pin positioning prior to taping. When completed, seal the connection as indicated on the Plans and in subsection 108-3.5.

The manufacturer’s minimum bend radius or NEC requirements (whichever is more restrictive) shall apply. Cable installation, handling and storage shall be per manufacturer’s recommendations. During cold weather, particular attention shall be paid to the manufacturer’s minimum installation temperature. Cable shall not be installed when the temperature is at or below the manufacturer’s minimum installation temperature. At the Contractor’s option, the Contractor may submit a plan, for review by the Engineer, for heated storage of the cable and maintenance of an acceptable cable temperature during installation when temperatures are below the manufacturer’s minimum cable installation temperature.

Cable shall not be dragged across base can or manhole edges, pavement or earth. When cable must be coiled, lay cable out on a canvas tarp or use other appropriate means to prevent abrasion to the cable jacket.

108-3.3 INSTALLATION OF DIRECT-BURIED CABLE IN TRENCHES. Unless otherwise specified, the Contractor shall not use a cable plow for installing the cable. Mechanical cable-laying equipment may be used in conjunction with a trenching machine if shown on the Plans and indicated in the Specifications. The installation should provide for physical inspection of cable prior to backfilling. Cable shall be unreeled uniformly in place alongside or in the trench and shall be carefully placed along the bottom of the trench. Inspect cable as it is removed from the reel to determine that the cable is free of visible defects. Support reel so that reel turns easily and without undue strain on the cable. The cable shall not be unreeled and pulled into the trench from one end. Slack cable sufficient to provide strain relief shall be placed in the trench in a series of S curves. Sharp bends or kinks in the cable shall not be permitted.

Where cables must cross over each other, a minimum of 3 inches vertical displacement shall be provided with the topmost cable depth at or below the minimum required depth below finished grade.

- Trenching. Where turf is well established and the sod can be removed, it shall be carefully stripped and properly stored. Trenches for cables may be excavated manually or with mechanical trenching equipment. Walls of trenches shall be essentially vertical so that a minimum of surface is disturbed. Graders shall not be used to excavate the trench with their blades. The bottom surface of trenches shall be essentially smooth and free from coarse aggregate. Unless otherwise specified, cable trenches shall be excavated to a minimum depth of 18 inches below finished grade per NEC Table 300.5, except as follows:

  - When off the airport or crossing under a roadway or driveway, the minimum depth shall be 36 inches unless otherwise specified.

  - Minimum cable depth when crossing under a railroad track, shall be 42 inches unless otherwise specified.

The Contractor shall excavate all cable trenches to a width not less than 6 inches. Unless otherwise specified on the plans, all cables in the same location and running in the same general direction shall be installed in the same trench.

When rock is encountered, the rock shall be removed to a depth of at least 3 inches below the required cable depth and it shall be replaced with bedding material of earth or sand containing no mineral aggregate particles that would be retained on a 1/4-inch sieve. Flowable backfill material may alternatively be used.

Duct bank or conduit markers temporarily removed for trench excavations shall be replaced as required.

It is the Contractor’s responsibility to locate existing utilities within the work area prior to excavation. Where existing active cables cross proposed installations, the Contractor shall ensure that these cables are adequately protected. Where crossings are unavoidable, no splices will be allowed in the existing cables, except as specified on the plans. Installation of new cable where such crossings must occur shall proceed as follows:

  - Existing cables shall be located manually. Unearthed cables shall be inspected to assure absolutely no damage has occurred.

  - Trenching, etc., in cable areas shall then proceed, with approval of the Engineer, with care taken to minimize possible damage or disruption of existing cable, including careful backfilling in area of cable.

In the event that any previously identified cable is damaged during the course of construction, the Contractor shall be responsible for the complete repair or replacement.

- Backfilling. After the cable has been installed, the trench shall be backfilled. The first layer of backfill in the trench shall encompass all cables; be 3 inches deep, loose measurement; and shall be either earth or sand containing no mineral aggregate particles that would be retained on a 1/4-inch sieve. This layer shall not be compacted. The second layer shall be 5 inches deep, loose measurement, and shall contain no particles that would be retained on a one inch sieve. The remaining third and subsequent layers of backfill shall not exceed 8 inches of loose measurement and be excavated or imported material and shall not contain stone or aggregate larger than 4 inches maximum diameter.

The second and subsequent layers shall be thoroughly tamped and compacted to at least the density of the adjacent material. If the cable is to be installed in locations or areas where other compaction requirements are specified (under pavements, embankments, etc.), the backfill compaction shall be in accordance with the Plans and Specifications for the indicated materials.

Trenches shall not contain pools of water during backfilling operations. The trench shall be completely backfilled and tamped level with the adjacent surface, except that when turf is to be established over the trench, the backfilling shall be stopped at an appropriate depth consistent with the type of turfing operation to be accommodated. A proper allowance for settlement shall also be provided. Any excess excavated material shall be removed and disposed of per the plans and specifications.

Underground electrical warning (caution) tape shall be installed in the trench above all direct-buried cable. Contractor shall submit a sample of the proposed warning tape for acceptance by the Engineer. If not shown on the Plans, the warning tape shall be located 6 inches above the direct-buried cable or the counterpoise wire if present. A 3 to 6-inch wide polyethylene film detectable tape, with a metalized foil core, shall be installed above all direct buried cable or counterpoise. The tape shall be of the color and have a continuous legend as indicated on the Plans. The tape shall be installed 8 inches minimum below finished grade.

- Restoration. Following restoration of all trenching near airport movement surfaces, the Contractor shall visually inspect the area for foreign object debris (FOD) and remove any that is found.  Where soil and sod has been removed, it shall be replaced as soon as possible after the backfilling is completed. All areas disturbed by work shall be restored to its original condition. The restoration shall include the sodding, topsoiling, fertilizing, liming, seeding, sprigging, or mulching as shown on the Plans. The Contractor shall be held responsible for maintaining all disturbed surfaces and replacements until final acceptance. When trenching is through paved areas, restoration shall be equal to existing conditions.  Restoration shall be considered incidental to the pay item of which it is a component part.

108-3.4 CABLE MARKERS for direct-buried cable. When called for in the Plans, the location of direct buried circuits shall be marked by a concrete slab marker, 2 feet square and 4 to 6-inch thick, extending approximately one inch above the surface. Each cable run from a line of lights and signs to the equipment vault shall be marked at approximately every 200 feet along the cable run, with an additional marker at each change of direction of cable run. All other direct-buried cable shall be marked in the same manner. Cable markers shall be installed directly above the cable. The Contractor shall impress the word “CABLE” and directional arrows on each cable marking slab. The letters shall be approximately 4 inches high and 3 inches wide, with width of stroke 1/2-inch and 1/4-inch deep. Stencils shall be used for cable marker lettering; no hand lettering shall be permitted.

At the location of each underground cable connection/splice, except at lighting units, or isolation transformers, a concrete marker slab shall be installed to mark the location of the connection/splice. The Contractor shall impress the word “SPLICE” on each slab. The Contractor also shall impress additional circuit identification symbols on each slab as directed by the Engineer. All cable markers and splice markers shall be painted international orange. Paint shall be specifically manufactured for uncured exterior concrete. After placement, all cable or splice markers shall be given one coat of high-visibility aviation orange paint as approved by the Engineer. Furnishing and installation of cable markers is incidental to the respective cable pay item.

108-3.5 SPLICING. Connections of the type shown on the Plans shall be made by experienced personnel regularly engaged in this type of work and shall be made as follows:

- Cast Splices. These shall be made by using crimp connectors for jointing conductors. Molds shall be assembled, and the compound shall be mixed and poured per the manufacturer’s instructions and to the satisfaction of the Engineer.

- Field-Attached Plug-In Splices. These shall be assembled per the manufacturer’s instructions. These splices shall be made by plugging directly into mating connectors. The joint where the connectors come together shall be finished by one or more of the following methods as shown on the Plans:

  - Wrapped with at least one layer of rubber or synthetic rubber tape and one layer of plastic tape, one-half lapped, extending at least 1-1/2 inches on each side of the joint.

  - Covered with heat shrinkable tubing with internal sealant at ends only extending from cable to cable across the entire assembly.

  - On connector kits equipped with water seal flap; roll-over water seal flap to sealing position on mating connector.

- Factory-Molded Plug-In Splices. These shall be made by plugging directly into mating connectors. The joint where the connectors come together shall be finished by one or more of the following methods as shown on the Plans:

  - Wrapped with at least one layer of rubber or synthetic rubber tape and one layer of plastic tape, one-half lapped, extending at least 1-1/2 inches on each side of the joint.

  - Covered with heat shrinkable tubing with internal sealant at ends only extending from cable to cable across the entire assembly.

  - On connector kits so equipped with water seal flap; roll-over water seal flap to sealing position on mating connector.

- Taped or Heat-Shrink Splices. A taped splice shall be made in the following manner:

  - Bring the cables to their final position and cut so that the conductors will butt.

  - Remove insulation and jacket allowing for bare conductor of proper length to fit compression sleeve connector with 1/4-inch of bare conductor on each side of the connector.

  - Prior to splicing, the two ends of the cable insulation shall be penciled using a tool designed specifically for this purpose and for cable size and type. Do not use emery paper on splicing operation since it contains metallic particles. The copper conductors shall be thoroughly cleaned.

  - Join the conductors by inserting them equidistant into the compression connection sleeve.

  - Crimp conductors firmly in place with crimping tool that requires a complete crimp before tool can be removed.

  - Test the crimped connection by pulling on the cable.

  - Scrape the insulation to assure that the entire surface over which the tape will be applied (plus 3 inches on each end) is clean. After scraping, wipe the entire area with a clean lint-free cloth. Do not use solvents.

  - Apply high-voltage rubber tape one-half lapped over bare conductor. This tape should be tensioned as recommended by the manufacturer. Voids in the connector area may be eliminated by highly elongating the tape, stretching it just short of its breaking point. The manufacturer's recommendation for stretching tape during splicing shall be followed. Always attempt to exactly half-lap to produce a uniform buildup. Continue buildup to 1-1/2 times cable diameter over the body of the splice with ends tapered a distance of approximately one inch over the original jacket.

  - Cover rubber tape with two layers of vinyl pressure-sensitive tape one-half lapped. Do not use glyptol or lacquer over vinyl tape as they react as solvents to the tape. No further cable covering or splice boxes are required.

  - Heat shrinkable tubing shall be installed following manufacturer’s instructions. Direct flame heating shall not be permitted unless recommended by the manufacturer. Cable surfaces within the limits of the heat-shrink application shall be clean and free of contaminates prior to application.

- Assembly. Surfaces of equipment or conductors being terminated or connected shall be prepared in accordance with industry standard practice and manufacturer’s recommendations.  All surfaces to be connected shall be thoroughly cleaned to remove all dirt, grease, oxides, nonconductive films, or other foreign material.  Paints and other nonconductive coatings shall be removed to expose base metal.  Clean all surfaces at least 1/4-inch beyond all sides of the larger bonded area on all mating surfaces.  Use a joint compound suitable for the materials used in the connection.  Repair painted/coated surface to original condition after completing the connection.

- Insulation Removal. Insulation of 5000V wire shall be trimmed with a proper trimming/penciling tool to exact barrel length as recommended by the manufacturer.  Scoring insulation with a knife is not an acceptable method as it may damage the wire.

108-3.6 BARE COUNTERPOISE WIRE INSTALLATION FOR LIGHTNING PROTECTION AND GROUNDING. If shown on the Plans or indicated in the Specifications, a solid or stranded bare copper counterpoise wire, #6 AWG minimum size, shall be installed for lightning protection of the underground cables. The Engineer shall select one of two methods of lightning protection for the airfield lighting circuit based upon sound engineering practice and lightning strike density.

The counterpoise system shall terminate at the transformer vault or at the power source. It shall be securely attached to the vault or equipment grounding system. The connections shall be made as shown on the Plans and indicated in the Specifications.

- Equipotential. The counterpoise size is as shown on the Plans. The equipotential method is applicable to all airfield lighting systems; i.e. runway, taxiway, apron – touchdown zone, centerline, edge, threshold and approach lighting systems. The equipotential method is also successfully applied to provide lightning protection for power, signal and communication systems. The light bases, counterpoise, etc., all components, are bonded together and bonded to the vault power system ground loop/electrode.

Counterpoise wire shall be installed in the same trench for the entire length of buried cable, conduits and duct banks that are installed to contain airfield cables.  The counterpoise is centered over the cable/conduit/duct to be protected.

The counterpoise conductor shall be installed no less than 8 inches minimum or 12 inches maximum above the raceway or cable to be protected, except as permitted below:

  - The minimum counterpoise conductor height above the raceway or cable to be protected shall be permitted to be adjusted subject to coordination with the airfield lighting and pavement designs.

  - The counterpoise conductor height above the protected raceway(s) or cable(s) shall be calculated to ensure that the raceway or cable is within a 45-degree area of protection, 45 degrees on each side of vertical creating a 90-degree angle.

The counterpoise conductor shall be bonded to each metallic light base, mounting stake, and metallic airfield lighting component.

All metallic airfield lighting components in the field circuit on the output side of the constant current regulator (CCR) or other power source shall be bonded to the airfield lighting counterpoise system.

All components rise and fall at the same potential; with no potential difference, no damaging arcing and no damaging current flow.

See AC 150/5340-30 Design and Installation Details for Airport Visual Aids and NFPA 780, Standard for the Installation of Lightning Protection Systems, Chapter 11, for a detailed description of the Equipotential Method of lightning protection.

- Isolation. Counterpoise size is as shown on the Plans.  The isolation method is an alternate method for use only with edge lights installed in turf and stabilized soils and raceways installed parallel to and adjacent to the edge of the pavement.  NFPA 780 uses 15 feet to define “adjacent to”.

The counterpoise conductor shall be installed halfway between the pavement edge and the light base, mounting stake, raceway, or cable being protected.

The counterpoise conductor shall be installed 8 inches minimum below grade. The counterpoise is not connected to the light base or mounting stake.  An additional grounding electrode is required at each light base or mounting stake.  The grounding electrode is bonded to the light base or mounting stake with a #6 AWG solid or stranded copper conductor.

See AC 150/5340-30 Design and Installation Details for Airport Visual Aids and NFPA 780, Standard for the Installation of Lightning Protection Systems, Chapter 11, for a detailed description of the Isolation Method of lightning protection.

- Common Installation requirements. When a metallic light base is used, the grounding electrode shall be bonded to the metallic light base or mounting stake with a #6 AWG bare, annealed or soft drawn, solid or stranded copper conductor.

When a nonmetallic light base is used, the grounding electrode shall be bonded to the metallic light fixture or metallic base plate with a #6 AWG bare, annealed or soft drawn, solid or stranded copper conductor.

Grounding electrodes may be rods, ground dissipation plates, radials, or other electrodes listed in the NEC or NFPA 780.

Where raceway is installed by the directional bore, jack and bore, or other drilling method, the counterpoise conductor shall be permitted to be installed concurrently with the directional bore, jack and bore, or other drilling method raceway, external to the raceway or sleeve.

The counterpoise wire shall also be exothermically welded to ground rods installed as shown on the plans but not more than 500 feet apart around the entire circuit.  The counterpoise system shall be continuous and terminate at the transformer vault or at the power source.  It shall be securely attached to the vault or equipment external ground ring or other made electrode-grounding system.  The connections shall be made as shown on the Plans and indicated in the Specifications.

Where an existing airfield lighting system is being extended or modified, the new counterpoise conductors shall be interconnected to existing counterpoise conductors at each intersection of the new and existing airfield lighting counterpoise systems.

- Parallel Voltage Systems.  Provide grounding and bonding in accordance with NFPA 70, National Electrical Code (NEC).

- Grounding System. If shown on the Plans or indicated in the Specifications, a stranded bare copper wire, #6 AWG minimum size, shall be installed as grounding for the lighting system. The bare ground wire shall be installed in the same conduit it is designed to protect. The ground wire shall be securely attached to each light fixture base. The ground wire shall be continuous through each light base and handhole or be spliced using an irreversible compression connector. The circuit ground wire shall not rely on the mechanical ground lug in the light base for continuity. The ground wire shall also be securely attached to ground rods using exothermically welded connections as shown on the Plans but not more than 1,000 feet apart around the entire circuit.

The grounding system shall terminate at the transformer vault or at the power source. It shall be securely attached to the vault or equipment grounding system. The connections shall be made as shown on the Plans and indicated in the Specifications.

The housing or baseplate of each light fixture shall be bonded to the light base ground using a bare or green insulated #6 AWG stranded copper wire or equivalent tinned-copper braid.

108-3.7 Counterpoise installation above multiple conduits and duct banks. Counterpoise wires shall be installed above multiple conduits/duct banks for airfield lighting cables, with the intent being to provide a complete area of protection over the airfield lighting cables. When multiple conduits and/or duct banks for airfield cable are installed in the same trench, the number and location of counterpoise wires above the conduits shall be adequate to provide a complete area of protection measured 45 degrees each side of vertical.

Where duct banks pass under pavement to be constructed in the project, the counterpoise shall be placed above the duct bank. Reference details as shown on the Plans.

108-3.8 Counterpoise installation at existing duct banks. When airfield lighting cables are indicated on the Plans to be routed through existing duct banks, the new counterpoise wiring shall be terminated at ground rods at each end of the existing duct bank where the cables being protected enter and exit the duct bank. The new counterpoise conductor shall be bonded to the existing counterpoise system.

108-3.9 EXOTHERMIC BONDING. Bonding of counterpoise wire shall be by the exothermic welding process or equivalent method accepted by the Engineer. Only personnel experienced in and regularly engaged in this type of work shall make these connections.

Contractor shall demonstrate to the satisfaction of the Engineer, the welding kits, materials and procedures to be used for welded connections prior to any installations in the field. The installations shall comply with the manufacturer’s recommendations and the following:

- All slag shall be removed from welds.

- Using an exothermic weld to bond the counterpoise to a lug on a galvanized light base is not recommended unless the base has been specially modified.  Consult the manufacturer’s installation directions for proper methods of bonding copper wire to the light base.  See AC 150/5340-30 for galvanized light base exception.

- If called for in the Plans, all buried copper and weld material at weld connections shall be thoroughly coated with 1/4–inch of 3MTM ScotchkoteTM, or approved equivalent, or coated with coal tar Bitumastic® material to prevent surface exposure to corrosive soil or moisture.

108-3.10 TESTING. The Contractor shall furnish all necessary equipment and appliances for testing the airport electrical systems and underground cable circuits before and after installation. The Contractor shall perform all tests in the presence of the Engineer. The Contractor shall demonstrate the electrical characteristics to the satisfaction of the Engineer. All costs for testing are incidental to the respective item being tested. For phased projects, the tests must be completed by phase. The Contractor must maintain the test results throughout the entire project as well as during the warranty period that meet the following:

- Earth resistance testing methods shall be submitted to the Engineer for approval. Earth resistance testing results shall be recorded on an approved form and testing shall be performed in the presence of the Engineer. All such testing shall be at the sole expense of the Contractor.

- Should the counterpoise or ground grid conductors be damaged or suspected of being damaged by construction activities the Contractor shall test the conductors for continuity with a low resistance ohmmeter. The conductors shall be isolated such that no parallel path exists and tested for continuity. The Engineer shall approve of the test method selected. All such testing shall be at the sole expense of the Contractor.

After installation, the Contractor shall test and demonstrate to the satisfaction of the Engineer the following:

- That all affected lighting power and control circuits (existing and new) are continuous and free from short circuits.

- That all affected circuits (existing and new) are free from unspecified grounds.

- That the insulation resistance to ground of all new non-grounded circuits or cable segments Meet the requirements in Table 108-1 Insulation Resistance Minimum Requirements. Test durations shall be 60 seconds (minimum) or until reading has stabilized. Tests shall be performed with all isolation transformers and connectors in place as a complete circuit.

Notify the Engineer of any test results not meeting the desired insulation resistance values for further consideration. Verify continuity of all series airfield lighting circuits prior to energization.

TABLE 108-1. INSULATION RESISTANCE MINIMUM REQUIREMENTS

| Voltage Rating of Cable/Circuit | Minimum Test Voltage (DC) | Desired Insulation Resistance (megohms) | Minimum Insulation Resistance (megohms) |
| --- | --- | --- | --- |
| 5000V | 1000V | 2000 | 500 |
| 600V | 1000V | 1000 | 150 |

Notes: 	1.	Minimum Table 108-1 values from AC 5340-26 and FAA Conditional MOS

(ANC_2021_26294).

2. If calculating insulation resistance values, field test results or Table 108-1

minimums may not meet calculated values.

- That all affected circuits (existing and new) are properly connected per applicable wiring diagrams.

- That all affected circuits (existing and new) are operable. Tests shall be conducted that include operating each control not less than 10 times and the continuous operation of each lighting and power circuit for not less than 1/2-hour.

- That the impedance to ground of the installed grounding electrode system at each building or structure does not exceed 25 ohms prior to acceptance and/or establishing connections to other grounding electrode systems. The fall-of-potential ground impedance test shall be used, as described by American National Standards Institute/Institute of Electrical and Electronic Engineers (ANSI/IEEE) Standard 81, to verify this requirement. As an alternate, clamp-on style ground impedance test meters may be used to satisfy the impedance testing requirement.  Test equipment and its calibration sheets shall be submitted for review and approval by the Engineer prior to performing the testing.

Two copies of tabulated results of all cable tests performed shall be supplied by the Contractor to the Engineer. Where connecting new cable to existing cable, insulation resistance tests shall be performed on the new cable prior to connection to the existing circuit.

Whenever the scope of work requires connection to an existing circuit, the existing circuit’s insulation resistance shall be tested in the presence of the Engineer. The test shall be performed per these Specifications and prior to any activity that will affect the respective circuit. When the work affecting the circuit is complete, the circuit’s insulation resistance shall be checked again in the presence of the Engineer.

The Contractor shall record the results of both tests on forms acceptable to the Engineer. When circuits have similar conditions (length, number of transformers) before and after the project work, the two test results shall be similar. When circuits conditions have been changed, the results of the two tests shall be considered by the Engineer for differences deemed abnormal based on the circuit changes performed and the test results of the new circuit portions described above.

The Contractor shall make the necessary repairs to the existing circuit as required to correct test results inconsistent with the circuit changes made. All repair costs including replacement of the L-823 connectors, L-830 transformers and L-824 cable, if necessary, will be the Contractor’s responsibility. All test results will be submitted in the Operation and Maintenance (O&M) Manual.

There are no approved “repair” procedures for items that have failed testing other than complete replacement of the materials causing the failed tests.

METHOD OF MEASUREMENT

108-4.1 TRENCHING. Trenching will not be measured for payment. Excavation, backfill, bedding, dewatering and restoration will be subsidiary to the unit price bid for the work.

108-4.2 CABLE OR COUNTERPOISE WIRE. Cable or counterpoise wire installed in trench, duct bank or conduit will be measured by the number of linear feet installed, with grounding connectors, and trench marking tape ready for operation, and accepted as satisfactory. Separate measurement will be made for each cable or counterpoise wire installed in trench, duct bank or conduit. The measurement for this item will include additional quantities required for slack as shown on the Plans and indicated in these Specifications.

108-4.3 GROUND RODS. Ground rods will be measured by the number of ground rods installed in place, completed, ready for operation, and accepted as satisfactory. If the pay item for ground rods is absent from the bid schedule, no separate payment will be made. All work, materials, and equipment required for ground rods will be subsidiary to the associated equipment or system.

108-4.4 LUMP SUM. Lump sum items will not be measured for payment per GCP section 90.

108-4.5 UNDERGROUND CABLE REMOVAL. Removal of underground cable shall be subsidiary to the removal of the associated equipment served by the cable as shown and described on the Plans, unless otherwise indicated.

108-4.6 TEMPORARY JUMPER. Temporary jumper by unit price shall be measured by the number of linear feet of new temporary jumper cable measured in place, ready for operation, and accepted as satisfactory. The unit price shall include all terminations, securing of cables, disconnections, and reconnections required for relocation of the jumpers due to construction activities; maintenance of the jumpers for the duration of their use; and removal when no longer required.

108-4.7 CABLE CONNECTIONS. No separate payment will be made for cable connections.

BASIS OF PAYMENT

108-5.1 Payment will be made at the contract unit price for trenching, cable and bare counterpoise wire installed in trench (direct-buried), or cable and equipment ground installed in duct bank or conduit, in place by the Contractor and accepted by the Engineer. This price shall be full compensation for furnishing all materials and for all preparation and installation of these materials, and for all labor, equipment, tools, and incidentals, including ground rods and ground connectors and trench marking tape, necessary to complete this item.

Payment will be made under:

Item L108.010.1006	Underground Cable #6 AWG, Copper, 5kV FAA Type B, L-824 - per linear foot

Item L108.020.2006	Underground Cable #6 AWG, Copper, 5kV FAA Type C, L-824 - per lump sum

Item L108.030.0006	#6 Bare Copper Ground Conductor - per linear foot

Item L108.040.0006	#6 Bare Copper Ground Conductor - per lump sum

References

The publications listed below form a part of this specification to the extent referenced. The publications are referred to within the text by the basic designation only.

Advisory Circulars (AC)

AC 150/5340-26	Maintenance of Airport Visual Aid Facilities

AC 150/5340-30	Design and Installation Details for Airport Visual Aids

AC 150/5345-7	Specification for L-824 Underground Electrical Cable for Airport Lighting Circuits

AC 150/5345-26	Specification for L-823 Plug and Receptacle, Cable Connectors

AC 150/5345-53	Airport Lighting Equipment Certification Program

Commercial Item Description

A-A-59544A	Cable and Wire, Electrical (Power, Fixed Installation)

A-A-55809	Insulation Tape, Electrical, Pressure-Sensitive Adhesive, Plastic

ASTM International (ASTM)

ASTM B3	Standard Specification for Soft or Annealed Copper Wire

ASTM B8	Standard Specification for Concentric-Lay-Stranded Copper Conductors, Hard, Medium-Hard, or Soft

ASTM D4388	Standard Specification for Nonmetallic Semi-Conducting and Electrically Insulating Rubber Tapes

Mil Spec

MIL-I-24391	Insulation Tape, Electrical, Plastic, Pressure Sensitive

National Fire Protection Association (NFPA)

NFPA 70	National Electrical Code (NEC)

NFPA 780	Standard for the Installation of Lightning Protection Systems

American National Standards Institute (ANSI)/Institute of Electrical and Electronics Engineers (IEEE)

ANSI/IEEE STD 81	IEEE Guide for Measuring Earth Resistivity, Ground Impedance, and Earth Surface Potentials of a Ground System

Federal Aviation Administration Standard

# Comments

Note to Designer:

MOS Condition:  1. Please save the document responding to my questions submitted 08/16/2021 (from the sponsor via Patrick Zettler) to the MOS record.

2. As the sponsor's own response concedes, new cable insulation typically tests in the Gig ohm range, new installed airfield cable insulation must test to a 150 meg ohm minimum.

3. If the grounding rods test at above 25 ohms, the Engineer of record may defer to the submitted table for guidance and acceptance.

4. The terms approved in MOS are specific and applicable to this project and its conditions only, and are not applicable to any other project.

NOTE TO DESIGNER: When installing three conductors or cables into a raceway, ensure that the ratio of the raceway (inside diameter) to the conductor or cable ((outside diameter) does not fall between 2.8 and 3.2, or jamming may occur. Reference NEC Ch. 9, Table 1, Informational Note No. 2.