## ITEM L-115 ELECTRICAL MANHOLES

DESCRIPTION

115-1.1 This item shall consist of electrical manholes installed per this Specification, at the indicated locations and conforming to the lines, grades and dimensions shown on the Plans or as required by the Engineer. This item shall include the installation of each electrical manhole with all associated excavation, backfilling, sheeting and bracing, concrete, reinforcing steel, ladders, appurtenances, testing, dewatering and restoration of surfaces to the satisfaction of the Engineer, including removal of existing manholes as shown on the Plans.

EQUIPMENT AND MATERIALS

115-2.1 General. All other equipment and materials covered by other referenced specifications shall be subject to acceptance through the manufacturer’s certification of compliance with the applicable specification when requested by the Engineer.

115-2.2 Concrete structures.  Concrete shall be proportioned, placed, and cured per P-610 Concrete for Miscellaneous Structures.  Cast-in-place concrete structures shall be as shown on the Plans.

If the Contractor chooses to propose a different structural design, the Contractor shall submit signed and sealed shop drawings, design load ratings, and other information requested by the Engineer for evaluation by the Engineer, per review process defined in GCP subsection 60-08.

115-2.3 Precast concrete structures. Precast concrete structures shall be furnished by a plant meeting National Precast Concrete Association Plant Certification Program or another third party certification program approved by the Engineer.  Provide precast concrete structures where shown on the Plans. Precast concrete structures shall conform to ASTM C478, where applicable.

Precast concrete structures shall be designed by the manufacturer. Precast units shall have mortar or bitumastic sealer placed between all joints to make them watertight. The structure shall be designed to withstand the loadings specified or shown on the Plans . Openings or knockouts for conduit entries, drains, and ground rods shall be provided in the structure as shown on the Plans.

Threaded inserts and pulling eyes shall be cast in as shown on the Plans.

Submit signed and sealed shop drawings, design load ratings, and other information requested by the Engineer for evaluation by the Engineer per the process defined in the GCP subsection 60-08.

115-2.4 Junction boxes.  Refer to L-125 for requirements regarding all work and materials to install junction boxes and handholes.

115-2.5 Mortar. The mortar shall be composed of one part of cement and two parts of mortar sand, by volume. The cement shall be per the requirements in ASTM C150, Type I. The sand shall be per the requirements in ASTM C144. Hydrated lime may be added to the mixture of sand and cement in an amount not to exceed 15% of the weight of cement used. The hydrated lime shall meet the requirements of ASTM C206. Water shall be potable, reasonably clean and free of oil, salt, acid, alkali, sugar, vegetable, or other substances injurious to the finished product.

115-2.6 PORTLAND CEMENT Concrete. Refer to P-610 for requirements regarding work and materials to place Portland cement concrete.

115-2.7 Frames and covers. The frames shall conform to one of the following requirements:

- ASTM A48	Gray iron castings

- ASTM A47	Malleable iron castings

- ASTM A27	Steel castings

- ASTM A283, Grade D	Structural steel for grates and frames

- ASTM A536	Ductile iron castings

- ASTM A897	Austempered ductile iron castings

All castings or structural steel units shall conform to the dimensions shown on the Plans and shall be designed to support the loadings specified or shown on the Plans for the associated manhole.

Each frame and cover unit shall be provided with fastening members to prevent it from being dislodged by traffic, but which will allow easy removal for access to the structure.  Unless otherwise indicated, frames and covers shall be hinged. Cast iron covers shall be provided with a spring-assist mechanism for opening.

All castings shall be thoroughly cleaned. After fabrication, structural steel units shall be galvanized to meet the requirements of ASTM A123.

Each cover shall have the word “ELECTRIC” or other approved designation cast on it. Each frame and cover shall be as shown on the Plans or approved equivalent. No cable notches are required.

Where required, each manhole shall be provided with a “DANGER -- PERMIT-REQUIRED CONFINED SPACE, DO NOT ENTER” safety warning sign as detailed in the Contract Documents and in accordance with OSHA 1910.146 (c)(2).

115-2.8 Ladders. Ladders, if specified, shall be galvanized steel or as shown on the Plans.

115-2.9 Reinforcing steel. All reinforcing steel shall be deformed bars of new billet steel meeting the requirements of ASTM A615, Grade 60.

115-2.10 Bedding/special backfill. Bedding or special backfill shall be as shown on the Plans.

115-2.11 Flowable backfill. Flowable material used to backfill shall conform to the requirements of P-153 Controlled Low Strength Material.

115-2.12 Cable trays and racks. Cable trays and racks shall be non-metallic and located as shown on the Plans.

115-2.13 conduit. Conduit shall comply with L-110 Airport Underground Electrical Duct Banks and Conduits.

115-2.14 Conduit terminators. Conduit terminators shall be pre-manufactured for the specific purpose and sized as required or as shown on the Plans.

115-2.15 Pulling-in irons. Pulling-in irons shall be manufactured with 7/8-inch diameter hot-dipped galvanized steel or stress-relieved carbon steel roping designed for concrete applications (7 strand, 1/2-inch diameter with an ultimate strength of 270,000 pounds per square inch (psi)). Where stress-relieved carbon steel roping is used, a rustproof sleeve shall be installed at the hooking point and all exposed surfaces shall be encapsulated with a polyester coating to prevent corrosion.

115-2.16 Ground rods. Ground rods shall be one piece, copper clad steel. The ground rods shall be of the length and diameter specified on the Plans, but in no case shall they be less than 10 feet long or less than 3/4-inch in diameter.

CONSTRUCTION METHODS

115-3.1 Unclassified excavation. It is the Contractor’s responsibility to locate existing utilities within the work area prior to excavation. Damage to utility lines, through lack of care in excavating, shall be repaired or replaced to the satisfaction of the Engineer without additional expense to the Department.

The Contractor shall perform excavation for structures and structure footings to the lines and grades or elevations shown on the Plans or as staked by the Engineer. The excavation shall be of sufficient size to permit the placing of the full width and length of the structure or structure footings shown.

All excavation shall be unclassified.

Boulders, logs and all other objectionable material encountered in excavation shall be removed. All rock and other hard foundation material shall be cleaned of all loose material and cut to a firm surface either level, stepped or serrated, as directed by the Engineer. All seams, crevices, disintegrated rock and thin strata shall be removed. When concrete is to rest on a surface other than rock, special care shall be taken not to disturb the bottom of the excavation. Excavation to final grade shall not be made until just before the concrete or reinforcing is to be placed.

The Contractor shall provide all bracing, sheeting and shoring necessary to implement and protect the excavation and the structure as required for safety or conformance to governing laws. The cost of bracing, sheeting and shoring shall be included in the unit price bid for the structure.

Unless otherwise provided, bracing, sheeting and shoring involved in the construction of this item shall be removed by the Contractor after the completion of the structure. Removal shall be effected in a manner that will not disturb or mar finished masonry. The cost of removal shall be included in the unit price bid for the structure.

After each excavation is completed, the Contractor shall notify the Engineer. Structures shall be placed after the Engineer has approved the depth of the excavation and the suitability of the foundation material.

Prior to installation the Contractor shall provide a minimum of 6 inches of sand or a material approved by the Engineer as a suitable base to receive the structure. The base material shall be compacted and graded level and at proper elevation to receive the structure in proper relation to the conduit grade or ground cover requirements, as shown on the Plans.

115-3.2 Concrete structures. Concrete structures shall be built on prepared foundations conforming to the dimensions and form indicated on the Plans. The concrete and construction methods shall conform to the requirements specified in P-610. Any reinforcement required shall be placed as indicated on the Plans and shall be approved by the Engineer before the concrete is placed.

115-3.3 Precast unit installations. Precast units shall be installed plumb and true. Joints shall be made watertight by use of sealant at each tongue-and-groove joint and at roof of manhole. Excess sealant shall be removed and severe surface projections on exterior of neck shall be removed.

115-3.4 Placement and treatment of castings, frames and fittings. All castings, frames and fittings shall be placed in the positions indicated on the Plans or as directed by the Engineer and shall be set true to line and to correct elevation. If frames or fittings are to be set in concrete or cement mortar, all anchors or bolts shall be in place and position before the concrete or mortar is placed. The unit shall not be disturbed until the mortar or concrete has set.

Field connections shall be made with bolts, unless indicated otherwise. Welding will not be permitted unless shown otherwise on the approved shop drawings and written approval is granted by the casting manufacturer. Erection equipment shall be suitable and safe for the workman. Errors in shop fabrication or deformation resulting from handling and transportation that prevent the proper assembly and fitting of parts shall be reported immediately to the Engineer and approval of the method of correction shall be obtained. Approved corrections shall be made at Contractor’s expense.

Anchor bolts and anchors shall be properly located and built into connection work. Bolts and anchors shall be preset by the use of templates or such other methods as may be required to locate the anchors and anchor bolts accurately.

Pulling-in irons shall be located opposite all conduit entrances into structures to provide a strong, convenient attachment for pulling-in blocks when installing cables. Pulling-in irons shall be set directly into the concrete walls of the structure.

115-3.5 Installation of ladders. Ladders shall be installed such that they may be removed if necessary. Mounting brackets shall be supplied top and bottom and shall be cast in place during fabrication of the structure or drilled and grouted in place after erection of the structure.

115-3.6 Removal of sheeting and bracing. In general, all sheeting and bracing used to support the sides of trenches or other open excavations shall be withdrawn as the trenches or other open excavations are being refilled. That portion of the sheeting extending below the top of a structure shall be withdrawn, unless otherwise directed, before more than 6 inches of material is placed above the top of the structure and before any bracing is removed. Voids left by the sheeting shall be carefully refilled with selected material and rammed tight with tools especially adapted for the purpose or otherwise as may be approved.

The Engineer may direct the Contractor to delay the removal of sheeting and bracing if, in his judgment, the installed work has not attained the necessary strength to permit placing of backfill.

115-3.7 Backfilling. After a structure has been completed, the area around it shall be backfilled in horizontal layers not to exceed 6 inches in thickness measured after compaction to the density requirements in P-152. Each layer shall be deposited all around the structure to approximately the same elevation. The top of the fill shall meet the elevation shown on the Plans or as directed by the Engineer.

Backfill shall not be placed against any structure until approval is given by the Engineer. In the case of concrete, such approval shall not be given until tests made by the laboratory under supervision of the Engineer establish that the concrete has attained sufficient strength to provide a factor of safety against damage or strain in withstanding any pressure created by the backfill or the methods used in placing it.

Where required, the Engineer may direct the Contractor to add, at his own expense, sufficient water during compaction to assure a complete consolidation of the backfill. The Contractor shall be responsible for all damage or injury done to conduits, duct banks, structures, property or persons due to improper placing or compacting of backfill.

115-3.8 Connection of duct banks. Duct bank and conduit openings shall be grounded solid with non-shrink grout after installation of conduits but prior to backfilling. To relieve stress of joint between concrete-encased duct banks and structure walls, reinforcement rods shall be placed in the structure wall and shall be formed and tied into duct bank reinforcement at the time the duct bank is installed.

115-3.9 Grounding. Manhole grounding shall be as shown on the Plans. Where shown, a ground rod shall be installed in the floor of all concrete structures so that the top of rod extends 6 inches above the floor. The ground rod shall be installed within one foot of a corner of the concrete structure. Ground rods shall be installed prior to casting the bottom slab. Where the soil condition does not permit driving the ground rod into the earth without damage to the ground rod, the Contractor shall drill a 4-inch diameter hole into the earth to receive the ground rod. The hole around the ground rod shall be filled throughout its length, below slab, with Portland cement grout. Ground rods shall be installed in precast bottom slab of structures by drilling a hole through bottom slab and installing the ground rod. Bottom slab penetration shall be sealed watertight with Portland cement grout around the ground rod.  Where shown, ground rods shall be installed outside the manhole with a ground wire extended into the manhole through a conduit sleeve. The sleeve shall be sealed watertight.

Where shown, a grounding bus of 4/0 bare stranded copper shall be exothermically bonded to the ground rod and loop the concrete structure walls or a copper ground bar shall be mounted to the structure wall. The ground bus shall be a minimum of one foot above the floor of the structure and separate from other cables. #6 American wire gauge (AWG) bare copper pigtails shall bond the grounding bus to all covers, frames, metallic cable trays and other metal hardware within the concrete structure. Connections to the cable-type grounding bus shall be exothermic. If an exothermic weld is not possible, connections to the grounding bus shall be made by using compression connectors approved for direct burial in soil or concrete per UL 467.  Connections to a ground bar shall be two-hole lugs.  Hardware connections may be mechanical, using a lug designed for that purpose.

115-3.10 Cleanup and repair. After erection of all galvanized items, damaged areas shall be repaired by applying a liquid cold-galvanizing compound per MIL-P-21035. Surfaces shall be prepared and compound applied per the manufacturer’s recommendations.

Prior to acceptance, the entire structure shall be cleaned of all dirt and debris.

115-3.11 Restoration. After the backfill is completed, the Contractor shall dispose of all surplus material, dirt and rubbish from the site. The Contractor shall restore all disturbed areas equivalent to or better than their original condition.

The Contractor shall grade around structures as required to provide positive drainage away from the structure.

Areas with special surface treatment, such as roads, sidewalks, or other paved areas shall have backfill constructed and compacted to match surrounding areas, and surfaces shall be repaired using materials comparable to original materials.

Following restoration of all trenching near airport movement surfaces, the Contractor shall thoroughly visually inspect the area for foreign object debris (FOD), and remove any such FOD that is found.

After all work is completed, the Contractor shall remove all tools and other equipment, leaving the entire site free, clear and in good condition.

115-3.12 Inspection. Prior to final approval, the electrical structures shall be thoroughly inspected for conformance with the Plans and this Specification. Any indication of defects in materials or workmanship shall be further investigated and corrected.

115-3.13 Manhole elevation adjustments. The Contractor shall adjust the tops of existing manholes in areas designated on the Plans to the new elevations shown. The Contractor shall be responsible for determining the exact height adjustment required to raise or lower the top of each manhole to the new elevations. The existing top elevation of each manhole to be adjusted shall be determined in the field and subtracted/added from the proposed top elevation.

The Contractor shall remove/extend the existing top section or ring and cover on the manhole structure or manhole access. The Contractor shall install precast concrete sections or grade rings of the required dimensions to adjust the manhole top to the new proposed elevation or shall cut the existing manhole walls to shorten the existing structure, as required by final grades. The Contractor shall reinstall the existing manhole top section or ring and cover on top or install a new top section and cover and check the new top elevation.  All new cast in place or precast manhole sections, covers, or other components required for elevation adjustment shall meet the requirements of this Specification for new manholes and shall be designed to support the loadings indicated in the Specifications, or shown on the Plans.

Where shown, the Contractor shall construct a concrete slab around the top of adjusted structures located in graded areas that are not to be paved. The concrete slab shall conform to the dimensions shown on the Plans.

115-3.14 Duct extension to existing ducts. Where existing concrete encased ducts are to be extended, the duct extension shall be concrete encased plastic conduit. The fittings to connect the ducts together shall be standard manufactured connectors designed and approved for the purpose. The duct extensions shall be installed according to the concrete encased duct detail and as shown on the Plans.

METHOD OF MEASUREMENT

115-4.1 ELECTRICAL MANHOLE. Electrical manholes shall be measured by each unit completed in place and accepted. The following items shall be included in the price of each unit:  All required excavation and dewatering; sheeting and bracing; all required backfilling with on-site materials; restoration of all surfaces and finished grading and turfing; all required connections; temporary cables and connections; and grounding.

115-4.2 ADJUST ELECTRICAL Manhole. Manhole elevation adjustments shall be measured by the completed unit installed, in place, completed, and accepted. Separate measurement shall not be made for the various types and sizes.

BASIS OF PAYMENT

115-5.1 The accepted quantity of electrical manholes will be paid for at the Contract unit price per each, complete and in place. This price shall be full compensation for furnishing all materials and for all preparation, excavation, backfilling and placing of the materials, furnishing and installation of appurtenances and connections to duct banks and other structures as may be required to complete the item as shown on the Plans and for all labor, equipment, tools and incidentals necessary to complete the work.

- Subsidiary Work. Work listed is subsidiary to the respective L-115 pay items requiring its use.

  - All unclassified excavation, subgrade and embankment work.

  - Dewatering necessary for structure installation and erosion protection per federal, state, and local requirements.

  - All sodding, grading and restoration work.

  - FOD inspection and removal.

115-5.2 Payment shall be made at the contract unit price for manhole elevation adjustments. This price shall be full compensation for furnishing all materials and for all preparation, assembly, and installation of these materials, and for all labor, equipment, tools, and incidentals necessary, including but not limited to, spacers, concrete, rebar, dewatering, excavating, backfill, topsoil, sodding and pavement restoration, where required, to complete this item as shown in the Plans and to the satisfaction of the Engineer.

Payment will be made under:

Item L115.010.0000	Electrical Manhole – per each

Item L115.020.0000	Adjust Electrical Manhole – per each

References

The publications listed below form a part of this Specification to the extent referenced. The publications are referred to within the text by the basic designation only.

ASTM International (ASTM)

ASTM A27	Standard Specification for Steel Castings, Carbon, for General Application

ASTM A47	Standard Specification for Ferritic Malleable Iron Castings

ASTM A48	Standard Specification for Gray Iron Castings

ASTM A123	Standard Specification for Zinc (Hot Dip Galvanized) Coatings on Iron and Steel Products

ASTM A283	Standard Specification for Low and Intermediate Tensile Strength Carbon Steel Plates

ASTM A536	Standard Specification for Ductile Iron Castings

ASTM A615	Standard Specification for Deformed and Plain Carbon-Steel Bars for Concrete Reinforcement

ASTM A897	Standard Specification for Austempered Ductile Iron Castings

ASTM C144	Standard Specification for Aggregate for Masonry Mortar

ASTM C150	Standard Specification for Portland Cement

ASTM C206	Standard Specification for Finishing Hydrated Lime

Mil Spec

MIL-P-21035	Paint High Zinc Dust Content, Galvanizing Repair