## ITEM L-150	WEATHERPROOF OUTLETS

DESCRIPTION

150-1.1 Provide a complete and operational system of weatherproof outlets, 120 volts Alternating Current (AC) receptacles, at designated locations as shown on the Plans.

This work shall include all materials and incidentals necessary to place the outlets in operation as a completed unit to the satisfaction of the Engineer. This work shall also include removal and disposal of equipment and materials as shown on the Plans, and testing of the system. Excavation and backfill required for installation of new system components are included in this work.

MATERIALS

150-2.1 GENERAL. All other equipment and materials covered by other referenced specifications shall be subject to acceptance through manufacturer's certification of compliance with the applicable specification when requested by the Engineer.  Provide materials that are listed for their intended use.

150-2.2 ELECTRICAL. Unless otherwise noted, comply with L-108 Underground Power Cable for Airports, L-110 Airport Underground Electrical Duct Banks and Conduits, and L-125 Installation of Airport Lighting Systems for handholes, junction boxes, conduit, wiring, grounding, and other associated work and equipment.

Receptacles shall be 20-amp, 120-volt, GFCI type with LED protection indicator.  Receptacles shall be rated weather-resistant and provided with a padlock capable, metallic weatherproof-in-use cover plate.

Unless specifically described elsewhere, use standard commercial grade wiring devices, boxes, and other equipment suitable for the location where they will be installed.

Provide load center or meter center and electrical service to power weatherproof outlets. Unless otherwise   noted, comply with L-160 Electrical Load Centers and L-161 Electrical Meter Centers as applicable. Provide quantity of meters and circuit breakers as indicated on the Plans.

150-2.3 CONCRETE. Concrete shall be proportioned, placed, and cured per P-610 Concrete for Miscellaneous Structures.

150-2.4 RACEWAY, CONDUCTORS, AND CONNECTORS.  Provide wiring with copper conductors, type XHHW-2 insulation, in rigid steel or HDPE conduit outdoors and Electrical Metallic Tubing (EMT) or Intermediate Metal Conduit (IMC) indoors except where specifically noted or specified otherwise.

Use solderless lug connections for #6 American Wire Gauge (AWG) copper conductors and larger. Use insulated wire nut connections for #8 AWG copper conductor and smaller.

Identify conductors with the system voltage color code.  Conductors larger than #6 AWG may be color-coded by wrapping ends with colored tape at each termination, except that white (or gray) and green insulated conductors shall not be phase-taped for any use other than neutral and ground respectively.  Color-coding for the installation shall follow Table 150-1.

TABLE 150-1. COLOR-CODING FOR CONDUCTORS

|  | 240/120 volts, 1-phase, 3-wire | 208/120 volts, 3-phase, 4-wire |
| --- | --- | --- |
| Phase A | Black | Black |
| Phase B | Red | Red |
| Phase C | - | Blue |
| Neutral | White | White |
| Ground | Green | Green |

CONSTRUCTION METHODS

150-3.1 Perform sitework, and installation of distribution panel, equipment supports, wiring systems, and all components and accessories as shown on the Plans and included in these Specifications.

Perform work in accordance with the latest versions of National Electrical Code (NEC) and International Building Code (IBC) as adopted by the State of Alaska and in accordance with other applicable codes and statutes. Unless otherwise indicated, install material and equipment in accordance with the manufacturer’s recommendations, instructions, and installation drawings, and in accordance with National Electrical Contractors Association’s (NECA) National Electrical Installation Standards (NEIS).

When penetrating building wall assemblies with conduit, seal penetrations with Underwriters Laboratories (UL) listed fireproofing materials to maintain fireproofing integrity and watertightness, as applicable.

When penetrating electrical enclosures, maintain integrity of enclosure rating and watertightness.

Support receptacle and service equipment on approved types of wall brackets, receptacle posts, and other support structures as shown on the Plans.

Repair damage to finished surfaces where caused by installation of electrical equipment.

Make trenches for placement of underground circuits. Install conduit, wiring, and grounding as shown on the Plans and according to L-108 Underground Power Cable for Airports and L-110 Airport Underground Electrical Duct Banks and Conduits.

150-3.2 TESTING.  Furnish all necessary testing equipment, labor, materials, supplies, and power for conducting operating tests on the completed installation. Include functional demonstrations of all installed equipment.

Provide operational test and insulation resistance test per L-108 Underground Power Cable for Airports.  Repair systems that do not test satisfactorily at no additional cost to the Department and retest.

METHOD OF MEASUREMENT

150-4.1 LUMP SUM. Lump sum quantities will not be measured for payment per GCP section 90.

BASIS OF PAYMENT

150-5.1 Payment will be made according to GCP Section 90 at the contract price for provision of the weatherproof outlet system and the following. Payment is for a complete, operating system. The lump sum price is full compensation for removal and disposal of existing materials, furnishing all supplies, material and labor required to prepare the site and to install all equipment and materials to complete the work, including all installation, connections, testing, and commissioning.

- Subsidiary Work.

  - Portland Cement Concrete. Portland cement concrete is subsidiary to L-150 pay items requiring its use. Refer to P-610 for requirements regarding all work and materials to place Portland cement concrete.

  - Underground Power Cables. Underground power cables are subsidiary to L-150 pay items requiring their use. Refer to L-108 for requirements regarding all work and materials to install underground power cables.

  - Underground Electrical Duct Banks and Conduits. Underground electrical duct banks and conduits are subsidiary to L-150 pay items requiring their use. Refer to L-110 for requirements regarding all work and materials to install underground electrical duct banks and conduits.

  - Handholes and Junction Boxes. Handholes and junction boxes are subsidiary to L-150 pay items requiring their use. Refer to L-125 for requirements regarding all work and materials to install handholes and junction boxes.

Payment will be made under:

Item L150.010.0000	Weatherproof Outlets – per lump sum

# Comments

Note to Designers:

MOA Condition: Grounding requirements shall comply with the National Electric Code.