## ITEM L-155	FLOOD LIGHTING

DESCRIPTION

155-1.1 Furnish and install a flood lighting system to include driven pile or concrete bases, poles, bullhorns, fixtures, obstruction lighting, photoelectric cells, lighting contactors, wiring systems, and appurtenances.

This work shall include all sitework, wiring, connections to new service equipment, and all other materials, equipment, accessories, and labor necessary to provide a complete and operational flood lighting system to the satisfaction of the Engineer. This work shall also include removal and disposal of all equipment and materials as shown on the Plans, and testing of the system. Excavation and backfill required for installation of new system components is included in this work.

MATERIALS

155-2.1 GENERAL. All other equipment and materials covered by other referenced specifications shall be subject to acceptance through manufacturer's certification of compliance with the applicable specification when requested by the Engineer. Unless specifically described elsewhere, use standard commercial grade light fixtures, wiring devices, boxes and other equipment that are suitable for the location installed.

Provide new materials, listed for the intended use, that conform to the requirements indicated in these Specifications and as shown on the Plans.

155-2.2 ELECTRICAL. Unless otherwise noted, comply with L-108 Underground Power Cable for Airports, L-110 Airport Underground Electrical Duct Banks and Conduits, and L-125 Installation of Airport Lighting Systems for handholes, junction boxes, conduit, wiring, grounding, and other associated work and equipment.

155-2.3 CONCRETE. Concrete shall be proportioned, placed, and cured per P-610 Concrete for Miscellaneous Structures.

155-2.4 RACEWAY, CONDUCTORS, AND CONNECTORS.  Provide wiring with copper conductors, type XHHW-2 insulation, in rigid steel or HDPE conduit outdoors and Electrical Metallic Tubing (EMT) or Intermediate Metal Conduit (IMC) indoors except where specifically noted or specified otherwise.

Use solderless lug connections for #6 American Wire Gauge (AWG) copper conductors and larger. Use insulated wire nut connections for #8 AWG copper conductor and smaller.

Use solderless lug connections for #6 American Wire Gauge (AWG) copper conductors #6 and larger. Use insulated wire nut connections for  #8 AWG copper conductors #8 and smaller.

Identify conductors with the system voltage color code.  Conductors larger than #6 AWG may be color-coded by wrapping ends with colored tape at each termination, except that white (or gray) and green insulated conductors shall not be phase-taped for any use other than neutral and ground respectively.  Color-coding for the installation shall follow Table 155-1.

TABLE 155-1. COLOR-CODING FOR CONDUCTORS

|  | 240/120 volts, 1-phase, 3-wire | 208/120 volts, 3-phase, 4-wire |
| --- | --- | --- |
| Phase A | Black | Black |
| Phase B | Red | Red |
| Phase C | - | Blue |
| Neutral | White | White |
| Ground | Green | Green |

155-2.5 APRON FLOODLIGHT. Apron floodlight shall be LED, 4000K maximum color temperature, full-cutoff fixture, with light output and accessories as indicated on the Plans.

155-2.6 PHOTOELECTRIC CONTROL. If shown on the Plans or indicated in these Specifications, the Contractor shall furnish and install an automatic control switch at the location shown on the Plans. The switch shall be a photoelectric type, standard commercially available unit complying with UL 773, with supply voltage rating of 120-277V AC, integral surge protection, -40°F to 140°F temperature range, and EEI-NEMA standard twist-lock mounting base with matching receptacle.  The photoelectric switch shall be installed, connected, and adjusted per the manufacturer’s instructions.

CONSTRUCTION METHODS

155-3.1 Perform work in accordance with the latest versions of National Electrical Code (NEC) and International Building Code (IBC) as adopted by the State of Alaska, in accordance with other applicable codes and statutes, and according to the requirements of the utility company furnishing services to the installation. Secure and pay for all inspections, fees, permits, etc. required by local and state agencies.

Unless otherwise indicated, install material and equipment in accordance with the manufacturer’s recommendations, instructions, and installation drawings, and in accordance with National Electrical Contractors Association’s (NECA) National Electrical Installation Standards (NEIS).

When penetrating building wall assemblies with conduit, seal penetrations with Underwriters Laboratories (UL) listed fireproofing materials to maintain fireproofing integrity and watertightness, as applicable.

When penetrating electrical enclosures, maintain integrity of enclosure rating and watertightness.

Repair damage to finished surfaces where caused by installation of electrical equipment.

Make trenches for placement of underground circuits. Install conduit, wiring, and grounding as shown on the Plans and according to L-108 Underground Power Cable for Airports and L-110 Airport Underground Electrical Duct Banks and Conduits.

155-3.2 TESTING.  Furnish all necessary testing equipment, labor, materials, supplies, and power for conducting operating tests on the completed installation. Include functional demonstrations of all installed equipment.  Provide operational test and insulation resistance test per L-108 Underground Power Cable for Airports.  Repair systems that do not test satisfactorily at no additional cost to the Department and retest.

METHOD OF MEASUREMENT

155-4.1 LUMP SUM. Lump sum quantities will not be measured for payment per GCP section 90.

BASIS OF PAYMENT

155-5.1 Payment will be made according to GCP Section 90 at the contract price for provision of the flood lighting system and the following. Payment is for a complete, operating system. The lump sum price is full compensation for removal and disposal of existing materials, furnishing all supplies, material and labor required to prepare the site and to install all equipment and materials to complete the work, including all installation, connections, testing, and commissioning.

- Subsidiary Work.

  - Portland Cement Concrete. Portland cement concrete is subsidiary to L-155 pay items requiring its use. Refer to P-610 for requirements regarding all work and materials to place Portland cement concrete.

  - Underground Power Cables. Underground power cables are subsidiary to L-155 pay items requiring their use. Refer to L-108 for requirements regarding all work and materials to install underground power cables.

  - Underground Electrical Duct Banks and Conduits. Underground electrical duct banks and conduits are subsidiary to L-155 pay items requiring their use. Refer to L-110 for requirements regarding all work and materials to install underground electrical duct banks and conduits.

  - Handholes and Junction Boxes. Handholes and junction boxes are subsidiary to L-155 pay items requiring their use. Refer to L-125 for requirements regarding all work and materials to install handholes and junction boxes.

Payment will be made under:

Item L155.010.0000	Flood Lighting – per lump sum