## ITEM L-160	ELECTRICAL LOAD CENTERS

DESCRIPTION

160-1.1 Furnish and install load center assemblies at the locations indicated in the Plans. Modify existing load centers when indicated.

The work shall include all materials and incidentals necessary to place the system in operation as a completed unit to the satisfaction of the Engineer. This work shall also include removal and disposal of all equipment and materials as shown on the Plans, and testing of the system. Excavation and backfill required for installation of new system components is included in this work.

Use load centers of the following types as shown on the Plans in load center detail sheets:

- Type 1. Pad mounted with underground service (large)

- Type 1A. Pad mounted with underground service (small)

- Type 2. Post mounted with underground service

- Type 3. Pole mounted with overhead service

MATERIALS

160-2.1 GENERAL. All other equipment and materials covered by other referenced specifications shall be subject to acceptance through manufacturer's certification of compliance with the applicable specification when requested by the Engineer.

160-2.2 ELECTRICAL. Unless otherwise noted, comply with L-108 Underground Power Cable for Airports, L-110 Airport Underground Electrical Duct Banks and Conduits, and L-125 Installation of Airport Lighting Systems for handholes junction boxes, conduit, wiring, grounding, and other associated work and equipment.

160-2.3 CONCRETE. Concrete shall be proportioned, placed, and cured per P-610 Concrete for Miscellaneous Structures.

160-2.4 Conform to the standards of National Electrical Code (NEC), the National Electrical Safety Code (NESC), and local safety codes as adopted and amended by the authority having jurisdiction. Use materials that conform to applicable National Electrical Manufacturers Association Standards (NEMA) and American National Standards Institute (ANSI) standards, the Materials Certification List, the Plans, specifications, and the following:

- Grout. Use non-shrink, non-corrosive, non-metallic, cement-based grout meeting requirements of American Society for Testing and Materials (ASTM) C1107, except  develop a 28-day compressive strength of 9,000 psi when tested according to AASHTO T 106 or ASTM C109.

- Wood Posts. Construction grade, 6 x 6-inch nominal dimension S4S Douglas Fir, Hem-Fir, Western Larch, Western Hemlock, Mountain Hemlock or Southern Pine meeting Standard Grading and Dressing Rules, West Coast Lumber Inspection Bureau. Treat posts using preservatives and treatment processes in accordance with American Association of State Highway Transportation Officials (AASHTO) M 133 and Best Management Practices for the Use of Treated Wood in Aquatic Environments (BMPs), published by the Western Wood Preservers Institute, 12503 SE Mill Plain Blvd., #205, Vancouver, WA 98684 (Phone: 360-693-9958).  Treat products according to American Wood Protection Association (AWPA) Standard U1, Commodity Specification A: Sawn Products for soil and freshwater applications meeting Use Category 4B.

- Load Center. NEMA 3R enclosure constructed of zinc-coated A60 finish sheet steel per ASTM A653 and ASTM A924, with no external screws, bolts, or nuts.

Shop coat cabinet components with a 2-part urethane paint undercoat and 2-part urethane finish coats. Finish coats must be standard white for removable panels and non-gloss silver-gray, closely matching FSS No. 5950 Color No. 36622, for the enclosure.

The load center must be labeled as a unit by a State of Alaska-approved independent electrical testing laboratory (such as UL, ETL, CSA, etc.) defined by ANSI Standard Z34.1 Third-Party Certification Programs for Products Processes and Services and conform to applicable published standards noted herein, the Plans, and Special Provisions. The load center must be marked with the maximum available fault current and the date the fault current calculation was performed.  The marking must be sufficiently durable to withstand the environment. The load center must be labeled as service entrance equipment.

- Panelboards. Load panels in load centers must conform to FSS W-P-115C, Type 1 - Circuit Breaker Panelboards; Underwriters Laboratories (UL) 67 - Panelboards; and NEMA PB1 - Panelboards with Molded Case Circuit Breakers. The rated voltage of the panels must be as noted on the load center summary in the Plans, 120/240volt or 240/480-volt single phase or 120/208-volt or 277/480-volt three-phase. The ampacity rating of panels must not be less than the ampacity noted on the load center summary, 100 amps minimum, at rated voltage. Provide separate copper neutral and ground buses.

A label must be applied to the exterior of the panelboard indicating the potential arc flash hazard at the enclosure.  The label must comply with NEC 110.16(A) and must include the information required by NFPA 70E, including the estimated arc flash incident energy as calculated per IEEE 1584.

- Circuit Breakers. Use bolt-on type circuit breakers. The series rated interrupting capacity of the circuit breakers in the panels must not be less than shown on the load center summary, or 10,000 ampere interrupting capacity (AIC) minimum, at rated voltage.  Ensure that the circuit breakers installed are rated to be operated in the ambient temperatures to which they will be exposed.

Use circuit breakers that are molded-case thermal-magnetic types with single-trip indicating switch handle. They must have an enclosed toggle type operating mechanism with quick-make/quick-break action and have a trip-free disconnect from the switch handle that will prevent the contacts from being held in the closed position. The circuit breakers must have the frame size, interrupting capacities, and trip rating clearly marked on the breaker. Multi-pole circuit breakers must have a common trip mechanism.

Contacts must be silver alloy enclosed in an arc quenching chamber. Overload trip ratings must be self-compensating for ambient temperatures from 14 °F to 140 °F. Circuit breakers must be 240 or 277-volt maximum rated for 120/240/277-volt circuits, whichever is applicable, and have an interrupting capacity (RMS - symmetrical) of not less than 10,000 amperes. They must have not less than 480-volt rating for circuits above 277 volts and have an interrupting capacity (RMS - symmetrical) of not less than 14,000 amperes.

- Contactor. Electrically-held type consisting of an operating coil, a laminated armature, contacts, and terminals. Contacts must be fine silver, silver alloy, or superior alternative material rated to switch the specified load, 30 amperes minimum at rated voltage, and be normally open, unless otherwise noted. Contactor coils must be rated for operation at 240 volts Alternating Current (AC).

- Meters. Equip all meter sockets mounted in Type-1 and Type-1A load centers with internal mounted meters with manual circuit closing devices. The devices may be either the link or lever type. Do not use the horn and sliding types. Equip all load centers with internal mounted meters with safety sockets (that is, provisions for de-energizing the meter jaws). The test section cover must be sealable with a 0.047-inch stainless steel bail.

- Transformers. Transformers in load centers containing load panels of different nominal voltages must be isolated winding type with primary and secondary voltages and kilo-volt amperes (kVA) ratings as noted on the Plans. Transformers must carry rated volt-amperes continuously without exceeding a 240°F temperature rise above a 100°F ambient temperature.

Where installed outside of the load center enclosure, use a non-ventilated transformer enclosure fabricated from aluminum, stainless steel, or galvanized steel and filled with high-melting point, thermal setting, or epoxy insulating compounds to prevent moisture from entering the winding enclosure. Coat enclosures fabricated from sheet metal with moisture-resistant paint. Insulate transformer leads with non-hygroscopic material and extend them 9 inches beyond the winding chamber seal.

- Conductors. Stranded copper with either type XHHW-2 or RHW insulation.

- Conduit. Galvanized rigid conduit made of mild steel meeting UL standard UL-6.

- Terminals. Size all terminals according to the amperage ratings of the conductor used. They must be suitable for termination of copper and aluminum conductors.

- Photoelectric Controls. Photoelectric controls shall be standard commercially available unit complying with UL 773, with supply voltage rating of 120-277V AC, integral surge protection, -40°F to 140°F temperature range, and EEI-NEMA standard twist-lock mounting base with matching receptacle.  The photoelectric switch shall be installed, connected, and adjusted per the manufacturer’s instructions.

- Galvanizing. Hot-dip galvanize all anchor bolts, nuts, washers, tie-rods, clamps, and other miscellaneous ferrous parts in conformance with AASHTO M 232. After galvanizing, ensure that the bolt threads accept galvanized standard nuts without requiring tools or causing removal of protective coatings.

Galvanize rigid metal conduit in conformance with AASHTO M 232.

Hot-dip galvanize structural steel shapes, plates, bars and their products according to AASHTO M 111.

Repair damage to galvanized coatings per AASHTO M 36.

- Equipment List(s) and Drawings. Within 30 days after the Contract award, submit eight (8) collated copies of a portfolio of equipment and materials proposed for installation to the Department for review and approval. Include a table of contents in the portfolio(s) that includes each item’s intended use(s) and the following:

- Materials on the Qualified Products List: A description that includes product name, manufacturer, model or part number, and the conditions listed for approval.

- Materials Not on the Qualified Products List: Catalog cuts that include the manufacturer’s name, type of product, size, model number, conformance specifications, and other data as may be required, including manufacturer’s maintenance and operations manuals, or sample articles.

- Materials Not Requiring Certification: Incidental materials incorporated into the work (such as nuts, ties, bolts, washers, etc.) must meet all applicable Specifications and be installed per all manufacturer’s recommendations. Certification is not needed unless required by the Special Provisions or requested by the Engineer.

CONSTRUCTION METHODS

160-3.1 Install load centers at the location and position shown on the Plans. Any deviation from the plan location must be coordinated with and approved by the serving utility and the Engineer.

Furnish conduit, conductors, contactors, breakers, transformers, and all other necessary materials at all new and modified load centers to complete the installation.

Install a rigid metal conduit of the size shown in the Plans at a 30-inch depth from the load center and extend it to a location 2 feet from the power source. Install a pull rope in the conduit, cap the end, and mark the terminus with a 2-inch x 4-inch stake or 1-inch rebar, 3 feet long. Extend the end of the stake or bar 1 inch above the ground. When the servicing utility requires the complete conduit and weather head to be in place on the designated service pole, furnish and install all materials required by the utility. The additional work and materials are subsidiary to the load center bid item.

Where the service is to be installed on a utility-owned pole, coordinate the positioning of the riser and service equipment with the service utility.

House circuit breakers, switches, and contactors in a NEMA 3R type enclosure listed by an approved independent electrical testing laboratory as service equipment with a hinged and locking front cover. Indelibly label panel covers with the circuit number. Legend plates, labels, and signs must be engraved plastic or metal fastened with screws, non-cold-susceptible adhesive, or component mounting hardware.

Size and wire load center cabinets to serve all of the circuits shown in the Plans. Each cabinet must be a single enclosure subdivided to form compartments as required. Include hinged lockable door(s) or panel cover(s) with provision for a padlock with a 5/16-inch diameter shackle for each compartment. Circuit breaker ratings must be as shown in the load center summary for each location.

Wire and equip load centers with commonly metered thaw wire and lighting circuits with separate contactors, selector switches, and terminal blocks for lighting and thaw wire circuits. Control the thaw wires as described in D-760 Thaw Pipe and Thaw Wires.

Where a meter is required, furnish and install a meter socket that is acceptable to the serving utility, complete with sealing rings. Do not mount the meter socket on doors or removable panels.

Load centers containing contactors must have contactor control switches mounted in the load distribution section. Control switches for systems having automatic controls (for example, photo cell, thermostats, or time controls) must be 3-position types with the positions labeled “On”, “Off” and “Auto”. Control switches for manual control only must be a 2-position type with positions labeled “On” and “Off”. Label each switch to identify function being controlled.

Mount transformer fuses in dead-front fuse holders with lighted blown fuse indicators, where required. Label them to indicate function and fuse amp rating.

Install a 3/4-inch x 10-foot copper clad ground rod inside the base readily accessible through the removable cover, or adjacent to the supporting post. Install one or two rods as required by the serving utility or as shown on the Plans. Connect ground rod to ground bus with a soft-drawn copper grounding electrode conductor sized per NEC, #6 AWG minimum. Bond all non-current carrying metal parts of the load center to the ground bus.  Install main bonding jumper between the ground and neutral bus.

Locate the photo cell for lighting control on the nearest light standard or top of the load center as shown on the load center summary. Orient it to the unobstructed northern sky. Submit for approval the method of attachment of the conduit to the load center. Use either a 3/C or a 5/C #14 AWG cable to connect the photo cell to the load center. When the photo cell is on a lighting standard with a slip base or frangible coupling style base, use an approved break-away disconnect in the base of the light standard. Restrain the cable in a similar manner as the illumination cable in the pole base.

Provide a typed circuit directory for each load panel inside of the load center door, protected with a plastic cover, describing each circuit, with even and odd numbered circuit breaker positions shown on separate parts of the directory. Provide a power and control one-line diagram protected by a laminated plastic cover inside the load center. Include the following information on the directory and one-line diagram: Load center identification (A, B, etc.), Project Name, Project number (Federal/State) and Service Voltage.

160-3.2 TESTING.  Provide operational test and insulation resistance test per L-108 Underground Power Cable for Airports.  Repair systems that do not test satisfactorily at no additional cost to the Department and retest.

METHOD OF MEASUREMENT

160-4.1 LOAD CENTER.  The quantity to be paid will be the actual number of load centers, modified load centers, and transformers completed and accepted as shown on the Plans or as directed by the Engineer.

BASIS OF PAYMENT

160-5.1 Payment will be made according to GCP section 90 at the contract price for provision of the load center and the following. Payment is for a complete, operating unit. The price is full compensation for furnishing all supplies, material and labor required to prepare the site and to install all equipment and materials to complete this item, including all installation, connections, testing, and commissioning.  Load circuits, consisting of conduits and conductors attached to the load centers and photoelectric controls, and terminations of field wiring, are subsidiary to other work.

- Subsidiary Work.

  - Portland Cement Concrete. Portland cement concrete is subsidiary to L-160 pay items requiring its use. Refer to P-610 for requirements regarding all work and materials to place Portland cement concrete.

  - Underground Power Cables. Underground power cables are subsidiary to L-160 pay items requiring their use. Refer to L-108 for requirements regarding all work and materials to install underground power cables.

  - Underground Electrical Duct Banks and Conduits. Underground electrical duct banks and conduits are subsidiary to L-160 pay items requiring their use. Refer to L-110 for requirements regarding all work and materials to install underground electrical duct banks and conduits.

  - Handholes and Junction Boxes. Handholes and junction boxes are subsidiary to L-160 pay items requiring their use. Refer to L-125 for requirements regarding all work and materials to install handholes and junction boxes.

Payment will be made under:

Item L160.___.____	Load Center, Type ____ – per each

Item L160.050.0000	Modify Load Center – per each

# Comments

Note to Designer:

MOA Condition: Equipment shall be rated NEMA 3R or higher as needed