STATE OF ALASKA

DEPARTMENT OF TRANSPORTATION

AND PUBLIC FACILITIES

STANDARD SPECIFICATIONS

FOR

AIRPORT CONSTRUCTION

(Advisory Circular 150/5370-10A, Standards for Specifying Construction of Airports,

as modified, and approved by the Federal Aviation Administration

for Airport Improvement Program contracts in Alaska)

US Customary

NOTE: Special Provisions for each project are marked as changes to the text of the Standard Specifications. Deleted text is identified by strikethrough. Additions are underlined. The location of each Special Provision is shown by a vertical bar in the margin.

NOTICE TO USERS

These Standard Specifications are intended for use in contracts for the construction of airport improvements in the State of Alaska, funded under the Airport Improvement Program (AIP). They represent the standards contained in FAA Advisory Circular (AC) 150/5370-10A, Standards for Specifying Construction of Airports, as modified by the State of Alaska Department of Transportation and Public Facilities under the authority of FAA Order 5300.1, Approval Level for Modification of Agency Airport Design and Construction Standards.

Specifications included herein are effective as of the date shown on the page footers. Subsequent changes to AC 150/5370-10A, issued by the FAA, will govern over these specifications.

These Standard Specifications are to be supplemented, as necessary, by appropriate Special Provisions included in the contract. Special Provisions must be approved by the FAA, prior to advertising.

Special Provisions for each project are to be marked as changes to the text of the Standard Specifications. Deleted text is to be identified by strikethrough. Additions are to be underlined. Indicate the location of each Special Provision by a vertical bar in the margin. Retain the original effective dates of the base Standard Specification (shown on all page footers). Extentions may be added to a footer date to identify revision by Special Provision. Example:  8/01 (rev 9/15/01)

Airport sponsors must consult the latest published FAA Advisory Circular Checklist for any pertinent changes, prior to final design. A listing of FAA Advisory Circulars is available on the FAA web site at: http://www.faa.gov/arp/arphome.htm.

These specifications are designed to meet the requirements for primary airports, but are generally suitable for the construction of all commercial service airports (both primary and nonprimary) as well as general aviation airports. However, they will not fit every situation. It is intended that the designer refer to the “notes to the Engineer” in the most current AC 150/5370-10A in order to ensure that the specifications for the project will meet applicable FAA standards and to review other acceptable specification options available.

AC 150/5370-10A will govern for standard items not modified by this document.

Airport designers must incorporate the Materials Sampling & Testing Frequency table (Appendix) in each advertised contract.

Further modification of these Standard Specifications is permitted only in accordance with FAA Order 5300.1.

CONTENTS

Effective

Date

PART I - GENERAL PROVISIONS

Section 10. Definitions and Terms		7/02

Section 20. Bidding Requirements and Conditions		7/02

Section 30. Award and Execution of Contract		8/01

Section 40. Scope of Work		7/02

Section 50. Control of Work		8/01

Section 60. Control of Materials		7/02

Section 70. Legal Relations and Responsibility to Public		7/02

Section 80. Prosecution and Progress		7/02

Section 90. Measurement and Payment		8/01

Section 100. Contractor Quality Control Program		7/02

Section 110. Method of Estimating Percentage of Material Within Specification Limits (PWL)		8/01

PART II - EARTHWORK

Item P-151 Clearing and Grubbing		7/02

Item P-152 Excavation and Embankment 		7/02

Item P-154 Subbase Course		8/01

Item P-157 Erosion, Sediment, and Pollution Control (over 5 acres)		7/02

Item P-158 Erosion, Sediment, and Pollution Control (5 acres or less)		7/02

PART III - AGGREGATE BASE & SURFACE COURSES

Item P-208 Aggregate Surface Course		7/02

Item P-209 Crushed Aggregate Base Course		7/02

PART V - FLEXIBLE SURFACE COURSES

Item P-401 Plant Mix Bituminous Pavement		7/02

PART VI - RIGID PAVEMENT

Item P-501 Portland Cement Concrete Pavement		7/02

PART VII - MISCELLANEOUS

Item P-602 Bituminous Prime Coat		8/01

Item P-603 Bituminous Tack Coat		8/01

Item P-605 Joint Sealing Filler		8/01

Item P-606 Adhesive Compound		8/01

Item P-609 Seal Coats and Bituminous Surface Treatment		7/02

Item P-610 Structural Portland Cement Concrete		8/01

Item P-620 Runway and Taxiway Painting		8/01

Item P-625 Coal-Tar Pitch Emulsion Seal Coat		8/01

Item P-626 Emulsified Asphalt Slurry Seal Surface Treatment		7/02

Item P-630 Pavement Grooving		8/01

Item P-640 Segmented Circle		8/01

Item P-650 Aircraft Tie-Down		8/01

PART VIII - FENCING

Item F-160 Wire Fence with Wood Posts		8/01

Item F-161 Wire Fence with Steel Posts		8/01

Item F-162 Chain Link Fence		8/01

PART IX - DRAINAGE

Item D-701 Storm Drains and Culverts		7/02

Item D-702 Slotted Drains		8/01

Item D-705 Pipe Underdrains		8/01

Item D-751 Manholes, Catch Basins, Inlets, and Inspection Holes		8/01

Item D-752 Concrete Culverts, Headwalls, and Miscellaneous Drainage Structures		8/01

Item D-754 Concrete Gutters, Ditches, and Flumes		8/01

PART X - TURFING

Item T-901 Seeding		8/01

Item T-905 Topsoiling		7/02

Item T-908 Soil Stabilization		8/01

PART XI - LIGHTING INSTALLATION

Item L-100 Runway & Taxiway Lighting		7/02

Item L-101 Rotating Beacon		8/01

Item L-103 Beacon Tower		8/01

Item L-107 Wind Cone		8/01

Item L-108 Underground Cable		7/02

Item L-109 Transformer Vault and Vault Equipment		7/02

Item L-110 Underground Electrical Duct		7/02

Item L-119 Obstruction Lights		8/01

PART XII - STRUCTURES

Item S-143 Fuel Tank		8/01

PART XIII - CONTRACTOR FURNISHED SERVICES

Item G-100 Mobilization and Demobilization		8/01

Item G-120 Disadvantaged Business Enterprise (DBE) Program		8/01

Item G-130 Services to be Furnished by the Contractor		8/01

Item G-131 Engineering Transportation		8/01

Item G-135 Construction Surveying and Monuments		8/01

Item G-150 Equipment Rental		8/01

PART XIV - MARINE AVIATION FACILITIES

(Reserved)

APPENDIX

Materials Sampling & Testing Frequency		8/01

PART I - GENERAL PROVISIONS

SECTION 10

DEFINITIONS AND TERMS

10-01 GENERAL. Wherever in the Specifications or other contract documents the following abbreviations and terms, or pronouns in place of them, are used, the intent and meaning shall be interpreted as set forth below.

Terms not defined below shall have their ordinary accepted meanings within the context in which they are used. Words which have a well-known technical or trade meaning when used to describe work, materials or equipment shall be interpreted in accordance with such meaning.

The titles and headings of the sections, subsections and subparts herein are intended for convenience of reference and shall not be considered as having bearing on their interpretation. Working titles which have a masculine gender, such as "workman" and "flagman" and the pronouns and adjectives "he", "his" and "him" are utilized in the contract documents for the sake of brevity, and are intended to refer to persons of either sex.

When a publication is specified, it shall refer to the most recent date of issue prior to the date of advertisement for the project unless the issue as of a specific date or year is specified.

In order to avoid cumbersome and confusing repetition of expressions in these Specifications, it is provided that whenever anything is, or is to be, done, if, as, or, when, or where "contemplated, required, determined, directed, specified, authorized, ordered, given, designated, indicated, considered necessary, deemed necessary, permitted, reserved, suspended, established, approval, submitted, approved, disapproved, acceptable, unacceptable, suitable, unsuitable, accepted, satisfactory, unsatisfactory, sufficient, insufficient, rejected, or condemned," it shall be understood as if the expression were followed by the words "by the Engineer" or "to the Engineer".

Any reference to a specific requirement of a numbered paragraph of the contract specifications or a cited standard shall be interpreted to include all general requirements of the entire section, specification item, or cited standard that may be pertinent to such specific reference.

Some specifications are written in an abbreviated format, incomplete sentences, or active voice grammar. Omission of words or phrases such as “a”, “an”, “the”, “the Contractor shall”, “unless otherwise specified”, or “unless otherwise directed” is intentional. These Specifications are written to the Contractor. All actions required, unless otherwise noted, are to be performed by the Contractor or his agent.

10-02 ACRONYMS. Wherever the following abbreviations are used in these Specifications or on the Plans, they are to be construed the same as the respective expression represented:

AAN	American Association of Nurserymen

AASHTO	American Association of State Highway and Transportation Officials

AC	Advisory Circular

ACI	American Concrete Institute

AGC	Associated General Contractors of America

AIA	American Institute of Architects

AIP	Airport Improvement Program

ANSI	American National Standards Institute

AOA	Air Operations Area

AS	Alaska Statute

ASTM	American Society for Testing & Materials

ATM	Alaska Test Methods (Alaska Test Manual)

BLM	Bureau of Land Management, Department of Interior

FAA	Federal Aviation Administration

FOP	Field Operating Procedure (See Alaska Test Manual)

FSS	Flight Service Station

ICEA	Insulated Cable Engineers Association (formerly IPCEA)

NEC	National Electrical Code

NEMA	National Electrical Manufacturers Association

UL	Underwriters Laboratory

WAQTC	Western Alliance for Quality in Transportation Construction (See Alaska Test Manual)

10-03 DEFINITIONS.

ACCEPTANCE TESTS. Tests and inspections by the Department to determine the acceptability of materials incorporated into the work.

ACCESS ROAD. The right-of-way, the roadway, and all improvements constructed thereon connecting the airport to another public thoroughfare.

ADDENDA. Clarifications, corrections, or changes to the Plans, Specifications or other contract documents issued graphically or in writing by the Department after the advertisement but prior to the opening of bids.

ADVERTISEMENT. The public announcement, as required by law, inviting bids for work to be performed or materials to be furnished.

AIR OPERATIONS AREA (AOA). For the purpose of these Specifications, the term air operations area shall mean any area of the airport used or intended to be used for the landing, takeoff, or surface maneuvering of aircraft. An air operation area shall include such paved or unpaved areas that are used or intended to be used for the unobstructed movement of aircraft in addition to its associated runway, taxiway, or apron.

AIRPORT. Airport means an area of land or water which is used or intended to be used for the landing and takeoff of aircraft, and includes its buildings and facilities, if any.

Airport Improvement Program (AIP). A grant-in-aid program, administered by the FAA.

AWARD. The acceptance, by the Department, of the successful bid. The award is effective upon execution of the contract by the Contracting Officer.

BID. The offer of a bidder, on the prescribed forms, to perform the work at the prices quoted.

BID BOND. A type of bid guaranty.

BIDDER. An individual, firm, corporation or any acceptable combination thereof, or joint venture submitting a bid for the advertised work.

BID GUARANTY. The security furnished with a bid to guarantee that the bidder will enter into a contract if his bid is accepted by the Department

CALENDAR DAY. Every day shown on the calendar beginning and ending at midnight.

CHANGE ORDER. A written order by the Department covering changes to the contract, within its general scope, and establishing the basis of payment and time adjustment, if any, for the work affected.

COMPLETION DATE. The date on which all contract work is specified to be completed.

CONTINGENT SUM PAY ITEM. When the bid schedule contains a Contingent Sum Pay Item, the work covered shall be performed only upon written directive by the Engineer and payment will be made as specified in the directive.

CONTRACT. The written agreement between the Department and the Contractor setting forth the obligations of the parties for the performance of the work.

The contract includes the Invitation For Bids, Bid Form, Bid Schedule, Construction Contract Form, Contract Bonds, Standard Specifications, Special Provisions, Plans, Addenda and any change orders, directives or supplemental agreements that are required to complete the construction of the work in an acceptable manner, all of which constitute one instrument.

CONTRACTING OFFICER. The person authorized by the Commissioner to enter into and administer the contract on behalf of the Department. He has authority to make findings, determinations and decisions with respect to the contract and, when necessary, to modify or terminate the contract.

The Contracting Officer is identified on the Invitation For Bids.

CONTRACT ITEM (PAY ITEM). A specifically described item of work for which a price is provided in the contract.

CONTRACTOR. The individual, partnership, firm, corporation, or any acceptable combination thereof, contracting with the Department for performance of prescribed work.

CONTRACT TIME. The time allowed under the contract, including authorized time extensions, for the completion of all work by the Contractor and specified either in calendar days or by completion date.

CONTROLLING ITEM. Any feature of the work considered at the time by the Engineer as essential to the orderly completion of the work and which, if delayed, will delay the time of completion of the contract (such as an item of work on the critical path of a network schedule.)

CULVERT. Any structure not classified as a bridge which provides an opening under the embankment.

DEPARTMENT. The Alaska Department of Transportation and Public Facilities.

DIRECTIVE. A written communication to the Contractor from the Engineer enforcing or interpreting a contract requirement or ordering commencement or suspension of an item of work already established in the Contract.

DRAINAGE SYSTEM. The system of pipes, ditches, and structures by which surface or subsurface waters are collected and conducted from the airport area.

ENGINEER. The authorized representative of the Contracting Officer who is responsible for administration of the contract.

EQUIPMENT. All machinery together with the necessary supplies for upkeep and maintenance, and also tools and apparatus necessary for the proper construction and acceptable completion of the work.

EXTRA WORK. An item of work not provided for in the contract as awarded but found essential by the Engineer for the satisfactory completion of the contract within its intended scope.

Federal Aviation Administration (FAA). Branch of the U.S. Department of Transportation. When used to designate a person, FAA shall mean the Administrator or his/her duly authorized representative.

FEDERAL SPECIFICATIONS. The Federal Specifications and Standards, Commercial Item Descriptions, and supplements, amendments, and indices thereto which are prepared and issued by the General Services Administration (GSA) of the Federal Government. They may be obtained from the Superintendent of Documents, U.S. Government Printing Office, Washington, D.C. 20402. The GSA is mandated to cancel Federal Specifications and replace them with commercially available alternatives. GSA-published alternatives will prevail over Federal Specifications referenced in this contract. Refer to the following website to determine the status of replaced Federal Specifications: <http://www.fss.gsa.gov/pub/fed-specs.cfm>

HOLIDAYS. In the State of Alaska, legal holidays occur on:

- New Year's Day - January 1

- Martin Luther King Jr.'s Birthday - Third Monday in January

- Presidents' Day - Third Monday in February

- Seward's Day - Last Monday in March

- Memorial Day - Last Monday in May

- Independence Day - July 4

- Labor Day - First Monday in September

- Alaska Day - October 18

- Veteran's Day - November 11

- Thanksgiving Day - Fourth Thursday in November

- Christmas Day - December 25

- Every Sunday

- Every day designated by public proclamation by the President of the United States or the Governor of the State as a legal holiday.

If any holiday listed above falls on a Saturday, Saturday and the preceding Friday are both legal holidays for officers and employees of the state. If the holiday should fall on a Sunday, except (l.) above, Sunday and the following Monday are both legal holidays (See Title 44, Alaska Statutes).

INSPECTOR. The Engineer's authorized representative assigned to make detailed inspections of contract performance.

Interim Work Authorization. A written order by the Engineer initiating changes to the Contract, within its general scope, until a subsequent Change Order is executed.

INVITATION FOR BIDS. The advertisement for bids for all work or materials on which bids are required.

LABORATORY. The official testing laboratories of the Department or such other laboratories as may be designated by the Engineer.

LIGHTING. A system of fixtures providing or controlling the light sources used on or near the airport or within the airport buildings. The field lighting includes all luminous signals, markers, floodlights, and illuminating devices used on or near the airport or to aid in the operation of aircraft landing at, taking off from, or taxiing on the airport surface.

MAJOR CONTRACT ITEM. Any contract item for which the product of the bid quantity and the unit bid price equals 10% or more of the contract award amount.

MATERIALS. Any substances specified for use in the construction of the project.

MINOR CONTRACT ITEM. Any contract item for which the product of the bid quantity and the unit bid price equals less than 10% of the contract award amount.

NOTICE OF INTENT TO AWARD. The written notice by the Department announcing the apparent successful Bidder and establishing the Department's intent to award the Contract when all required conditions are met.

NOTICE TO PROCEED. A written notice to the Contractor to begin the work and establishing the date on which Contract Time begins.

ORIGINAL GROUND (OG). The ground surface prior to the initiation of the proposed work.

PAVEMENT STRUCTURE. The combined surface course, base course, and subbase course, if any, considered as a single unit.

PAYMENT BOND. The security furnished by the Contractor and his surety to guarantee payment of the debts covered by the bond.

PERFORMANCE BOND. The security furnished by the Contractor and his surety to guarantee performance and completion of the work in accordance with the contract.

PLANS. The approved contract drawings, profiles, typical cross sections, working drawings and supplemental drawings, or reproductions thereof, which show the location, character, dimensions, and details of the work to be done.

PRECONSTRUCTION CONFERENCE. A meeting between the Contractor and the Engineer, and other parties affected by the construction, to discuss the project before the Contractor begins work.

PROFILE GRADE. The trace of a vertical plane intersecting the top surface of the layer shown on the typical section, usually along the longitudinal centerline of the runway, taxiway, or roadway. Profile grade means either elevation or gradient of such trace according to the context.

PROJECT. The specific section of the airport together with all appurtenances and construction to be performed thereon under the contract.

QUALITY CONTROL. Tests and inspections by the Contractor to insure the acceptability of materials incorporated into the work. Also known as process control.

RUNWAY. The area of the airport prepared for the landing and takeoff of aircraft.

RUNWAY SAFETY AREA (RSA). A defined surface surrounding the runway prepared or suitable for reducing the risk of damage to airplanes in the event of an undershoot, overshoot, or excursion from the runway.

SPECIAL PROVISIONS. Additions and revisions to the Standard Specifications covering conditions peculiar to an individual project.

SPECIALTY ITEMS. Contract items designated in the bid schedule which require equipment and crafts not ordinarily associated with the types of work covered by the contract.

SPECIFICATIONS. A general term applied to all directions, provisions and requirements pertaining to performance of the work.

STANDARD SPECIFICATIONS. Specifications approved for general application and repetitive use. The Standard Specifications for Airport Construction conform with AC 150/5370-10A, Standards for Specifying Construction of Airports, as modified for Alaskan conditions and as approved by the FAA. The Standard Specifications consist of the General Contract Provisions, and the Construction Specifications.

STATE. The State of Alaska acting through its authorized representative.

STRUCTURES. Airport facilities such as bridges; culverts; catch basins, inlets, retaining walls, cribbing; storm and sanitary sewer lines; water lines; underdrains; electrical ducts, manholes, handholes, lighting fixtures and bases; transformers; flexible and rigid pavements; navigational aids; buildings; vaults; and, other manmade features of the airport that may be encountered in the work and not otherwise classified herein.

SUBCONTRACTOR. An individual, partnership, firm, corporation or any acceptable combination thereof to whom the Contractor sublets part of the contract.

SUBGRADE. The top surface of the embankment or excavation upon which the pavement structure is constructed.

SUBSIDIARY. Not paid for directly. Compensation for such work is included in the payment for other items of work and no separate payment will be made.

SUPERINTENDENT. The Contractor's authorized representative in responsible charge of the work.

SUPPLEMENTAL AGREEMENT. A negotiated written agreement between the Department and the Contractor authorizing the performance of work beyond the general scope of the contract.

SURETY. The corporation, partnership or individual, other than the Contractor, executing a bond furnished by the Contractor.

TAXIWAY. The portion of the air operations area of an airport that has been designated for movement of aircraft to and from runways or aircraft parking areas.

TAXIWAY SAFETY AREA (TSA). A defined surface alongside the taxiway prepared or suitable for reducing the risk of damage to an airplane unintentionally departing the taxiway.

TRAFFIC CONTROL PLAN (TCP). A drawing of one or more specific plans that detail the routing of pedestrian and/or vehicular traffic through or around a construction area for work outside the air operations area.

UTILITY. The privately, publicly or cooperatively owned lines, facilities and systems for producing, transmitting or distributing communications, power, electricity, light, heat, gas, oil, crude products, water, steam, waste, storm water not connected with highway or runway drainage, and other similar commodities, including publicly owned fire and police signal systems, street lighting systems, and railroads which directly or indirectly serve the public or any part thereof. The term "utility" shall also mean the utility company, inclusive of any wholly owned or controlled subsidiary.

WORK. Work is the act of, and the result of, performing services, furnishing labor, furnishing and incorporating materials and equipment into the project and performing all other duties and obligations required by the contract.

WORKING DRAWINGS. Stress sheets, shop drawings, erection plans, falsework plans, framework plans, cofferdam plans, bending diagrams for reinforcing steel, wiring diagrams and schematics, or any other supplementary plans or similar data which the Contractor is required to submit to the Engineer for approval.

SECTION 20

BIDDING REQUIREMENTS AND CONDITIONS

20-01 QUALIFICATION OF BIDDERS. On Federal-Aid projects any Contractor otherwise qualified by the State to perform such work, is not required to be licensed nor to submit application for license in advance of submitting a bid or having such bid considered; provided, however, that such exemption does not constitute a waiver of the State's right under its license laws to require a Contractor, determined to be a successful bidder, to be licensed to do business as a Contractor in the State of Alaska in connection with the award of a contract to him.

On wholly State funded projects, all Bidders shall be required to submit evidence of their Contractor's Registration, under AS 08.18, and of their valid Alaska Business License at the time of bid.

Before a bid is considered for award, the bidder will submit a completed Contractor’s Questionnaire stating the bidder’s previous experience in performing comparable work, his business and technical organization, financial resources, and equipment available to be used in performing the contemplated work.

Nothing contained in this section shall be construed as depriving the Department of its discretion in the matter of determining the lowest responsible bidder.

20-02 CONTENTS OF BID FORMS. Upon request, the Department will furnish the prospective bidder with bid forms which will state the location and description of the contemplated construction and will show the approximate estimate of the various quantities and kinds of work to be performed or materials to be furnished, and will have a schedule of items for which unit bid prices are invited. The bid will state the time in which the work must be completed, the amount of the bid guaranty and the date, time and place for the opening of bids.

The Plans, Specifications, and other documents designated in the bid, will be considered a part of the bid whether attached or not and shall be the basis for the submitted bid.

20-03 INTERPRETATION OF QUANTITIES IN BID SCHEDULE. The quantities appearing in the bid schedule are approximate and are prepared for the comparison of bids. Payment to the Contractor will be made for the actual quantities of work performed and accepted or materials furnished in accordance with the contract. The scheduled quantities of work to be done and materials to be furnished may each be increased, decreased, or eliminated as provided herein.

20-04 EXAMINATION OF PLANS, SPECIFICATIONS, SPECIAL PROVISIONS AND SITE OF WORK. The bidder is expected to examine carefully the site of the proposed work and all Contract documents before submitting a bid. The submission of a bid shall be considered prima facie evidence that the bidder has made such examination and is satisfied as to the conditions to be encountered in performing the work and as to the requirements of the Plans, Specifications, Special Provisions, and contract.

Any explanation desired by bidders regarding the meaning or interpretation of drawings and specifications must be requested in writing and with sufficient time allowed for a reply to reach them before the submission of their bids. Any clarification or change to the Plans or Specifications will be in the form of an addendum furnished to all bidders.

Material Reports, Soils Investigation Reports, and other records are available for inspection by bidders. This information was obtained and is intended for Department design and estimating purposes. It is made available to bidders so that they may have access to identical information available to the Department, and is not intended as a substitute for personal investigation, interpretations, and judgment of the bidders.

20-05 PREPARATION OF BID. The bidder shall submit his bid on the forms furnished by the Department, or legible copies thereof. The bid schedule will provide for quotation of a price or prices for one or more Contract items which may include unit price or lump sum items and alternative, optional or supplemental price schedules or a combination thereof which will result in a total bid amount for the proposed work.

The bidder shall specify a unit price, in figures, for each pay item for which a quantity is given and shall also show the products of the respective unit prices and quantities written in figures in the column provided for that purpose and the total amount of the bid obtained by adding the amounts of the several items. All the figures shall be in ink or typed. In the event of a discrepancy between unit bid prices and extensions, the unit bid price shall govern. Any changes shall be initialed by the person signing the bid.

When an item in the bid contains a choice to be made by the bidder, the bidder shall indicate his choice in accordance with the Specifications for that particular item, and no further choice will be permitted.

The bidder's bid must be signed with ink. If the bidder is a corporation, the bid shall be signed by an individual having authority to sign the Contract. If the bidder is a partnership, the bid shall be signed by any authorized member of the partnership. If the bidder is a joint venture, the bid shall be signed by one or more representatives of the joint venture authorized to sign. If the bidder is a sole proprietorship, the bid shall be signed by the owner.

At certain bid openings a bidder may wish to submit bids on more projects than he desires to have awarded to him. The bidder may indicate the total amount desired to be accepted and the Department will determine which of his low bids on these projects, up to the final total indicated, will be accepted. This limitation will only apply when the bidder has added the following statement to the Bid Form for at least one of the projects being bid:

"We desire to disqualify all of our bids at this letting which exceed the total of $_____________ or ____ contract(s) and hereby authorize the Department to determine which bids shall be disqualified."

20-06 NON-RESPONSIVE BIDS. Bids may be considered non-responsive and rejected for the following reasons:

- The bid is on a form other than that furnished by the Department, or legible copies thereof; or if the form is altered or any part thereof is detached; or if the bid is improperly signed.

- There are unauthorized additions, conditional or alternative bids, or irregularities of any kind which may tend to make the bid incomplete, indefinite, or ambiguous as to its meaning.

- The bidder adds any provisions reserving the right to accept or reject any award, or to enter into a contract pursuant to an award, except for a maximum limit on the total amount of awards acceptable to the bidder at any one bid letting, as provided in Subsection 20-05.

- The bid does not contain a unit price for each pay item listed, except in the case of authorized alternate pay items.

- The bidder has not acknowledged receipt of each addendum by its assigned number and date.

- The bidder fails to furnish an acceptable bid guaranty with the bid.

- Any of the unit prices bid are excessively unbalanced (either above or below the amount of a reasonable bid) to the potential detriment of the Department.

20-07 BID GUARANTY. All bids shall be accompanied by a bid guaranty in the form of an acceptable Bid Bond (Form 25D-14), or a certified check, cashier's check or money order made payable to the State of Alaska. Bid Bonds must be accompanied by a legible Power of Attorney. The amount of the bid guaranty is specified on the Invitation for Bids.

The surety of a Bid Bond may be any corporation or partnership authorized to do business in Alaska as an insurer under AS 21.09.

An individual surety will not be accepted as a bid guaranty.

20-08 DELIVERY OF BIDS. Each bid should be submitted in a special envelope furnished by the Department. Do not include in the envelope any bids for other work. The envelope shall be labeled correctly to clearly indicate its contents. When an envelope other than the special one furnished by the Department is used, it shall be of the same general size and shape and be similarly marked to clearly indicate its contents. When sent by mail, the sealed bid shall be addressed to the Department at the address and in care of the official in whose office the bids are to be received.

Unless specifically called for, electronic or fax bids will not be considered.

20-09 WITHDRAWAL OR REVISION OF BIDS. A bidder may withdraw or revise a bid after it has been deposited with the Department, provided that the request for such withdrawal or revision is received by the designated office, in writing or by fax, before the time set for opening of bids.

Revisions shall include both the modification of the unit bid price and the total modification of each item modified, but shall not reveal the amount of the total original or revised bids.

20-10 COMBINATION BIDS. If the Department so elects, bids may be issued for projects in combination and/or separately, so that bids may be submitted either on the combination or on separate units of the combination. The Department reserves the right to make awards on combination bids or separate bids to the best advantage of the Department. No combination bids, other than those specifically set up on the bids by the Department, will be considered.

20-11 ADDENDA REQUIREMENTS. Addenda will be issued to the individual or company to whom bidding documents were issued. Addenda may be issued by any reasonable method such as mail, fax, telegram, or courier. Addenda will be issued to the address or telephone number as stated on the planholder’s list unless picked up in person or included with the bid documents. It is the bidder’s responsibility to insure that he has received all addenda affecting the Invitation for bids. No claim or protest will be allowed based on the bidder’s allegation that they did not receive all of the addenda for an Invitation for Bids. All addenda shall be acknowledged on the Bid Form or by fax prior to the scheduled time of bid opening. If no addenda are received by the bidder, the word "None" should be entered on the Bid Form.

20-12 RECEIPT AND OPENING OF BIDS. All bids, including any amendment or withdrawal, must be received by the Department prior to the scheduled time of bid opening in order to be considered.

Bids will be opened and read publicly at the time and place indicated in the Invitation for Bids.

No responsibility will attach to any officer or employee of the Department for the premature opening of, or failure to open, a bid improperly addressed or identified.

20-13 DISQUALIFICATION OF BIDDERS. Any of the following reasons may be considered as being sufficient for the disqualification of a bidder and the rejection of his bid or bids:

- Uncompleted work of a bidder which, in the judgment of the Department, might hinder or prevent the prompt completion of additional work if awarded.

- Failure to pay, or satisfactorily settle, all bills due for labor and material on previous contracts in force at the time of issuance of bids.

- Failure to comply with any qualification requirements of the Department.

- Default under previous contracts, or fraud or dishonesty in the performance of previous contracts.

- Unsatisfactory performance on previous work.

- Failure to reimburse the State for monies owed on any previous contracts.

- More than one bid for the same work from an individual, firm, or corporation under the same or different name.

- Evidence of bid rigging or collusion among bidders. Participants in collusion will receive no recognition as bidders for any future work of the Department until any such participant shall have been reinstated as a qualified bidder.

Nothing contained in this section shall deprive the Department of its discretion in the matter of determining the lowest responsive bidder.

20-14 FOREIGN TRADE RESTRICTION. (Federal-Aid Contracts)

The Contractor or subcontractor, by submission of an offer and/or execution of a contract, certifies that it:

- is not owned or controlled by one or more citizens or nationals of a foreign country included in the list of countries that discriminate against U.S. firms published by the Office of the United States Trade Representative (USTR);

- has not knowingly entered into any contract or subcontract for this project with a contractor that is a citizen or national of a foreign country on said list, or is owned or controlled directly or indirectly by one or more citizens or nationals of a foreign country on said list.

- has not procured any product nor subcontracted for the supply of any product for use on the project that is produced in a foreign country on said list.

Unless the restrictions of this clause are waived by the Secretary of Transportation in accordance with 49 CFR 30.17, no contract shall be awarded to a contractor or subcontractor who is unable to certify to the above. If the Contractor knowingly procures or subcontracts for the supply of any product or service of a foreign country on the said list for use on the project, the FAA may direct, through the sponsor, cancellation of the contract at no cost to the government.

Further, the Contractor agrees that, if awarded a contract resulting from this solicitation, it will incorporate this provision for certification without modification in each contract and in all lower tier subcontracts. The Contractor may rely upon the certification of a prospective subcontractor unless it has knowledge that the certification is erroneous.

The Contractor shall provide immediate written notice to the sponsor if the Contractor learns that its certification or that of a subcontractor was erroneous when submitted or has become erroneous by reason of changed circumstances. The subcontractor agrees to provide immediate written notice to the Contractor, if at any time it learns that its certification was erroneous by reason of changed circumstances.

This certification is a material representation of fact upon which reliance was placed when making the award. If it is later determined that the Contractor or subcontractor knowingly rendered an erroneous certification, the FAA may direct, through the sponsor, cancellation of the contract or subcontract for default at no cost to the Government.

Nothing contained in the foregoing shall be construed to require establishment of a system of records in order to render, in good faith, the certification required by this provision. The knowledge and information of a contractor is not required to exceed that which is normally possessed by a prudent person in the ordinary course of business dealings.

This certification concerns a matter within the jurisdiction of an agency of the United Stated of America and the making of a false, fictitious, or fraudulent certification may render the maker subject to prosecution under Title 18, United States Code, Section 1001.

SECTION 30

AWARD AND EXECUTION OF CONTRACT

30-01 CONSIDERATION OF BIDS. After the bids are opened and read, they will be compared on the basis of the summation of the products of the quantities shown in the bid schedule by the unit bid prices. The results of such comparisons will be made available to the public as soon as practicable. Until the award of the Contract the Department reserves the right to reject any or all bids, to waive minor informalities or to advertise for new bids without liability against the Department, if in the judgment of the awarding authority the best interests of the Department will be promoted thereby.

The apparent low bidder shall submit a completed Subcontractor List, form 25D-5, within 5 working days following receipt of written notification by the Department.

An apparent low bidder who fails to submit a completed Subcontractor List, form 25D-5, will be found not to be a responsible bidder and may be required to forfeit the bid security. The Department will then consider the next lowest bidder for the award of the Contract.

If a bidder fails to list a subcontractor or lists more than one subcontractor for a particular portion of work and the value of that work is in excess of one-half of one percent of the total bid, the bidder agrees to perform that portion of work without the use of a subcontractor and to have represented that he is qualified to perform that work.

A bidder who attempts to circumvent the requirements of this Subsection by listing as a subcontractor another contractor who, in turn, sublets the majority of the work required under the Contract, violates this Subsection.

If a contract is awarded to a bidder who violates this Subsection, the Contracting Officer may:

- cancel the contract without any damages accruing to the Department; or

- after notice and a hearing, assess a penalty on the bidder in an amount that does not exceed 10% of the value of the subcontract at issue.

A bidder may replace a listed subcontractor who:

- fails to comply with AS 08.18;

- files for bankruptcy or becomes insolvent;

- fails to execute a contract with the bidder involving performance of the work for which the subcontractor was listed and the bidder acted in good faith;

- fails to obtain bonding;

- fails to obtain insurance acceptable to the Department;

- fails to perform the Contract with the bidder involving work for which the subcontractor was listed;

- must be replaced in order for the prime contractor to satisfy required State and/or Federal affirmative action requirements;

- refuses to agree or abide with the bidder's labor agreement; or

- is determined by the Contracting Officer not to be responsible.

In addition to the circumstances described above, the Contractor may request permission from the Contracting Officer to add or replace a listed subcontractor. The request must be made in advance, in writing, specifically detailing the basis for the request, and shall include appropriate supporting documentation. The Contracting Officer will approve the request if it is determined to be in the best interest of the State.

30-02 AWARD OF CONTRACT. The successful bidder will be notified in writing of the Department's intent to award the Contract and requested to execute certain documents, including the contract form, bonds and insurance.

The Contract will not be awarded until receipt by the Department of all required documents, properly executed, within the time specified in the letter of intent to award. Failure to enter into a contract within the specified time shall be grounds for forfeiture of the bid security and consideration of the second low bidder for award.

The letter of award, if the Contract is to be awarded, will be issued to the lowest responsible and responsive bidder as soon as practicable.

For AIP contracts, no award shall be made until the FAA has concurred in the Department’s recommendation to make such award and has approved the Department's proposed contract to the extent that such concurrence and approval are required by 49 CFR Part 18.

30-03 RETURN OF BID GUARANTY. Bid guaranties, other than bid bonds, will be returned to all bidders, except the two low bidders, as soon as practicable after the opening of bids. The guaranty of the lowest and the second lowest bidder will be returned immediately after the contract has been awarded.

30-04 PERFORMANCE AND PAYMENT BONDS. The successful bidder shall furnish, when required, Performance and Payment Bonds on forms provided by the Department for the sums prescribed in the Contract. The surety on each bond may be any corporation or partnership authorized to do business in the State as an insurer under AS 21.09 or two responsible individual sureties approved by the Contracting Officer.

When individual sureties are used, two individual sureties must each provide the State with security equal to the amount of each bond. The net worth and the total value of the security assets, located in Alaska, of each individual surety may not be less than the penal amount of the bond. In addition, each individual surety must execute an affidavit of individual surety on a form provided upon request by the Department. Each individual surety affidavit contains a Certificate of Sufficiency which must be signed by an official of an institution having full knowledge of assets and responsibilities of the surety. Any costs incurred by the Contractor or individual surety shall be borne by the Contractor.

Individual sureties shall provide security by one, or a combination, of the following methods:

- Escrow account, with a Federally-insured financial institution, in the name of the Department. Acceptable securities would include, but not necessarily be limited to: cash, treasury notes, bearer instruments having a specific value or money market certificates.

- First deed of trust, with the Department named as beneficiary, against the unencumbered value of real property or an agreement by a second party, including deeds of trust, mortgage, lien or judgement interests to subrogate their interests to that of the Department in the real property which has been offered by the individual surety. A title insurance policy, with the Department as a named beneficiary, and a current (within 3 months) professional appraisal or assessed valuation will be required to ascertain the true value of the property offered as collateral. If buildings or other valued improvements are involved then fire and casualty insurance with the Department as a named insured and in limits and coverages acceptable to the Contracting Officer shall be required. The appraiser shall acknowledge in writing that the appraisal is prepared for the benefit of the Department and the Department has the right to rely on its contents. This deed must be recorded in the recording office where the property is located.

These bonds and security assets, as applicable, shall remain in effect for 12 months after the date of final payment and until all obligations and liens under this contract have been satisfied.

The Contracting Officer may, at his option, notify the surety of any potential default or liability.

If the surety on any bond furnished in connection with this Contract is declared bankrupt or becomes insolvent or its right to do business is terminated in any state where any part of the project is located or it ceases to meet the requirements above or otherwise becomes unacceptable to the Department, or if any such surety fails to furnish reports as to his financial condition as requested by the Department, the Contractor shall within five days thereafter substitute another bond and surety, both of which must be acceptable to the Department.

An individual Surety may be replaced by a corporate surety during the course of the Contract period. If the surety desires to dispose of the collateral posted, the Department may, at its option, accept substitute collateral.

30-05 INSURANCE REQUIREMENTS. The Contractor shall provide evidence of insurance with a carrier or carriers satisfactory to the Department covering injury to persons and/or property suffered by the State of Alaska or a third party, as a result of operations under this contract by the Contractor or by any subcontractor. This coverage will also provide protection against injuries to all employees of the Contractor and the employees of any subcontractor engaged in work under this contract. The delivery to the Department of a written 30 day notice is required before cancellation of any coverage or reduction in any limits of liability. Insurance carriers providing coverage shall have an acceptable financial rating.

The Contractor shall maintain in force at all times, during the performance of work under this contract, the following policies of insurance. All insurance policies shall comply with, and be issued by insurers licensed to transact the business of insurance under AS 21. Failure to maintain the specified insurance may, at the option of the Contracting Officer, be deemed as unacceptable work and remedied under Subsection 50-11. Where specific limits and coverages are shown, it is understood that they shall be the minimum acceptable. The requirements of this subsection shall not limit the Contractor's indemnity responsibility under Subsection 70-13. Additional insurance requirements specific to this contract are contained in the Special Provisions, when applicable.

- Workers’ Compensation Insurance: The Contractor shall provide and maintain, for all employees of the Contractor engaged in work under this contract, Workers’ Compensation Insurance as required by AS 23.30.045. The Contractor shall be responsible for Workers’ Compensation Insurance for any subcontractor who provides services under this contract, to include:

- Waiver of subrogation against the State and Employer’s Liability Protection in the amount of $500,000 each accident/$500,000 each disease.

- If the Contractor directly utilizes labor outside of the State of Alaska in the prosecution of the work, “Other States” endorsement shall be required as a condition of the contract.

- Whenever the work involves activity on or about navigable waters, the Workers’ Compensation policy shall contain a United States Longshoreman’s and Harbor Worker’s Act endorsement, and when appropriate, a Maritime Employer’s Liability (Jones Act) endorsement with a minimum limit of $1,000,000.

- Commercial General Liability Insurance: on an occurrence basis covering all operations by or on behalf of the Contractor with combined single limits not less than:

$1,000,000 Each Occurrence

$1,000,000 Personal Injury

$2,000,000 Products-Completed Operations Aggregate

$2,000,000 General Aggregate, Project

- Automobile Liability Insurance: covering all vehicles used by the Contractor in the performance of services under this agreement with combined single limits not less than $1,000,000 each occurrence.

The State of Alaska shall be named as additional insured. This insurance shall be considered to be primary and non-contributory to any other insurance carried by the State through self insurance or otherwise.

In addition to providing the above coverages the Contractor shall, in any contract or agreement with subcontractors performing work, require that all indemnities and waivers of subrogation it obtains, and that any stipulation to be named as an additional insured it obtains, also be extended to waive rights of subrogation against the State of Alaska and to add the State of Alaska as additional named indemnitee and as additional insured.

Evidence of insurance shall be furnished to the Department prior to the award of the contract. Such evidence, executed by the carrier's representative and issued to the Department, shall consist of a certificate of insurance or the policy declaration page with required endorsements attached thereto which denote the type, amount, class of operations covered, effective (and retroactive) dates, and dates of expiration. Acceptance by the Department of deficient evidence does not constitute a waiver of contract requirements.

When a certificate of insurance is furnished, it shall contain the following statement:

“This is to certify that the policies described herein comply with all aspects of the insurance requirements of (Project Name and Number). The insurance carrier agrees to notify the Engineer, in writing, at least 30 days before cancellation of any coverage or reduction in any limits of liability. "

30-06 EXECUTION AND APPROVAL OF CONTRACT. The Contract Form and all other required documents shall be executed by the successful bidder and returned to the Department within 15 days after receipt by the bidder. No contract shall be considered as effective until it has been fully executed by all of the parties thereto.

30-07 FAILURE TO EXECUTE CONTRACT. Failure of the successful bidder to appropriately execute and return the Contract Form and other documents within 15 days, as required above, will be just cause for the cancellation of the notice of intent to award and the forfeiture of the bid guaranty to the Department, for damages sustained. Award may then be made to the next lowest responsive and qualified bidder, or the work may be readvertised.

30-08 ORAL STATEMENTS. No oral statement of any person whomsoever shall in any manner or degree modify or otherwise affect the terms of this Contract.

SECTION 40

SCOPE OF WORK

40-01 INTENT OF CONTRACT. The intent of the contract is to provide for the construction and completion in every detail of the work described. The Contractor shall furnish all labor, materials, supervision, equipment, tools, transportation and supplies required to complete the work in accordance with the Plans, Specifications and terms of the contract.

40-02 CHANGES. The Department reserves the right to make, at any time during the progress of the work, without notice to the sureties and within the general scope of the contract, such changes, deviations, additions to or deletions from the Plans or Specifications, including the right to alter the quantity of any item or portion of the work, as may be deemed by the Engineer to be necessary or desirable and to require such extra work as may be determined by the Engineer to be required for the proper completion or construction of the whole work contemplated. Such changes will be set forth in writing as a Change Order and shall neither invalidate the Contract nor release the surety. The Contractor agrees to perform the work, as changed, the same as if it had been a part of the original Contract.

Where such work does not materially differ in character or unit cost from specified Contract work, the Engineer may order the work done and it shall be measured and paid for at contract unit prices, except that an increase or decrease of more than 25% in the quantity of a major contract item shall be subject to the provisions of Subsection 90-04.

If, however, an ordered change requires work which is materially different in character or unit cost from that specified in the Contract, a new contract item (or items) shall be established at agreed prices. If prices cannot be agreed upon, the Engineer may (1) issue a unilateral change order requiring the Contractor to proceed with the work, either with payment and/or contract time allowance provided on the basis of the Engineer's estimate of reasonable value, or with equitable adjustment to be determined later, or (2) order the work to be done on a time and materials basis in accordance with the provisions of Subsection 90-05. When required, the Contractor shall cooperate with the Engineer in keeping complete daily records of the cost of such work.

Before a Change Order or Supplemental Agreement covering work for which there is no established price is approved, the Contractor shall submit detailed cost or pricing data regarding the changed or extra work. The cost of pricing data shall include an itemization of all costs including labor, materials, and equipment required for the work. The Contractor shall certify that the data submitted is, to his best knowledge and belief, accurate, complete and current as of a mutually determined specified date and that such data will continue to be accurate and complete during the performance of the changed or extra work.

Should any contract item be found unnecessary, the Engineer may, by written order, eliminate such item from the Contract. Compensation for eliminated items will be made as provided for in Subsection 90-09.

40-03 DIFFERING SITE CONDITIONS. The Contractor shall promptly, and before such conditions are disturbed, notify the Engineer in writing of: (1) subsurface or latent physical conditions at the site, differing materially from those indicated in this contract, and which could not have been discovered by a careful examination of the site, or (2) unknown physical conditions at the site, of an unusual nature, differing materially from those ordinarily encountered and generally recognized as inherent in work of the character provided for in this contract.

The Engineer shall promptly investigate the conditions and, if he finds that such conditions do materially so differ and cause an increase or decrease in the Contractor's cost of, or the time required for, performance of this contract, an equitable adjustment shall be made and the Contract modified in writing accordingly.

Any claim for additional compensation by the Contractor under this clause shall be made in accordance with Subsection 50-18 and shall not be allowed unless the Contractor has first given the notice required above.

In the event that the Engineer and the Contractor are unable to reach an agreement concerning an alleged differing site condition, the Contractor will be required to keep an accurate and detailed record which will indicate the actual cost of the work done under the alleged differing site condition. Failure to keep such a record shall be a bar to any recovery by reason of such alleged differing site conditions. The Engineer shall be given the opportunity to supervise and check the keeping of such records.

40-04 MAINTENANCE OF TRAFFIC. It is the explicit intention of the contract that the safety of aircraft, as well as the Contractor's equipment and personnel, is the most important consideration. It is understood and agreed that the Contractor shall provide for the free and unobstructed movement of aircraft in the air operations areas of the airport with respect to his/her own operations and the operations of all his/her subcontractors as specified in Subsection 80-04. It is further understood and agreed that the Contractor shall provide for the uninterrupted operation of visual and electronic signals (including power supplies thereto) used in the guidance of aircraft while operating to, from, and upon the airport as specified in Subsection 70-16.

With respect to his/her own operations and the operations of all his/her subcontractors, the Contractor shall provide marking, lighting, and other acceptable means of identifying: personnel; equipment; vehicles; storage areas; and any work area or condition that may be hazardous to the operation of aircraft, fire-rescue equipment, or maintenance vehicles at the airport.

When the contract requires the maintenance of vehicular traffic on an existing road, street, or highway during the Contractor's performance of work that is otherwise provided for in the contract, Plans, and Specifications, the Contractor shall keep such road, street, or highway open to all traffic and shall provide such maintenance as may be required to accommodate traffic. The Contractor shall furnish erect, and maintain barricades, warning signs, flagmen, and other traffic control devices in reasonable conformity with the Manual on Uniform Traffic Control Devices for Streets and Highways (published by the United States Government Printing Office) and the Alaska Supplement (published by the Department), unless otherwise specified. The Contractor shall also construct and maintain in a safe condition any temporary connections necessary for ingress to and egress from abutting property or intersecting roads, streets or highways. Unless otherwise specified, the Contractor will not be required to furnish snow removal for such existing road, street, or highway.

The Contractor shall make his/her own estimate of all labor, materials, equipment, and incidentals necessary for providing the maintenance of aircraft and vehicular traffic as specified in this subsection.

The cost of maintaining the aircraft and vehicular traffic specified in this subsection shall not be measured or paid for directly, but shall be included in the various contract items.

40-05 REMOVAL OF EXISTING STRUCTURES. All existing structures encountered within the established lines, grades, or grading sections shall be removed by the Contractor, unless such existing structures are otherwise specified to be relocated, adjusted up or down, salvaged, abandoned in place, reused in the work or to remain in place. Unless otherwise specified, the cost of removing such existing structures shall not be measured or paid for directly, but shall be included in the various contract items.

Should the Contractor encounter an existing structure (above or below ground) in the work for which the disposition is not indicated on the Plans, the Engineer shall be notified prior to disturbing such structure. The disposition of existing structures so encountered shall be immediately determined by the Engineer in accordance with the provisions of the contract.

Except as provided in Subsection 40-06, it is intended that all existing materials or structures that may be encountered (within the lines, grades, or grading sections established for completion of the work) shall be utilized in the work as otherwise provided for in the contract and shall remain the property of the owner when so utilized in the work.

40-06 RIGHTS IN AND USE OF MATERIALS FOUND ON THE WORK. The Contractor may use on the project, with the Engineer's approval, such stone, gravel, sand, or other material determined suitable by the Engineer, as may be found in the excavation. The Contractor will be paid both for the excavation of such material at the corresponding contract unit price and for any contract item for which the excavated material is used.

The Contractor shall replace, at his own expense with other acceptable material, all of that portion of the excavated material so removed and used which was needed for embankment or backfill. No charge for the materials so used will be made against the Contractor except that he shall be responsible for payment of any royalties required.

The Contractor shall not excavate or remove any material from within the project which is not within the grading limits, as indicated by the slope and grade lines, without written authorization from the Engineer.

In the event the Contractor has processed materials from State-furnished sources in excess of the quantities required for performance of this contract, including any waste material produced as a by-product, the State may retain possession of such materials without obligation to reimburse the Contractor for the cost of their production. When such materials are in a stockpile, the Engineer may require: that it remain in stockpile; that the Contractor level such stockpile(s); or that the Contractor remove such materials and restore the premises to a satisfactory condition at no additional cost to the Department. This provision shall not preclude the State from arranging with the Contractor to produce material over and above the contract needs, payment for which shall be by written agreement between the State and the Contractor.

The material from any existing old structure may be used temporarily by the Contractor in the erection of the new structure. Such material shall not be cut or otherwise damaged except with the approval of the Engineer.

40-07 CLEANUP. Upon completion of the work and before final payment will be made, the project site, materials sources, and all ground occupied by the Contractor in connection with the work, shall be cleared of all rubbish, solid waste, excess materials, temporary structures and equipment, and all parts of the work shall be left in an acceptable condition.

40-08 Value Engineering Proposals by Contractor.

a.	Purpose and Scope. The purpose of this provision is to share with the Contractor any cost savings generated on this contract as a result of Value Engineering Proposals (VEPs) offered by the Contractor and approved by the Department. The purpose is to encourage the use of Contractor's ingenuity and experience in arriving at alternative designs or construction methods than those reflected in the contract.

The VEPs contemplated are those that could produce an immediate (under this contract) savings to the Department without impairing essential functions and characteristics of the facility including but not limited to, service life, economy of operation, ease of maintenance, desired appearance, and safety.

Not eligible for value engineering proposals are changes in the basic design of a pavement type, runway and taxiway lighting, visual aids, hydraulic capacity of drainage facilities, or changes in grade or alignment that reduce the geometric standards of the project.

b.	Submittal of Proposal. Submit the following materials and information with each VEP.

- A statement that the proposal is submitted as a Value Engineering Proposal under subsection 40-08.

- A description of the difference between the existing contract requirements and the proposed change. State the comparative advantages and disadvantages of each, including effects on service life, economy of operations, ease of maintenance, desired appearance, and safety.

- Drawings and/or specifications showing the proposed revisions relative to the original contract requirements. Schematics may be submitted for conceptual approval of the proposal.

- A complete analysis comparing the original estimated costs and quantities to be replaced by the VEP compared to the new costs and quantities generated by the proposal.

- A summary of the Contractor's development costs for the VEP. This shall include costs for designing, testing, preparing, and submitting the proposal.

- A description and estimate of costs the Department may incur in implementing the VEP, such as review of the proposal, testing and evaluation, and contract administration costs.

- A statement specifying the date by which a Change Order adopting the VEP must be executed so as to obtain the maximum cost reduction during the remainder of the contract. This date must be selected to allow the Department time for review and processing a Change Order without affecting the Contractor's schedule.

- A statement on the effect the VEP will have on the time for completing the contract. The VEP will not change the contract completion date unless specifically provided for in the Change Order authorizing the VEP.

- A description of any previous use or testing of the VEP and the conditions and results. If the proposal was previously submitted on another Department project, indicate the date, project name and number, and the action taken by the Department.

c.	Conditions. VEPs will be considered only when all of the following conditions are met:

- The Contractor is not to base any bid prices on the anticipated approval of a VEP. In the event of rejection, the Contractor shall complete the contract at the contract bid prices.

- VEPs submitted by the Contractor, apply only to the ongoing contract or contracts referenced in the proposal and become the property of the Department. The Department will have the right to use, duplicate and disclose any data necessary for the utilization of the proposal on this or other projects without obligation to the Contractor unless the Contractor identifies certain parts of the proposal as Restricted Use. This provision is intended to protect trade secrets, bidding and pricing methods, and rights provided by law with respect to patented designs, materials, or processes.

- The Department will not be liable for costs or delays due to the rejection of a VEP, including but not limited to, development costs, loss of anticipated profits, and increased material or labor costs.

- The Department will be the sole judge as to whether a VEP qualifies for consideration and evaluation. It may reject any proposal that requires excessive time or costs for review, evaluations and/or investigations, or which is not consistent with the Department's design standards and policies, safety considerations, land use restrictions, permit stipulations, right-of way limitations, or other essential criteria for the project.

- If additional information is needed to evaluate VEPs, this information will be provided in a timely manner. Failure to do so will result in rejection of the proposal.

- The Contractor may submit VEPs for an approved subcontractor, provided that reimbursement is made by the Department to the Contractor.

- When the Contractor utilizes the services of a design professional to prepare the proposal, the Contractor will require the design professional to seal the drawings and provide evidence of Professional Liability Insurance coverage. The minimum limits of the insurance shall be in an amount agreed to by the Department, prior to rendering services.

- The Contractor shall not begin proposed changes prior to Department approval.

- The Department will not consider proposals to share in cost savings due to changes previously approved or for work already done.

d.	Departmental Action.

- The Engineer will notify the Contractor of the status of the VEP as soon as practicable but no later than 3 weeks after its receipt. If additional time is required, the Engineer will notify the Contractor, providing the reason for the delay and the expected date of the decision.

- If the VEP is not accepted, the Engineer will notify the Contractor in writing, explaining the reasons for rejection. The Contractor may withdraw any VEP, in whole or in part, at any time before it is accepted.

- If the VEP is approved in concept (without final drawings and specifications), the Department may either undertake the re-design itself or issue the Contractor a limited notice to proceed, subject to mutual agreement, authorizing the final design. The notice to proceed will include reference to any pertinent design criteria, Department policies, and other limitations on the design or construction methods. When the VEP is approved in concept, the Department is under no obligation to accept, or to compensate the Contractor for, the final design.

- If the final VEP is accepted, the Engineer will issue a Change Order incorporating the VEP into the contract.

e.	Contract Modification and Payment. If the VEP is accepted by the Department, the changes and payment will be authorized in a Change Order. Reimbursement to the Contractor will be made as follows:

- The changes will be incorporated into the Contract by changes in the quantities of unit bid items or new agreed price items, as appropriate, in accordance with Subsection 40-02. The revised work will then be paid for at the agreed contract price or prices. Such price will include the Contractor's costs of developing and submitting the VEP.

- In addition to the above, the Department will share the savings with the Contractor, in a separate lump sum contract item, GCP-40a, VEP Incentive. The amount of the incentive will be 50% of the savings to the Department as reflected by the difference between the cost of the revised work and the cost of the related work required by the original contract Plans and Specifications computed at contract bid prices. For the purpose of this calculation, the cost of the revised work will include costs the Department may incur as a result of the VEP, such as review of the proposal, testing and evaluation, and added contract administration costs. These costs will be estimated and agreed to in the Change Order.

- The VEP Incentive, Item GCP-40a, will be paid on a prorated basis as the revised work is performed.

SECTION 50

CONTROL OF WORK

50-01 AUTHORITY OF THE ENGINEER. The Engineer will decide all questions which may arise as to the quality and acceptability of materials furnished, work performed and as to the rate of progress of the work; all questions which may arise as to the interpretation of the Plans and Specifications; all questions as to the acceptable fulfillment of the Contract on the part of the Contractor.

The Engineer will have the authority to suspend the work wholly or in part due to the failure of the Contractor to correct conditions unsafe for the workmen or the general public; for failure to carry out provisions of the Contract; for failure to carry out orders; for such periods as he may deem necessary due to unsuitable weather; for conditions considered unsuitable for the prosecution of the work; or for any other condition or reason deemed to be in the public interest.

The Engineer may, at reasonable times, inspect that part of the plant or place of business of the Contractor or subcontractor that is related to the performance of the Contract.

The Engineer may audit the books and records of the Contractor or a subcontractor to the extent that the books and records relate to the performance of the Contract or subcontract, including cost or pricing data submitted under subsection 40-02. Books and records that relate to the performance of the Contract shall be maintained by the Contractor for a period of 3 years after the date of final payment under the prime contract and by the subcontractor for a period of 3 years after date of final payment under the subcontract, unless a shorter period is authorized in writing by the Contracting Officer.

50-02 PLANS AND WORKING DRAWINGS. Plans will show lines, grades, typical cross sections, location and design of all structures and a summary of items.

Working drawings shall be furnished by the Contractor and consist of such details as may be required to adequately control the work and which are not included in the Plans furnished by the Department. Work shall not be performed or materials ordered until working drawings for such work, or changes thereto, are approved. Such approval shall not relieve the Contractor of responsibility for the successful completion of the work. The title block for all drawings shall include the project name and number. All working and detail drawings shall be full size, on white paper, and have dark blue or black lines.

The Contractor shall submit to the Engineer for approval not less than five sets of any required preliminary detail or shop working drawings. They shall be submitted in sufficient time to allow review and correction prior to beginning the work they cover. One set of these drawings will be returned to the Contractor approved or marked with corrections to be made. The other sets shall be retained by the Engineer.

The Contractor shall be responsible for agreement of dimensions and details as well as for conformity of his working drawings with the Plans and Specifications. The Contractor shall indicate on the working drawings all deviations from the Plans and Specifications and shall also itemize and explain all deviations in the letter of transmittal.

Upon receipt of an approved copy of the shop working drawings, the Contractor shall furnish to the Engineer:

- Enough additional copies to provide 8 approved sets of prints.

- One set of reproducible transparencies (polyester film).

- If requested, an electronic file in AutoCAD drawing interchange format (.DXF).

Fabricated materials or equipment to be incorporated into the work shall be approved by the Engineer prior to shipment to the project site. The Contractor shall, in ample time to permit compliance with the construction schedule, obtain and check manufacturer's shop drawings and other pertinent data for conformance with contract requirements. After completion of such checking, the Contractor shall submit for the Engineer's approval five copies of all shop drawings, materials and equipment listings, and other pertinent data. They shall be in such detail as the Engineer may require for information as to the design, installation, and operation of such items, and their compliance with the Plans and Specifications.

A copy of the approved drawings, lists, prints, specifications, samples, or other data, above, shall be kept with the jobsite plans, and the fabrications furnished shall conform to same. Approval of the above submittals shall not release the Contractor from his responsibility for the fulfillment of contract requirements or the purpose of the installation, or from his liability to replace materials or equipment that prove defective or fail to meet the specified requirements.

The contract price will include the cost of furnishing all working and as-built drawings.

50-03 CONFORMITY WITH PLANS AND SPECIFICATIONS. Work performed and materials furnished shall conform to the lines, grades, cross sections, dimensions and material requirements, including tolerances, shown on the Plans or indicated in the Specifications.

In the event the Engineer finds the materials or the finished product in which the materials are used or the work performed are not in conformity with the Plans and Specifications and have resulted in an unacceptable or unsatisfactory product, the work or materials shall be removed and replaced or otherwise corrected by the Contractor at no additional cost to the Department.

In the event the Engineer finds the materials furnished, work performed, or the finished product not in conformity with the Plans and Specifications but that reasonably acceptable work has been produced, he shall then make a determination if the work shall be accepted and remain in place. In this event, the Engineer will document the basis of acceptance by contract modification which will provide for an appropriate adjustment in the contract price for such work or materials as he deems necessary to conform to his determination based on engineering judgement.

The failure of the Department in any one or more instances to insist upon strict performance of any of the terms of this contract or to exercise any option herein conferred shall not be construed as a waiver or relinquishment to any extent of the right to assert or rely upon any terms or option on any future occasion.

50-04 COORDINATION OF PLANS, SPECIFICATIONS AND SPECIAL PROVISIONS. These Specifications, the Plans, Special Provisions, and all supplementary documents are essential parts of the contract, and a requirement occurring in one is as binding as though occurring in all. They are intended to be complementary and to describe and provide for a complete work. In case of discrepancy, calculated dimensions will govern over scaled dimensions.

Should other discrepancies appear between any of the following parts of the contract, a listed part shall take precedence over all those listed below it:

- Special Provisions

- Plans

- Standard Specifications

- Cited standards for materials testing and cited FAA Advisory Circulars

The Contractor shall take no advantage of any apparent error or omission in the Plans or Specifications. In the event the Contractor discovers such an error or omission, he shall immediately notify the Engineer. The Engineer will then make such corrections and interpretations as may be deemed necessary for fulfilling the intent of the contract.

50-05 COOPERATION BY CONTRACTOR. The Contractor will be supplied with a minimum of two full size sets of conformed Plans and contract assemblies including Special Provisions, one set of which the Contractor shall keep available on the work at all times. If cross-sections are available, one set will be supplied to the Contractor upon request.

The Contractor shall give the work the constant attention necessary to facilitate the progress thereof, and shall cooperate with the Engineer, his inspectors, and other contractors in every way possible.

The Contractor shall have on the work at all times, as his agent, a competent superintendent capable of reading and thoroughly understanding the Plans and Specifications and thoroughly experienced in the type of work being performed, who shall receive instructions from the Engineer or his authorized representatives. The superintendent shall have full authority to supply such materials, equipment, tools, labor and incidentals as may be required. The superintendent shall have the authority to sign Directives for the Contractor. Such superintendence shall be furnished irrespective of the amount of work sublet.

50-06 COOPERATION WITH UTILITIES. The contract will indicate the various utilities known to be within the work zone and indicate whether they are to remain in service, be abandoned in place, be adjusted by others, or be adjusted by the Contractor. The Department will notify all utility companies and endeavor to have all necessary adjustments to be made by others completed as soon as practicable.

The location and elevation of existing utilities shown on the Plans are approximate only. Additional utilities may exist that are not shown on the Plans. Before starting construction, the Contractor shall request all utility owners to locate their utilities and, at points of possible conflict, the Contractor shall uncover the located utilities. Should conflicts occur or utilities be discovered that are not shown on the Plans that require adjusting, the Engineer shall make contract adjustments in accordance with Subsection 40-02.

It is understood and agreed that the Contractor has considered in his bid all of the permanent and temporary utility appurtenances in their present or relocated positions as shown on the Plans, and the completion dates for various utility adjustments as may be stated in the Special Provisions, and that no additional compensation will be allowed for any delays, inconvenience or damage sustained by the Contractor due to any interference from the said utility appurtenances or the operation of moving them. If the completion of the various utility adjustments is delayed beyond the completion dates specified in the Special Provisions, and the delay is not a consequence of any action on the part of the Contractor, then contract time may be extended in accordance with Subsection 80-06.

50-07 COOPERATION BETWEEN CONTRACTORS. The Department may, at any time, contract for and perform other or additional work on or near the project.

When separate contracts are let within the limits of any one project, each contractor shall conduct his work so as not to interfere with or hinder the work being performed by other contractors. Contractors working on the same project shall cooperate with each other. The Contractor shall join his work with that of the others in an acceptable manner and shall perform it in proper sequence to that of the others.

Each contractor involved shall assume all liability, financial or otherwise, in connection with his contract and shall protect and save harmless the Department from any and all damages or claims that may arise because of inconvenience, delay, or loss experienced by him because of the presence and operations of other contractors.

50-08 SURVEY CONTROL. All surveying including, but not limited to, project layout, cross sections, slope stakes, grade stakes, as-built measurements, and quantity measurements shall be accomplished by the Contractor. The cost of surveying is to be subsidiary to the items of work for which surveying is required, unless a pay item for surveying is included in the bid schedule. The Contractor will be provided, on the Plans and readily apparent on the ground and on airport property, adequate horizontal and vertical control from which project layout can be accomplished. Immediately upon completion of initial cross sections, the Contractor shall furnish reduced and checked survey notes to the Engineer for plotting. From time to time throughout the work, as requested by the Engineer, the Contractor shall take appropriate sections and shall provide the Engineer with reduced and checked notes from which quantity calculations for progress payment purposes can be accomplished. Notes shall be kept in a neat, orderly, and legible form in accordance with professional surveying practices.

Upon completion of each phase of the work, the Contractor shall furnish the Engineer with all necessary measurements for completion of the as-built drawings. All original survey notes and field books shall become the property of the Department and shall be delivered to the Engineer as a condition to final payment on this contract.

50-09 DUTIES OF THE INSPECTOR. Inspectors employed by the Department are authorized to inspect all work done and materials furnished. The inspector is not authorized to issue instructions contrary to the Plans and Specifications, or to act as foreman for the Contractor; however, the inspector shall have the authority to reject work or materials until any questions at issue can be referred to and decided by the Engineer.

50-10 INSPECTION OF WORK. All materials and each part or detail of the work shall be subject to inspection. The Engineer shall be allowed access to all parts of the work and shall be furnished with such information and assistance by the Contractor as is required to make a complete and detailed inspection.

Neither observations or inspections by the Department nor tests or approvals by others shall relieve the Contractor from his obligation to perform the work in accordance with the contract.

The Contractor, at any time before acceptance of the work, shall remove or uncover such portions of the finished work as may be directed. After examination, the Contractor shall restore said portions of the work to the standard required by the Specifications. Should the work thus exposed or examined prove acceptable, the uncovering, or removing, and the replacing of the covering or making good of the parts removed will be paid for as extra work; but should the work so exposed or examined prove unacceptable, the uncovering, or removing, and the replacing of the covering or making good of the parts removed, will be at the Contractor's expense.

Any work done or materials used without inspection by an authorized Department representative may be ordered removed and replaced at the Contractor's expense unless the Department representative failed to inspect after having been given reasonable notice in writing that the work was to be performed.

When any unit of government, political subdivision, or any public or private utility is to pay a portion of the cost of the work covered by this contract, its respective representatives will have the right to inspect the work. Such inspection will not make any unit of government or political subdivision or any public or private utility a party to this contract, and will not interfere with the rights of either party hereunder.

The State of Alaska Department of Labor (DOL) may require electrical inspection of Public Structures. Requests for inspection by the DOL are mandatory. Inspection arrangements should be made by contacting the DOL Electrical Inspector, Anchorage, Alaska. Phone (907) 269-4925.

The Contractor shall request inspections a minimum of two weeks prior to the expected date of inspection being needed and if more than one item requires inspection a list of all dates of each stage of the inspections shall be submitted.

50-11 REMOVAL OF UNACCEPTABLE AND UNAUTHORIZED WORK. All work which does not conform to the requirements of the Contract will be considered unacceptable, unless otherwise determined acceptable under the provisions of Subsection 50-03.

Unacceptable work, whether the result of poor workmanship, use of defective materials, damage through carelessness or any other cause, found to exist prior to the final acceptance of the work, shall be remedied or removed immediately and replaced in an acceptable manner.

No work shall be done without lines and grades having been established. Work done contrary to instructions, work done beyond the lines shown on the Plans, or as given, except as herein specified, or any extra work done without authority, will be considered as unauthorized and will not be paid for under the provisions of the contract. Work so done may be ordered removed or replaced at the Contractor's expense.

Upon failure on the part of the Contractor to comply forthwith with any order of the Engineer made under the provisions of this section, the Engineer will have authority to cause unacceptable work to be remedied, or removed and replaced, unless determined acceptable under Subsection 50-03, and to deduct the costs from any monies due or to become due the Contractor.

50-12 LOAD RESTRICTIONS.

The Contractor shall comply with all legal size and weight regulations of 17 AAC 25 and all restrictions in the Administrative Permit Manual.

The Engineer may waive the permit requirements of regulation 17 AAC 25 regarding oversize and overweight vehicle movements within the project limits when the Contractor submits an acceptable Traffic Control Plan.

Permits may be obtained from the Department’s Division of Measurement Standards & Commercial Vehicle Enforcement for movements of oversize and overweight equipment outside of the project limits.

50-13 MAINTENANCE DURING CONSTRUCTION. The Contractor shall maintain the work, and those portions of the project affected by the work, from the date physical construction begins until project completion. This maintenance shall be a continual and effective effort prosecuted day by day, with adequate equipment and forces to the end that the work, and those portions of the project affected by the work, are kept in satisfactory condition at all times.

The Contractor may be relieved of specified portions of this maintenance responsibility during a seasonal suspension of work. Approximately one month prior to seasonal suspension of work, the Contractor shall schedule a preliminary meeting with the Engineer and Maintenance and Operations to outline the work he expects to complete before shut down and the condition the project is to be left in. The Contractor shall then schedule a field review for acceptance by the Department for winter maintenance. At the field review a punch list shall be prepared for implementation prior to acceptance. In order for the Contractor to be relieved of winter maintenance responsibility, the surface of all embankments shall be properly crowned for drainage and all edge lighting shall be in good working order. After acceptance for winter maintenance and until the Contractor resumes construction operations, maintenance of the facility agreed upon will be the responsibility of the Department.

In the case of a contract for the placing of a course upon a course or subgrade previously constructed, the Contractor shall maintain the previous course or subgrade during all construction operations.

All costs of maintenance work during construction and before the project is accepted shall be included in the unit prices bid on the various contract items, and the Contractor will not be paid an additional amount for such work.

50-14 FAILURE TO MAINTAIN THE WORK. Should the Contractor at any time fail to maintain the work as provided in Subsection 50-13, the Engineer shall immediately notify the Contractor of such noncompliance. Such notification shall specify a reasonable time within which the Contractor shall be required to remedy such unsatisfactory maintenance condition. The time specified will give due consideration to the exigency that exists.

Should the Contractor fail to respond to the Engineer's notification, the Engineer may suspend any work necessary for the Department to correct such unsatisfactory maintenance condition, depending on the exigency that exists. Any maintenance cost incurred by the Department, shall be deducted from monies due or to become due the Contractor.

50-15 PARTIAL ACCEPTANCE. If at any time during the prosecution of the work the Contractor completes a usable unit or portion of the project, the occupancy of which will benefit the Department, he may request the Engineer to make final inspection of that unit. If the Engineer finds upon inspection that the unit has been satisfactorily completed in compliance with the Contract, he may accept it as being completed, and the Contractor shall be relieved of further responsibility for that unit. Such partial acceptance and beneficial occupancy by the Department shall not void or alter any provision of the Contract, and shall only be made at the discretion of the Department.

50-16 PROJECT COMPLETION. Upon written notice from the Contractor of presumptive completion of all construction provided for under the Contract, the Engineer will conduct the final inspection.

If the inspection discloses any work as being unsatisfactory, the Engineer will so advise the Contractor, in writing. The Contractor shall immediately take appropriate action to complete such work in accordance with the Contract.

When all physical work and cleanup provided for under the Contract is found to be complete, a letter of project completion will be issued by the Engineer. Project completion will relieve the Contractor from further maintenance responsibilities and shall stop the count of contract time but will not relieve him of any other obligations under the Contract.

50-17 FINAL ACCEPTANCE. Following project completion, receipt of the Contractor's Release with no exceptions, certification of payment of payroll and revenue taxes, and final payment to the Contractor, the Department will issue the letter of Final Acceptance, releasing the Contractor from further obligations under the contract, except as specified under Subsections 30-04 and 70-19.

50-18 CLAIMS FOR ADJUSTMENT AND DISPUTES. If the Contractor becomes aware of any act or occurrence which may form the basis of a claim by the Contractor for additional compensation or an extension of time for performance, or if any dispute arises regarding a question of fact or interpretation of the Contract, the Contractor shall immediately inform the Engineer. If the matter cannot be resolved by agreement within 7 days, the Contractor shall, within the next 14 days, submit an Intent to Claim in writing to the Engineer.

If the Contractor believes additional compensation is warranted, the Contractor shall immediately begin to keep and maintain complete, accurate, and specific daily records concerning every detail of the potential claim including actual costs incurred. The Contractor shall give the Engineer access to any such record and, when so requested, shall forthwith furnish the Engineer copies thereof. Equipment costs shall be based on the Contractor's internal rates for ownership, depreciation, and operating expense and not on published rental rates.

Submit any Claim to the Contracting Officer, in writing, within 90 days of the act or occurrence forming the basis of the claim. The Contracting Officer will acknowledge receipt of the Claim in writing.

The Contractor agrees that unless these written notices are provided, the Contractor will have no entitlement to additional time or compensation for such act, event or condition. The Contractor shall in any case continue diligent performance of the contract.

The Claim shall specifically include the following:

- The act, event or condition giving rise to the claim.

- The contract provisions which apply to the claim and under which relief is provided.

- The item or items of contract work affected and how they are affected.

- The specific relief requested, including contract time if applicable, and the basis upon which it was calculated.

- A statement certifying that the claim is made in good faith, that the supporting cost and pricing data are accurate and complete to the best of the Contractor's knowledge and belief, and that the amount requested accurately reflects the contract adjustment for which the Contractor believes the Department is liable.

The Claim, in order to be valid, must not only show that the Contractor suffered damages or delay but that those conditions were actually a result of the act, event or condition complained of and that the Contract provides entitlement to relief to the Contractor for such act, event or condition.

The Department reserves the right to make written request to the Contractor at any time for additional information which the Contractor may possess relative to the Claim. The Contractor agrees to provide the Department such additional information within 30 days of receipt of such a request. Failure to furnish such additional information may be regarded as a waiver of the Claim.

The Contractor will be furnished the Contracting Officer's Decision within the next 90 days, unless additional information is requested by the Contracting Officer. The Contracting Officer's Decision is final and conclusive unless, within 14 days of receipt of the decision, the Contractor delivers a Notice of Appeal to the Appeals Officer. Procedures for appeals are covered under AS 36.30.625 and AS 36.30.630.

SECTION 60

CONTROL OF MATERIALS

60-01 SOURCE OF SUPPLY AND QUALITY REQUIREMENTS. Materials used shall meet all requirements of the Contract. Notify the Engineer of proposed sources of materials at least 30 days prior to shipment. Materials originating outside Alaska may be inspected by an agency designated by the Department. Inspectors are not authorized to approve materials. However, approval subject to field inspection may be given on the basis of inspection reports indicating full compliance with the Specifications. Submit to the Engineer and to the State Materials Engineer a complete listing of all materials to be purchased from outside suppliers sufficiently in advance of fabrication and/or shipment to permit inspection of such materials.

Unless otherwise specifically provided for, all equipment, materials and articles incorporated in the work covered by this Contract shall be new and of the specified grade. All manufactured materials shall be delivered and stored in their original containers and show the manufacturer's name, brand, and identifying number.

The Contractor shall furnish airport lighting equipment that conforms to the requirements of cited materials specifications. In addition, where an FAA specification for airport lighting equipment is cited in the Plans or Specifications, the Contractor shall furnish such equipment that is certified and listed under AC 150/5345-53, Airport Lighting Equipment Certification Program.

60-02 LOCAL MATERIAL SOURCES.

- General. Furnish all required materials from sources of the Contractor’s choice. Produce a sufficient quantity of materials meeting the specification requirements from the sources selected. If blend material is required to produce the specified product, it is subsidiary. Determine the type of equipment and methods to be used. Unless otherwise specified herein, all costs of exploring and developing material sources are subsidiary. Perform quality control during the processing of materials. Unless exempted under AS 27.19.050, the Contractor shall acquire from the Alaska Department of Natural Resources, or from an Agency having a Cooperative Management Agreement with the Department of Natural Resources, an approved Reclamation Plan and shall meet bonding requirements, in accordance with AS 27.19 and 11 AAC 97 for each Material Source prior to engaging in a mining operation in that source.

- Inspection and Acceptance. The Department will, at no cost to the Contractor, test samples to determine the acceptability of material to be incorporated into the work from the source. The Department reserves the right to reject materials at any time that the grading and other qualities of the product do not conform to the Specifications.

- State Furnished Sources. Existing drill logs, test results, and other data will be made available to bidders. Bidders have the right to further explore, at no cost to the State.

For sources under State control, submit a detailed mining plan to the Engineer for approval prior to any excavation. Include a plan view and cross-sectional view of the site, applicable boundaries or property lines, the areas and depths to be developed, access roads, locations of stripping, sorting, and waste piles, crushing and plant sites, stockpile sites, drainage features, and erosion and pollution control features.

Do not remove any material of any kind or quality other than that required for use on the project, from any material source under State control.

Sources under State control from which materials have been removed shall, upon completion of the work, be finished and graded to a neat, acceptable condition. Grade so that water will not collect or stand therein, and water pollution will not result in the event of possible erosive action within the pit. Draining of material sources dewatered by pumping or used as bail sites will not be required.

(1)	Designated Sources. The Department has acquired and made available to the Contractor the right to take materials from sources designated in the Contract together with the right to use designated sources for plant sites, stockpiles, and haul roads.

It is understood that it is not feasible to ascertain from samples the limits for an entire deposit, and that variations shall be considered normal and are to be expected.

If the Contractor chooses to furnish material from a designated source, the Engineer may order procurement of material from any portion of the deposit and may reject portions of the deposit as unacceptable. All material required may not be procurable from any one designated source.

If the Contractor chooses to furnish material from designated sources, and it is subsequently found that the quality and quantity of material producible from these sources is not as represented by the materials report and a change of sources is necessary for that reason, an equitable adjustment will be made.

If the Contractor chooses for some other reason to change between or among designated sources, the change in these sources shall not be considered to involve or constitute reason for an increase or decrease in the amount due the Contractor or any adjustment thereof, save the payment for actual quantities produced and accepted from one or several designated sources at the original contract prices for the pay items involved.

(2)	Available Sources. The Department may list other material sources that are available for use for the project by the Contractor. The Department makes no representation as to the quality or quantity of material from these sources.

(3)	Other Sources Under State Control. There may be other material sources under State control in the vicinity of the project that are not listed in the contract documents. If the Contractor desires to use material from these sources, the Department may, at its option, acquire or make available to the Contractor the right to take material from them. These sources will be added to the Contract by Change Order, but only when there is a demonstrated benefit to the State. The Department makes no representation as to the quality or quantity of material from these sources. Obtain acceptable samples from locations designated within the source.

d.	Contractor Furnished Sources. Acquire the necessary rights to take materials from these sources and pay all costs related to obtaining and developing the sources including any which may result from an increase in length of haul. Obtain all necessary environmental permits and clearances relating to the use of the material source prior to any clearing or ground disturbance in the material source. Obtain and furnish to the Engineer acceptable material samples from locations designated within the source.

60-03 TESTING AND ACCEPTANCE. Materials are subject to inspection and testing prior to incorporation into the work. Work in which untested materials are used without approval shall be performed at the Contractor's risk and may be considered unacceptable in accordance with Subsection 50-11.

a.	Quality Control. The Contractor is responsible for the quality of construction and materials used in the work. Quality control is process control and includes all activities that ensure that a product meets Contract specifications. When required, the Contractor shall implement a Quality Control Program as described in Section 100, Contractor Quality Control Program.

b.	Acceptance Testing. The Department has the exclusive right and responsibility for determining the acceptability of the construction and incorporated materials.

Acceptance tests will be performed by, and at the expense of, the Department. Samples will be taken by a qualified representative of the Department. Copies of tests will be furnished to the Contractor upon request.

Acceptance testing by the Department is not considered to be a substitute for the Contractor's quality control testing. When quality control testing is not performed in accordance with the accepted quality control plan, the Engineer will refuse to retest materials which have been shown to be unacceptable by standard acceptance testing procedures.

Acceptance sampling and testing frequencies are shown in the Appendix to these Specifications.

60-04 PLANT INSPECTION. The Department may undertake the inspection of materials at the source. Manufacturing plants may be inspected periodically for compliance with specified manufacturing methods and materials samples will be obtained for laboratory testing for compliance with materials quality requirements. This may be the basis for acceptance of manufactured lots as to quality. In the event plant inspection is undertaken the following conditions shall be met:

- The Engineer shall have the cooperation and assistance of the Contractor and the producer of materials.

- The Engineer shall have full entry at all times to such parts of the plant as may concern the manufacture or production of the materials being furnished.

- The inspector or inspection agency shall be advised of the production and/or fabrication schedule a minimum of 48 hours prior to beginning work on any item requiring inspection. All materials for which the Engineer has requested plant inspection and which are fabricated without such inspection shall be considered unacceptable. Any testing required to prove acceptability of such materials is subsidiary.

The Department reserves the right to retest all materials which have been tested at the source of supply, prior to incorporation into the work, and to reject all materials which, when retested, do not meet the requirements of the Specifications.

60-05 CERTIFICATION OF COMPLIANCE. The Engineer may permit the use, prior to sampling and testing, of certain materials or assemblies when accompanied by manufacturer's certificates of compliance stating that such materials or assemblies fully comply with the requirements of the Contract. The certificate shall be signed by the manufacturer. Each lot of such materials or assemblies delivered to the work must be accompanied by a certificate of compliance in which the lot is clearly identified.

Materials or assemblies used on the basis of certificates of compliance may be sampled and tested at any time and if found not to be in conformity with contract requirements will be subject to rejection whether in place or not.

The Engineer may also permit the use of materials that have been determined by the Engineer to be listed on the Department's Approved Products List, available from the State Materials Engineer.

When a material or assembly is specified by "brand name or equal" and the Contractor elects to furnish an "or equal" material or assembly, the Contractor shall be required to furnish the manufacturer's certificate of compliance for each lot of such material or assembly delivered to the work. Such certificate of compliance shall clearly identify each lot delivered and shall certify as to:

- Conformance to the specified performance, testing, quality or dimensional requirements; and,

- Suitability of the material or assembly for the use intended in the contract work.

The Engineer shall determine the acceptability of the proposed substitute for use in the work.

The Engineer reserves the right to refuse permission for use of materials or assemblies on the basis of certificates of compliance.

60-06 STORAGE OF MATERIALS. Materials shall be stored to preserve their quality and fitness for the work. Stored materials, even though approved before storage, may again be inspected prior to their use in the work. Stored materials shall be located so as to facilitate their prompt inspection. Approved portions of the project site may be used for storage purposes and for the placing of the Contractor's plant and equipment, but any additional space required therefor must be provided by the Contractor without extra compensation.

Private property shall not be used for storage purposes without written permission of the owner or lessee. If requested, copies of such written permission shall be furnished. All storage sites shall be restored to their original conditions, unless otherwise specified in the use agreement, by the Contractor without extra compensation.

60-07 DEPARTMENT-FURNISHED MATERIAL. The Contractor shall furnish all materials required to complete the work, except those specified to be furnished by the Department.

Material furnished by the Department will be made available to the Contractor at the points specified in the Special Provisions.

The cost of handling and placing all materials after they are delivered to the Contractor shall be included in the contract price for the item in connection with which they are used.

The Contractor will be held responsible for all material delivered to him, and deductions will be made from any monies due him to make good any shortages and deficiencies, from any cause whatsoever, and for any damage which may occur after such delivery, and for any demurrage charges.

60-08 SUBMITTAL PROCEDURE. A Submittal Register shall be completed, and submitted to the Engineer on forms provided by the State. The Submittal Register shall list all shop drawings, catalog cuts, manufacturer's certifications, quality control testing plans, schedules of work and other items required to be submitted to the Department by the Contractor including but not limited to Storm Water Pollution Prevention Plan, Quality Control Program, Progress Schedule, Blasting Plan, Mining Plan, annual EEO reports, DBE payment documentation and subcontracts. The register shall be filled out sequentially by bid item and shall allow at least three spaces between bid items. The intent of the Submittal Register is to provide a blueprint for the smooth flow of specified project documents.

The number of copies required for submittals may be included in the specifications for individual bid items. If the number of copies of a submittal is not otherwise specified, three copies shall be required. On each sheet of submittal, shop drawings, catalog cuts, etc., space shall be provided for Contractor and Department review stamps.

Each copy of each submittal shall include a Submittal Summary sheet. The Contractor may use forms provided by the State or a similar form of his choice as approved by the State. The Contractor shall note on the Submittal Summary the number of days he proposes for the Department's review. Unless otherwise acceptable to the State, the minimum time allowed for review shall be 15 working days after receipt by the approving office.

If the Contract has a duration of 180 days or less, the Contractor shall, within fifteen days after the date of the Notice to Proceed, submit to the Department for review all submittals.

No payment will be made for specific items until such time that the Department has received the Submittal Register and approved all required submittals.

60-09 BUY AMERICAN STEEL AND MANUFACTURED PRODUCTS. (Federal-Aid Contracts)

a.	The Contractor agrees that only domestic steel and manufactured products will be used by the contractor, subcontractors, material, men, and suppliers in the performance of this contract, as defined below.

b.	The following terms apply to this clause:

- Steel and Manufactured Products. As used in this clause, steel and manufactured products include (1) those produced in the United States or (2) a manufactured product produced or manufactured in the United States, if the cost of its components mined, produced or manufactured in the United States exceeds 60% of the cost of all its components and final assembly has taken place in the United States. Components of foreign origin of the same class or kind, as the products referred to in subparagraphs c.(1) or c.(2) shall be treated as domestic.

- Components. As used in this clause, components means those articles, materials, and supplies incorporated directly into steel and manufactured products.

- Cost of Components. This means the costs for production of the components, exclusive of final assembly labor costs.

c.	Buy American Certificate. Execution and submission of the Buy American Certificate Form 25D-061, is required in accordance with sections 30-06 and 30-07. If there are no exceptions to be listed on the certificate, the bidder shall enter "NONE" on the first line.

If exceptions are listed on the Buy American Certificate, they shall meet at least one of the following criteria for the certificate to be considered appropriately executed:

- Those products or materials that the U.S. Department of Transportation has determined, under the Aviation Safety and Capacity Expansion Act of 1990, are not produced in the United States in sufficient and reasonably available quantities and of a satisfactory quality. (The current list is included on the back of Form 25D-061.)

- Those products or materials where the U.S. Department of Transportation has determined, under the Aviation Safety and Capacity Expansion Act of 1990, that domestic preference would be inconsistent with the public interest.

- Where inclusion of domestic material will increase the cost of the overall project contract by more than 25%.

SECTION 70

LEGAL RELATIONS AND RESPONSIBILITY TO PUBLIC

70-01 LAWS TO BE OBSERVED. The Contractor shall keep fully informed of all Federal, State, and local laws, ordinances, and regulations and all orders and decrees of bodies or tribunals having any jurisdiction or authority, which in any manner affect those engaged or employed on the work, or which in any way affect the conduct of the work. He shall at all times observe and comply with all such laws, ordinances, regulations, orders and decrees; and shall protect and indemnify the State and its representatives against any claim or liability arising from or based on the violation of any such law, ordinance, regulation, order, or decree, whether by himself or his employee.

70-02 PERMITS, LICENSES, AND TAXES. The Contractor shall pay all charges, fees and taxes, and give all notices necessary and incidental to the due and lawful prosecution of the work. As a condition of the performance of this Contract, the Contractor shall pay all Federal, State and local taxes incurred by the Contractor, in the performance of this Contract. Proof of payment of these taxes is a condition precedent to final payment by the Department under this Contract.

The Department has secured permits and licenses required for the construction of the proposed project and the use of designated material sites and disposal areas. The terms, conditions, and stipulations contained in the permits obtained by either the Department or separately by the Contractor are hereby made a part of this Contract. It is the Contractor's responsibility to abide by the conditions contained in each permit. If it is determined that an activity cannot be performed as specified in the permits, the Contractor shall immediately notify the Engineer. Work which does not conform to permits cannot be conducted until a permit modification and/or any additional permits required are obtained. The Contractor is responsible for modifying contractor-acquired permits and acquiring any additional permits necessary to perform work which does not comply with existing permits. The Department will modify Department-acquired permits, if necessary.

Prior to removing, stockpiling, storing, staging, or disposing of any material or equipment in, on, or from a location not previously permitted for such use by the Contract, the Contractor shall obtain all necessary permits and clearances. These permits and clearances may include, but are not limited to: State Historic Preservation Officer approval; Division of Governmental Coordination Coastal Consistency Determination; Department of Natural Resources Mining Reclamation and Temporary Water Use Permits; Department of Environmental Conservation Section 401 Certification, Solid Waste Disposal Site and Construction Camp Permits; Department of Fish and Game Title 16 and Special Area Permits; U.S. Fish and Wildlife Service Threatened and Endangered Species clearance; U.S. Corps of Engineers Section 404/10 Permits; city or local government development permits and flood hazard permits; and the permission of the property owner or lessee.

The Contractor is responsible for providing qualified environmental professionals to collect any data or perform studies necessary to support the acquisition of any required permits for the use of sites outside the permitted project limits. For example, the Contractor would provide a certified archeologist to perform any required cultural surveys to obtain approval from the State Historic Preservation Officer, or an individual certified by the Corps of Engineers to perform any needed wetlands delineations.

Prior to the use of any area not previously permitted by the Contract, the Contractor shall provide a copy to the Engineer of the following items:

- All permits or clearances necessary to use the site for its intended purpose(s).

- A written statement that all permits or clearances necessary have been obtained.

- Written evidence that the Contractor has contacted all of the agencies listed above and no additional permits are required on the part of the Contractor. This evidence should at a minimum include the name of the agency and staff person contacted, the date contacted, and result of coordination.

- A plan that identifies how the site will be finally stabilized and protected.

Failure to provide any of the above information and/or failure to demonstrate that a proposed site can be finally stabilized to eliminate future adverse impacts to natural resources may result in the rejection of the site by the Engineer without extra compensation.

70-03 PATENTED DEVICES, MATERIALS AND PROCESSES. If the Contractor employs any design, device, material, or process covered by letters of patent trademark or copyright, he shall provide for such use by suitable legal agreement with the patentee or owner. The Contractor and the surety shall indemnify and save harmless the State, any affected third party, or political subdivision from any and all claims for infringement by reason of the use of any such patented design, device, material or process, or any trademark or copyright, and shall indemnify the State for any costs, expenses, and damages which it may be obliged to pay by reason of any infringement, at any time during the prosecution or after the completion of the work.

70-04 RESTORATION OF SURFACE OPENED BY PERMIT. The right to construct or reconstruct any public or private utility service, FAA or National Oceanic and Atmospheric Administration (NOAA) facility, or a utility service of another government agency within the project site or to grant permits for the same, at any time, is hereby expressly reserved by the Department. The Contractor shall not be entitled to any damages either for the digging up of the project site or for any delay occasioned thereby.

Any municipality, individual, firm, or corporation wishing to make an excavation in the project must secure a permit from the Department. The Contractor shall allow parties bearing such permits, and only those parties, to make excavations in the project. When ordered by the Engineer, the Contractor shall make all necessary repairs due to such excavations and such work will be paid for as extra work, or as provided in these Specifications, and will be subject to the same conditions as original work performed.

70-05 FEDERALLY ASSISTED PROJECTS. The work in this contract may be undertaken and accomplished in accordance with the terms and conditions of a Grant Agreement between the State of Alaska and the United States, under the Federal Aviation Reauthorization Act of 1996, as amended, pursuant to which the United States may pay a certain percentage of the costs of the project that are determined to be allowable under that Act.

When the United States Government pays all or any portion of the cost of a project, the Federal laws and the rules and regulations made pursuant to such laws must be observed by the Contractor, and the work shall be subject to the inspection of the appropriate Federal agency. Such inspection shall in no sense make the Federal Government a party to this Contract and will in no way interfere with the rights of either party hereunder.

In the employment of labor (except in executive, administrative, and supervisory positions), preference shall be given to qualified individuals who have served in the military service of the United States (as defined in section 101(1) of the Soldiers' and Sailors' Civil Relief Act of 1940) and have been honorably discharged from that service, except that preference may be given only where that labor is available locally and is qualified to perform the work to which the employment relates.

70-06 SANITARY, HEALTH, AND SAFETY PROVISIONS. The Contractor shall provide and maintain in a neat, sanitary condition such accommodations for the use of employees as necessary to comply with the requirements of the State and local Board of Health, or of other bodies or tribunals having jurisdiction.

Attention is directed to Federal, State, and local laws, rules, and regulations concerning construction safety and health standards. The Contractor shall not expose the public to, or require any workers to work under, conditions that are unsanitary, hazardous, or dangerous to health or safety.

70-07 ARCHAEOLOGICAL OR HISTORICAL DISCOVERIES. Should the Contractor's operation encounter prehistoric artifacts, burials, remains of dwelling sites, or paleontological remains, such as shell heaps, land or sea mammal bones or tusks, the Contractor shall cease operations in that area immediately and notify the Engineer. No artifacts or specimens shall be further disturbed or removed from the ground and no further operations shall be performed in that area until so directed by the Engineer. Should the Engineer order suspension of the Contractor's operations in order to protect an archaeological or historical finding, or order the Contractor to perform extra work, such shall be covered by an appropriate contract change document.

70-08 PUBLIC CONVENIENCE AND SAFETY. The Contractor shall control his/her operations and those of his/her subcontractors and all suppliers, to assure the least inconvenience to the traveling public. Under all circumstances, safety shall be the most important consideration.

The Contractor shall maintain the free and unobstructed movement of aircraft and vehicular traffic with respect to his/her own operations and those of his/her subcontractors and all suppliers in accordance with subsection 40-04 and shall limit such operations for the convenience and safety of the traveling public as specified in subsection 80-04.

70-09 BARRICADES, WARNING SIGNS AND HAZARD MARKINGS. The Contractor shall furnish, erect, and maintain all barricades, warning signs and markings for hazards necessary to protect the public and the work. When used during periods of darkness, such barricades, warning signs and hazard markings shall be suitably illuminated. It shall be the Contractor’s responsibility to maintain markers at all times to separate areas closed to aircraft from adjacent areas which are open to aircraft.

For vehicular and pedestrian traffic, the Contractor shall furnish, erect, and maintain barricades, warning signs, lights and other traffic control devices in reasonable conformity with the Manual on Uniform Traffic Control Devices for Streets and Highways (published by the United States Government Printing Office) and the Alaska Supplement (published by the Department).

When the work requires closing an airport operations area of the airport or portion of such area, the Contractor shall furnish, erect and maintain temporary markings and associated lighting conforming to the requirements of AC 150/5340-1, Standards for Airport Markings.

The Contractor shall furnish, erect, and maintain markings and associated lighting of open trenches, excavations, temporary stockpiles, and his parked construction equipment that may be hazardous to the operation of emergency, fire-rescue, or maintenance vehicles on the airport in reasonable conformance to AC 150/5370-2, Operational Safety on Airports During Construction Activity.

The Contractor shall identify each motorized vehicle or piece of construction equipment in reasonable conformance to AC150/5370-2.

The Contractor shall furnish and erect all barricades, warning signs and markings for hazards prior to commencing work which requires such erection and shall maintain the barricades, warning signs and markings for hazards until their dismantling is directed by the Engineer.

Open-flame type lights shall not be permitted within the air operations areas of the airport.

70-10 USE OF EXPLOSIVES. When the use of explosives is necessary for the prosecution of the work, the Contractor shall exercise the utmost care not to endanger life or property, including new work. The Contractor shall be responsible for all damage resulting from the use of explosives.

The Contractor shall comply with all laws and ordinances, as well as with Title 29, Code of Federal Regulations, Part 1926, Safety and Health Regulations for Construction (OSHA), whichever is the most restrictive, with respect to the use, handling, loading, transportation, and storage of explosives and blasting agents.

The Contractor shall notify each property owner and utility company having structures in proximity to the site of work of his intention to use explosives. Such notice shall be given sufficiently in advance to enable them to take such steps as they may deem necessary to protect their property from injury.

The Contractor shall obtain the Engineer’s approval for the use of electric blasting caps within 1,000 feet of the airport property.

70-11 PROTECTION AND RESTORATION OF PROPERTY AND LANDSCAPE. The Contractor shall be responsible for and shall protect carefully from disturbance all land monuments and property marks until the Engineer has approved the witnessing or otherwise referenced their location and shall not move them without approval.

The Contractor shall be responsible for all damage or injury to property of any character, resulting from any act, omission, neglect, or misconduct in his manner or method of executing the work, or at any time due to defective work or materials, during the prosecution of the work, and said responsibility will not be released until the project shall have been completed and accepted.

When or where any direct or indirect damage or injury is done to public or private property by or on account of any act, omission, neglect or misconduct in the execution of the work, or in consequence of the non-execution thereof by the Contractor, he shall restore, at his own expense, such property to a condition similar or equal to that existing before such damage or injury, all in an acceptable manner.

The Contractor shall conduct work in a manner that minimizes disturbance to and protects natural resources in compliance with all Federal, State, and local laws and regulations. When working near designated wetlands, as defined by the Corps of Engineers 1987 Manual, the Contractor shall place no fill, nor operate equipment outside the permitted slope limits. When working in or near designated fish streams, as defined by AS 16.05.840 and .870, the Contractor shall not place fill or dredge material, nor operate equipment within or on the banks of the stream (including fording) except as permitted by the Fish Habitat Permit issued for the project. The Contractor shall maintain fuel handling and storage facilities in a manner which prevents the discharge of petroleum products into receiving wetlands, waters, or land. These protective measures shall be addressed in the Hazardous Materials Control Plan (HMCP).

The Contractor shall not excavate, nor use for fill, any material at any site suspected of or found to contain hazardous materials or petroleum fuels without approved permit and disposal plans. The Contractor shall not stockpile, nor dispose of, any material at any site suspected of or found to contain hazardous materials or petroleum. The Contractor shall report immediately to the Engineer any known or suspected hazardous material discovered, exposed, or released into the air, ground, or water during construction of the project. The Contractor shall also report any containment, cleanup, or restoration activities anticipated or performed as a result of such release or discovery. Hazardous materials include, but are not limited to petroleum products, oils, solvents, paints, and chemicals that are toxic, corrosive, explosive, or flammable.

The Contractor shall not use land from any park, recreation area, wildlife or waterfowl refuge, or any historical site located inside or outside of the project limits for excess fill disposal, staging activities, equipment or material storage, or for any other purposes unless permitted by the Contract or unless all permits and clearances necessary for such work have been obtained by the Contractor as detailed in subsection 70-02.

All debris, trash, and other solid waste from project construction shall be removed from the area as soon as possible and in accordance with the Department of Environmental Conservation Solid Waste Program.

70-12 FOREST PROTECTION. The Contractor shall comply with all regulations of the State of Alaska, local governments, Federal agencies or other authority having jurisdiction, governing the protection of forests and the carrying out of work within forests, and shall observe all laws and regulations with respect to the performance of work in forest areas. He shall keep the areas in an orderly condition, dispose of all refuse, obtain permits for the construction and maintenance of all construction camps, stores, warehouses, residences, latrines, cesspools, septic tanks, and other structures in accordance with the requirements of the supervising authorities.

The Contractor shall take all reasonable precautions to prevent and suppress forest fires and shall require his employees and subcontractors, both independently and at the request of officials, to do all reasonably within their power to prevent and suppress and to assist in preventing and suppressing forest fires and to make every possible effort to notify a Forest official at the earliest moment of the location and extent of any fire seen by them.

70-13 RESPONSIBILITY FOR DAMAGE CLAIMS. The Contractor shall indemnify, save harmless, and defend the Department, its agents and its employees from any and all claims, actions, or liabilities for injuries or damages sustained by any person or property arising directly or indirectly from the construction or the Contractor's performance of this Contract; however, this provision has no effect if, but only if, the sole proximate cause of the injury or damage is the Department's negligence.

It is specifically agreed between the parties executing this Contract that it is not intended by any of the provisions of the Contract to create in the public or any member thereof a third party benefit hereunder, or to authorize anyone not a party to this Contract to maintain a suit for personal injuries or property damage pursuant to the terms or provisions of this contract.

70-14 OPENING SECTIONS OF THE PROJECT TO TRAFFIC. Opening of sections of the work to traffic prior to completion of the entire project may be considered necessary. Such openings shall be made when ordered by the Engineer. Under no condition shall such openings constitute acceptance of the work or a part thereof, or a waiver of any provisions of the Contract. Necessary repairs or renewals made on sections of the work opened to traffic, due to defective materials or work or to causes other than ordinary wear and tear, pending acceptance of the work, shall be in accordance with Subsection 70-15.

70-15 CONTRACTOR’S RESPONSIBILITY FOR WORK. Until acceptance of the project by the Engineer, the Contractor shall have the charge and care thereof and shall take every precaution against injury or damage to any part thereof by the action of the elements or from any other cause, whether arising from the execution or from the nonexecution of the work. The Contractor shall rebuild, repair, restore, and make good all injuries or damages to any portion of the work occasioned by any of the above causes before acceptance of the work and without extra compensation, except damage to the work due to unforeseeable causes beyond the control of and without the fault or negligence of the Contractor, including but not restricted to acts of God, of the public enemy or governmental authorities. Damage caused by the public, prior to acceptance (Partial Acceptance or Project Completion), shall be corrected without extra compensation.

In case of suspension of work from any cause, the Contractor shall take such precautions as may be necessary to prevent damage to the work or facilities affected by the work. This will include providing for drainage and erecting any necessary temporary structures, signs, or other facilities and maintaining all living material such as plantings, seedings, and soddings.

70-16 CONTRACTOR'S RESPONSIBILITY FOR UTILITY PROPERTY AND SERVICES. At points where the Contractor's operations are adjacent to properties of railway, communications, pipelines, and power companies, or are adjacent to other property, damage to which might result in considerable expense, loss, or inconvenience, work shall not be commenced until all arrangements necessary for the protection thereof have been made.

The Contractor shall cooperate with the owners of any utility lines or other facilities in their removal and rearrangement operations in order that these operations may progress in a reasonable manner, that duplication of work may be reduced to a minimum, and that services rendered by those parties will not be unnecessarily interrupted.

All work undertaken near energized high voltage overhead electrical lines or conductors shall conform to AS 18.60.670, AS 18.60.675, and AS 18.60.680.

In the event of accidental interruption to utility services, the Contractor shall promptly notify the utility owner and the Engineer and cooperate with them until service has been restored. No work shall be undertaken around fire hydrants until provisions for continued service have been approved.

When utilities are damaged by the Contractor, the utility owner shall have the choice of repairing the utility himself or having the Contractor repair the damage. In the following circumstances, the Contractor shall reimburse the utility owner for repair costs or provide at no cost to the utility owner or State, all materials, equipment and labor if he repairs the damage himself:

- When the utility is shown on the Plans or other contract documents.

- When the utility has been field located by the owner or operator.

- When a proper or timely field locate request was not made by the Contractor.

- When the utility is visually apparent in the field.

- When the Contractor could have, otherwise, reasonably been expected to be aware of such utility.

The Contractor will not be responsible for the costs of repairing damaged utilities under either of the following circumstances:

- When the field locate by the owner or operator of a buried utility, is found to be in error by more than 2.5 feet horizontally.

- When the utility was not shown or indicated in the Contract or located by the utility owner and the Contractor could not reasonably have been expected to be aware of such utility.

In these cases, any repair work done by the Contractor will be considered Extra Work and he shall be reimbursed in accordance with Subsection 90-05. This shall not be construed as relieving the Contractor of his obligations under Subsections 20-06 and 50-06.

70-17 FURNISHING RIGHT-OF-WAY. The Department will be responsible for securing all necessary right-of-way or property in advance of construction. Any exceptions will be indicated in the Contract.

70-18 PERSONAL LIABILITY OF PUBLIC OFFICIALS. In carrying out any of the provisions of these Specifications, or in exercising any power or authority granted to them by or within the scope of the Contract, there shall be no liability upon the Engineer, or his authorized representatives, either personally or as officials of the State, it being understood that in all such matters they act solely as agents and representatives of the State.

70-19 NO WAIVER OF LEGAL RIGHTS. The Department shall not be precluded or estopped by any measurement, estimate, or certificate made either before or after the completion and acceptance of the work and payment therefor, from showing the true amount and character of the work performed and materials furnished by the Contractor, nor from showing that any measurement, estimate or certificate is untrue or is incorrectly made, nor that the work or materials do not in fact conform to the Contract. The Department shall not be precluded or estopped, notwithstanding any such measurement, estimate, or certificate and payment in accordance therewith, from recovering from the Contractor or his sureties, or both, such damages as it may sustain by reason of his failure to comply with the terms of the contract. Neither the acceptance by the Department, or any representative of the Department, nor any payment for or acceptance of the whole or any part of the work, nor any extension of time, nor any possession taken by the Department, shall operate as a waiver of any portion of the Contract or of any power herein reserved, or of any right to damages. A waiver by the Department of any breach of the Contract shall not be held to be a waiver of any other subsequent breach.

70-20 GRATUITY AND CONFLICT OF INTEREST. The Contractor agrees that he will not extend any loan, gratuity or gift of money of any form whatsoever to any employee of the Department nor will he rent or purchase any equipment or materials from any employee of the Department or to the best of his knowledge from any agent of any employee of the Department. Before payment of the final estimate, the Contractor shall execute and furnish the Department an affidavit certifying that he has complied with the above provisions of the Contract.

SECTION 80

PROSECUTION AND PROGRESS

80-01 SUBLETTING OF CONTRACT. The Contractor shall not, nor shall he permit any subcontractor to, sublet, sell, transfer, assign, or otherwise dispose of the Contract, or any portion thereof, or of his right, title, or interest therein, without written consent of the Engineer. In case such consent is given, the Contractor will be permitted to sublet a portion thereof, but shall perform with his own organization, work amounting to not less than 30% of the original contract amount, except that any items designated in the Contract as "specialty items" may be performed by subcontract and the cost of any such specialty items so performed by subcontract may be deducted from the total cost before computing the amount of work required to be performed by the Contractor with his own organization. For the purpose of this Subsection, work is defined as the dollar value of the services, equipment, materials, and/or manufactured products furnished under the contract. Consent to sublet, assign or otherwise dispose of any portion of the Contract shall not be construed to relieve the Contractor of any responsibility for the fulfillment of the Contract. No subcontracts, or transfer of contract, shall in any case release the Contractor of his liability under the Contract and bonds.

a.	Onsite Production. Onsite production of materials is considered as subcontracting, unless performed by the Contractor. Onsite production of materials is construed to be production of crushed stone, gravel, and other materials with portable or semiportable crushing, screening, or washing plants set up or reopened in the vicinity of the work for the purpose of supplying materials to be incorporated into the work on a designated project.

b.	Commercial Plants. The purchase of sand, gravel, crushed stone, crushed slag, batched concrete aggregates, ready-mixed concrete, and any other materials produced at and furnished from established and recognized commercial plants, together with the delivery of such materials to the site of work by means of vehicles owned and operated by such plants or by recognized commercial hauling companies, shall not be considered as subcontracting under these provisions.

c.	Hauling. Except as hereinafter stated, all hauling of materials from airport production sources, or from railroad or commercial truck delivery points, to batching plants, mixing plants, or directly to their place of use in the project, and all hauling of materials from batching plants and mixing plants to their place of use in the project, unless done by the Contractor's own equipment or recognized commercial hauling companies, shall be considered as subcontracting under these provisions.

If batching plants or mixing plants are set up at rail or commercial truck delivery points and material in part supplied to such plants by rail or commercial truck transportation companies, the remaining materials required at such batching or mixing plants may be hauled to such plants without such hauling being considered as subcontracting.

d.	Owner-Operators. The Contractor (or an approved subcontractor) shall not be required to submit subcontracts for approval for the hauling of materials for the project by bona fide truck owner-operators who are listed as such on the certified payroll.

Truck owner-operators shall be required to submit documentation to the Contractor as is necessary to prove the trucker is a bona fide owner-operator. As a minimum, those records, for each truck owner-operator, shall include current and valid copies of the following:

- Alaska Driver's License with appropriate CDL class and endorsements.

- Business license for trucking together with supporting documents that list the driver as the business owner or corporate officer.

- Documents showing the driver's ownership interest in the truck including

- truck registration, and

- lease (if truck is not registered in driver's name or in the name of the driver's company).

The Contractor shall maintain legible copies of such records for a period of at least three years after final acceptance of the project.

Additionally, to be classified as a valid owner-operator a truck driver must also qualify as an independent contractor under the following Alaska Department of Labor (DOL) criteria which establishes whether or not they are an employee or an independent contractor. The status of owner-operators is subject to evaluation throughout the project period and when the criteria for an independent contractor are not found to exist, amended payrolls must be submitted listing the driver as an employee subject to all labor provisions of the Contract. These criteria are:

- the owner-operator's right to control the manner in which the work is to be performed;

- the owner-operator's opportunity for profit or loss depending upon their managerial skill;

- the owner-operator's investment in equipment or materials required for their task, or the employment of helpers;

- whether the service rendered requires a special skill;

- the degree of permanence of the working relationship; and

- whether the service rendered is an integral part of the owner-operator's business.

The Contractor shall issue a placard to each owner-operator. The placard shall identify both the truck driver and the vehicle and shall be prominently displayed such that it is visible to the scale person or inspectors. The identification system must be approved by the Engineer prior to use.

e.	Submittal of Subcontracts. The Contractor shall furnish the Engineer with 3 copies of any and all subcontracts. Subcontracts which are submitted for approval shall be signed by both parties and dated in order to be considered acceptable. Prices of subcontracted work shall be furnished by the Contractor. The Engineer will determine the value of the subcontract(s), based on contract unit prices, or upon reasonable value, if entire items are not subcontracted.

When the Contractor elects to utilize the services of a professional land surveyor or registered engineer to perform the construction related surveying, a professional services contract may be used. The professional land surveyor or registered engineer shall comply with provisions of AS 08.48 rather than AS 08.18. The stipulated criteria for submitting and approving/disapproving these agreements shall be the same as required for subcontracts. The professional land surveyor or professional engineer is not exempt from the requirements of AS 36, AS 43, or any other applicable Alaska Statute for on-site construction surveying services.

The Contractor shall ensure that the required prompt payment provisions of AS 36.90.210 are included in all subcontracts.

80-02 NOTICE TO PROCEED. The Notice to Proceed will stipulate the date on which it is expected the Contractor will begin the construction and from which date contract time will be charged. Construction operations shall not be performed before the effective date of the Notice to Proceed. The Contractor shall notify the Engineer at least 48 hours in advance of the time actual construction operations will begin.

80-03 PROSECUTION AND PROGRESS. Prior to commencing work, the Contractor shall meet with the Engineer for a preconstruction conference. Five working days before the preconstruction conference the Contractor shall submit the following:

- A progress schedule, in a format acceptable to the Engineer, showing the order in which he proposes to carry out the work and the contemplated dates on which he and his subcontractors will start and finish each of the salient features of the work, including any scheduled periods of shutdown. The schedule shall also indicate any anticipated periods of multiple-shift work.

- A list showing anticipated dates for procurement of materials and equipment, the ordering of articles of special manufacture, the furnishing of plans, drawings and other data required under Subsections 50-02 and 60-08, and for any other events such as inspection of structural steel fabrication.

- A list showing all proposed subcontractors and material suppliers.

- A Storm Water Pollution Prevention Plan and a Hazardous Material Control Plan.

- A letter designating the Contractor's Superintendent, defining that person's responsibility and authority, and providing a specimen of his signature.

- A letter designating the EEO Officer and the DBE Officer and those persons’ responsibilities and authority.

- A Traffic Control Plan, when required.

- A Submittal Register, in accordance with Subsection 60-08.

The Contractor shall provide adequate materials, labor and equipment to ensure the completion of the project in accordance with the Plans and Specifications. The work shall be performed as vigorously and as continuously as weather conditions or other interferences may permit. The Contractor shall take into consideration and make due allowances for foreseeable delays and interruptions to the work such as unfavorable weather, equipment breakdowns, shipping delays, quantity overruns, utility work and permit restrictions. He shall adjust his forces, equipment and work schedules as may be necessary to ensure completion of the work within the contract time.

Upon substantial changes to the Contractor's schedule of work or upon request of the Engineer, the Contractor shall submit revised progress schedules in the form required. Such revised schedules shall conform with the contract time and take into account changes or delays which may have been encountered in the performance of the work. In submitting a revised schedule, the Contractor shall state specifically the reason for the revision and the adjustments made in his schedule or methods of operation to ensure completion of all work within the contract time.

Should the prosecution of the work be discontinued for any reason, the Contractor shall notify the Engineer at least 24 hours in advance of resuming operations.

80-04 LIMITATION OF OPERATIONS. The Contractor shall not open up work to the prejudice or detriment of work already started. The Engineer may require the Contractor to finish a section on which work is in progress before work is started on any additional section if the opening of such section is essential to public convenience. The Contractor shall not be allowed to stop or otherwise impede traffic outside of the project limits without written permission.

The Contractor shall control his operations and the operations of his subcontractors and all suppliers so as to provide for the free and unobstructed movement of aircraft in the Air Operations Areas of the airport and the least inconvenience to traffic. Under all circumstances, safety shall be the most important consideration.

When the work requires the Contractor to conduct his operations within an Air Operations Area of the airport, the work shall be coordinated with airport management (through the Engineer) at least 48 hours prior to closure or change in the Air Operations Area or startup, resumption, cessation of or change in construction activity that affects aircraft operations. The Contractor shall not close an Air Operations Area until so authorized by the Engineer and until the necessary temporary marking and associated lighting is in place as provided in Subsection 70-09.

Vehicles, equipment and materials shall never be parked or left standing on open runways and taxiways. In Air Operations Areas, all vehicles shall be provided with a functional flashing amber hazard light and all obstructions except stakes or hazard markers shall be removed during non-working hours. The Contractor shall remove construction equipment from and otherwise clear the runway and the designated Runway Safety Areas for operation of regularly scheduled airline flights. He shall remain continuously informed regarding flight schedule times.

When the contract work requires the Contractor to work within an Air Operations Area of the airport on an intermittent basis (intermittent opening and closing of the Air Operations Area), the Contractor shall maintain constant communications as hereinafter specified; immediately obey all instructions to vacate the Air Operations Area; and immediately obey all instructions to resume work in such Air Operations Area. Failure to maintain the specified communications or to obey instructions shall be cause for suspension of the Contractor's operations in the Air Operations Area until the satisfactory conditions are provided. The Contractor shall establish and maintain communication or monitor communications with the appropriate radio facility as prescribed in the following:

- Airports With Control Towers: At those airports with control towers, the Contractor shall comply with the requests of the controller using 2-way radio communication on the appropriate ground control frequency. The Contractor shall furnish a liaison radio operator and radio with each work party located within a Runway or Taxiway Safety Area.

- Airports Without Control Towers:

- With a Flight Service Station: When the airport has an operating FSS, the Contractor shall have a liaison radio operator and 2-way radio communications on the work site whenever work is being conducted in the Air Operations Area. The frequency used will be the Common Traffic Advisory Frequency (CTAF) published in the current Alaska Flight Information Supplement.

- Without a Flight Service Station: At those airports without an operating FSS, whenever work is being conducted in the Air Operations Area, the Contractor shall monitor the Common Traffic Advisory Frequency (CTAF) published in the current Alaska Flight Information Supplement.

80-05 CHARACTER OF WORKMEN, METHODS AND EQUIPMENT. The Contractor shall at all times employ sufficient labor and equipment for prosecuting the several classes of work to full completion in the manner and time required by these Specifications.

All workers shall have sufficient skill and experience to perform properly the work assigned to them. Workers engaged in special work or skilled work shall have sufficient experience in such work and in the operation of the equipment required to perform all work properly and satisfactorily.

Any person employed by the Contractor or by any subcontractor who, in the opinion of the Engineer, does not perform his work in a proper and skillful manner or is intemperate or disorderly shall, at the written request of the Engineer, be removed forthwith by the Contractor or subcontractor employing such person, and shall not be employed again in any portion of the work without the approval of the Engineer.

Should the Contractor fail to remove such person or persons as required above, or fail to furnish suitable and sufficient personnel for the proper prosecution of the work, the Engineer may suspend the work by written notice until such orders are complied with.

No convict labor shall be employed under this contract. This provision shall not be construed as applying to convicts on parole or probation.

All equipment which is proposed to be used shall be of appropriate size and in such mechanical condition as to meet the requirements of the work and to produce a satisfactory quality of work.

When the methods and equipment to be used by the Contractor in accomplishing the construction are not prescribed in the Contract, the Contractor is free to use any methods or equipment that he demonstrates to the satisfaction of the Engineer will accomplish the contract work in conformity with the requirements of the Contract, except as provided above.

When the Contract specifies that the construction be performed by the use of certain methods and equipment, such methods and equipment shall be used unless others are authorized by the Engineer. If the Contractor desires to use a method or type of equipment other than specified in the contract, he may request authority from the Engineer to do so. The request shall be in writing and shall include a full description of the methods and equipment proposed and of the reasons for desiring to make the change. If approval is given, it will be on the condition that the Contractor will be fully responsible for producing work in conformity with contract requirements. If, after trial use of the substituted methods or equipment, the Engineer determines that the work produced does not meet contract requirements, the Contractor shall discontinue the use of the substitute method or equipment and shall complete the remaining work with the specified methods and equipment. The Contractor shall remove any deficient work and replace it with work of specified quality, or take such other corrective action as the Engineer may direct. No change will be made in basis of payment for the contract items involved nor in contract time as a result of authorizing a change in methods or equipment under this subsection.

80-06 DETERMINATION AND EXTENSION OF CONTRACT TIME.

a.	Calendar Days. When the contract time is specified on a calendar days basis, all work under the Contract shall be completed within the number of calendar days specified. The count of contract time begins on the day following receipt of the Notice to Proceed by the Contractor, if no starting day is stipulated therein.

Calendar days shall continue to be counted against contract time until and including the date of project completion. Calendar days, however, shall not be counted during the period from November 1 through April 30.

b.	Completion Date. When the contract time is specified by a completion date, all work under the contract shall be completed by that date.

c.	Suspension and Extension of Contract Time. The Engineer may, by written order, suspend work on the project, in whole or in part, for such periods as he determines to be necessary.

In those instances where the Engineer orders suspension of the work for unsafe conditions, for adverse weather, for failure by the Contractor to carry out contractual provisions, or for failure to carry out orders given by the Engineer within the limits of his contractual authority, the count of contract time shall continue through the suspension period.

Contract time may be extended by the Engineer because of delays in the completion of controlling items of work due to unforeseeable causes beyond the control of and without the fault or negligence of the Contractor, including but not restricted to acts of God or of the public enemy, fires, floods, epidemics, quarantine restrictions, strikes, freight embargoes, and unusually severe weather or delays of subcontractors due to such causes provided that the Contractor shall, within 10 days of the beginning of any such delay, notify the Engineer in writing of the cause of delay and request an extension of contract time. The Engineer will ascertain the facts and the extent of the delay and extend the time for completing the work when, in his judgment, the findings of fact justify such an extension. The Contractor's pleas that insufficient time was originally specified shall not constitute a valid reason for extension of contract time.

The time allowed in the contract, as awarded, for the performance of the work is based on the original estimate of the quantities, as defined in Subsection 20-03. If satisfactory fulfillment of the Contract requires performance of additional work or work in greater quantities than those set forth in the bid, the contract time may be extended on a basis commensurate with the amount and difficulty of the added work, provided that the added work is for a controlling item.

Suspension of work by the Engineer or delays in the completion of the work shall not constitute grounds for any claims by the Contractor for damages or extra compensation, unless otherwise provided for in the Contract.

80-07 FAILURE TO COMPLETE ON TIME. For each calendar day that the work remains incomplete after the expiration of the contract time the sum per day given in the following schedule shall be deducted from any monies due the Contractor. If no money is due the Contractor, the Department shall have the right to recover said sum from the Contractor, the surety or both. The amount of these deductions is to reimburse the Department for estimated additional contract administration expenses incurred as a result of the Contractor's failure to complete the work within the time specified. Such deductions are liquidated damages and are not to be considered as penalties.

Table 80-1	DAILY CHARGE FOR LIQUIDATED DAMAGES

FOR EACH CALENDAR DAY OF DELAY

| Original Contract Amount ($) | Daily Charge ($) |
| --- | --- |
| From More Than | To and Including |  |
| 0 | 100,000 | 300 |
| 100,000 | 500,000 | 550 |
| 500,000 | 1,000,000 | 750 |
| 1,000,000 | 2,000,000 | 1,000 |
| 2,000,000 | 5,000,000 | 1,500 |
| 5,000,000 | 10,000,000 | 2,500 |
| 10,000,000 | No Limit | 3,000 |

Permitting the Contractor to continue and finish the work or any part of it after the time fixed for its completion, or after the date to which the time for completion may have been extended, will in no way operate as a waiver on the part of the Department of any of its rights under the Contract.

80-08 DEFAULT OF CONTRACT. The Engineer will give notice in writing to the Contractor and his surety of such delay, neglect, or default if the Contractor:

- fails to begin work under the Contract within the time specified on the bid;

- fails to perform work with sufficient workmen, equipment or materials to assure the prompt completion of said work;

- performs the work unsuitably or neglects or refuses to remove materials or to perform anew such work as may be rejected as unacceptable and unsuitable;

- discontinues the prosecution of the work;

- fails to resume work which has been discontinued within a reasonable time after notice to do so;

- becomes insolvent, except that if the Contractor declares bankruptcy, termination shall be in accordance with 11 U.S.C. 362 and/or 11 U.S.C. 365. In the event that the Contractor declares bankruptcy, the Contractor agrees that the Contract will be assumed or rejected in a timely manner so that the contract will be completed by the date specified in the Contract;

- is nonresponsive to any final third party judgments;

- makes an assignment for the benefit of creditors, without the consent of the Engineer;

- is a party to fraud, or

- for any other cause whatsoever, fails to carry on the work in an acceptable manner.

If the Contractor or surety, within the time specified in the notice, shall not proceed in accordance therewith, then the Department may, upon written notification from the Engineer of the fact of such delay, neglect or default and the Contractor's failure to comply with such notice, have full power and authority, without violating the Contract, to take the prosecution of the work out of the hands of the Contractor. The Department may appropriate or use any or all materials and equipment on the project site as may be suitable and acceptable and may enter into an agreement for the completion of said contract according to the terms and provisions thereof, or use such other methods that in the opinion of the Engineer are required for the completion of said Contract in an acceptable manner.

The Engineer may, by written notice to the Contractor and his surety or his representative, transfer the employment of the work from the Contractor to the surety, or if the Contractor abandons the work undertaken under the Contract, the Engineer may, at his option, with written notice to the surety and without any written notice to the Contractor, transfer the employment for said work directly to the surety. The surety shall submit its plan for completion of the work, including any contracts or agreements with third parties for such completion, to the Department for approval prior to beginning completion of the work. Approval of such contracts shall be in accordance with all applicable Departmental requirements and procedures for approval of subcontracts, except that the limitation on percent of work subcontracted shall not apply.

Upon receipt of such notice the surety shall enter upon the premises and take possession of all materials, tools, and appliances thereon for the purpose of completing the work included under the contract and employ, by contract or otherwise, any person or persons to finish the work and provide the materials therefor, without termination of the continuing full force and effect of this agreement. In case of such transfer of employment to the surety, the surety shall be paid in its own name on estimates covering work subsequently performed under the terms of the Contract and according to the terms thereof without any right of the Contractor to make any claim for the same or any part thereof.

In case of discontinuance of employment by the Engineer as aforesaid, the Contractor shall not be entitled to receive any further balance of the amount to be paid under the Contract until the work shall be fully finished, at which time, if the unpaid balance of the amount to be paid under this Contract shall exceed the expenses incurred by the Engineer in finishing the work and all damages sustained, or which may be sustained by the Department by reason of such refusal, neglect, failure or discontinuance of employment, such excess shall be paid by the Department to the Contractor, but if such expenses and damage shall exceed the unpaid balance, the Contractor and his surety and each thereof shall be jointly and severally liable therefor to the Department, and shall pay the difference to the Department.

If, after notice of termination of the Contractor's right to proceed under the provisions of this clause, it is determined for any reason that the Contractor was not in default under the provisions of this clause, or that the delay was excusable under the provisions of this clause, the rights and obligations of the parties shall be the same as if the notice of termination had been issued pursuant to Subsection 80-09 as a termination for convenience of the Department.

80-09 TERMINATION OF WORK FOR DEPARTMENT'S CONVENIENCE. The performance of work under the contract may be terminated by the Department in accordance with this section in whole or in part, whenever, for any reason the Contracting Officer determines that such termination is in the best interest of the Department. Any such termination shall be effected by delivery to the Contractor of a Notice of Termination specifying termination is for the convenience of the Department, the extent to which performance of work under the Contract is terminated, and the effective date of the termination.

After receipt of a Notice of Termination and except as otherwise directed by the Contracting Officer, the Contractor shall:

- Stop work under the Contract on the date and to the extent specified in the Notice of Termination;

- Place no further orders or subcontracts for materials, services, or facilities except as may be necessary for completion of such portion of the work under the Contract as is not terminated;

- Terminate all orders and subcontracts to the extent that they relate to the performance of work terminated by the Notice of Termination;

- With the approval or ratification of the Contracting Officer, to the extent he may require, settle all outstanding liabilities and all claims arising out of such termination of orders and subcontracts, the cost of which would be reimbursable, in whole or in part, in accordance with the provisions of the Contract;

- Submit to the Contracting Officer a list, certified as to quantity and quality, of any or all items of termination inventory exclusive of items the disposition of which had been directed or authorized by the Contracting Officer;

- Transfer to the Contracting Officer the completed or partially completed plans, drawings, information, and other property which, if the Contract had been completed, would be required to be furnished to the Department;

- Take such action as may be necessary, or as the Contracting Officer may direct, for the protection and preservation of the property related to the Contract which is in the possession of the Contractor and in which the Department has or may acquire any interest.

The Contractor shall proceed immediately with the performance of the above obligations notwithstanding any delay in determining or adjusting the amount of any item or reimbursable cost under this clause.

When the Department orders termination of work under a contract effective on a certain date, all completed units of work within each pay item as of that date will be paid for at the contract unit price. Payment for partially completed work will be made at actual costs incurred plus a reasonable profit. Payment for materials included in the materials inventory described in e. above will be made at actual cost delivered to the project or storage site, including transportation charges, to which cost 15% will be added.

After receipt of a Notice of Termination, the Contractor shall submit to the Contracting Officer, his claim for additional damages or costs not covered above or elsewhere in these Specifications. Such claim may include such cost items as reasonable idle equipment time, mobilization efforts, bidding and project investigative costs, overhead expenses directly allocable to the project termination and not covered under work paid for in the preceding paragraph, legal and accounting charges and other expenses reasonably necessary in claim preparation, subcontractor costs not otherwise paid for, actual idle labor costs if work is stopped in advance of termination date, guaranteed payments for private land usage as part of the original Contract, and any other costs for which the Contractor feels reimbursement should be made. The intent of negotiating this claim would be to reach an equitable settlement figure with the Contractor for the actual costs incurred. In no event, however, will loss of anticipated profits or consequential damages be considered as part of any settlement.

For any claim related to operating equipment owned by the contractor, the contractor is entitled to recover equipment costs based on the contractor's actual costs for ownership and actual operating expenses. For any claim related to idle equipment time for equipment owned by the contractor, the contractor is entitled to recover equipment rates based on the contractor's internal ownership costs. Recovery for operating equipment or idle equipment time shall not be based on published rental rates. Claims for idle equipment time following termination of the contract are limited to a maximum of 30 days, and may not include any operating expenses. In the case of rented or leased equipment, the contractor shall recover the lesser of its actual rental costs or fair market rental costs, and the amount paid shall not exceed 30 days rental.

The termination claim shall be submitted promptly, but in no event later than 90 days from the effective date of termination, unless one or more extensions in writing are granted by the Contracting Officer upon request of the Contractor made in writing within the 90 day period. Upon failure of the Contractor to submit his termination claim within the time allowed, the Contracting Officer may determine, on the basis of information available to him, the amount, if any, due the Contractor by reason of the termination and will thereupon pay to the Contractor the amount so determined.

The Contractor and the Contracting Officer may agree upon whole or any part of the amount or amounts to be paid to the Contractor by reason of the total or partial termination of work pursuant to this section. The Contract will be amended accordingly, and the Contractor will be paid the agreed amount.

In the event of the failure of the Contractor and the Contracting Officer to agree in whole or in part, as provided heretofore, as to the amounts with respect to costs to be paid to the Contractor in connection with the termination of work the Contracting Officer will determine, on the basis of information available to him, the amount, if any, due to the Contractor by reason of the termination and will pay the Contractor the amount determined as follows:

- All costs and expenses reimbursable in accordance with the Contract not previously paid to the Contractor for the performance of the work prior to the effective date of the Notice of Termination;

- So far as not included under a. above, the cost of settling and paying claims arising out of the termination of work under subcontracts or orders which are properly chargeable to the terminated portions of the Contract;

- The reasonable costs of settlement with respect to the terminated portion of the Contract heretofore, to the extent that these costs have not been covered under the payment provisions of the Contract.

The Contractor shall have the right of appeal under the Department's claim procedures for any determination made by the Contracting Officer, except if the Contractor has failed to submit his claim within the time provided and has failed to request extension of such time, he shall have no such right of appeal.

- In arriving at the amount due the Contractor under this section, there shall be deducted:

- All previous payments made to the Contractor for the performance of work under the contract prior to termination;

- Any claim which the Department may have against the Contractor;

- The agreed price for, or the proceeds of sale of, any materials, supplies, or other things acquired by the Contractor or sold pursuant to the provisions of this section and not otherwise recovered by or credited to the Department; and,

- All partial payments made to the Contractor under the provisions of this section.

The Department will from time to time, under such terms and conditions as it may prescribe, make partial payments on account against costs incurred by the Contractor in connection with the terminated portion of the contract whenever in the opinion of the Contracting Officer the aggregate of such payments shall be within the amount to which the Contractor will be entitled hereunder, otherwise the Contractor shall not be entitled to receive further payments until final settlement is reached.

Where the work has been terminated by the Department, said termination shall not affect or terminate any of the rights of the Department against the Contractor or his surety then existing or which may thereafter accrue because of such termination. Any retention or payment of monies by the Department due to the Contractor under the terms of the Contract shall not release the Contractor or his surety from liability.

Unless otherwise provided for in the Contract, or by applicable statute, the Contractor, from the effective date of termination and for a period of three years after final settlement under this Contract, shall preserve and make available to the Department at all reasonable times at the office of the Contractor, all its books, records, documents, and other evidence bearing on the cost and expenses of the Contractor under this Contract and relating to the work terminated hereunder.

80-10 TERMINATION FOR NATIONAL EMERGENCIES. The Department shall terminate the Contract or portion thereof by written notice when the Contractor is prevented from proceeding with the construction contract as a direct result of an Executive Order of the President with respect to the prosecution of war or in the interest of national defense.

When the contract, or any portion thereof, is terminated before completion of all items of work in the Contract, payment will be made for the actual number of units or items of work completed at the contract price or as mutually agreed for items of work partially completed or not started. No claims for loss of anticipated profits shall be considered.

Reimbursement for organization of the work, and other overhead expenses when not otherwise included in the Contract, and moving equipment and materials to and from the job will be considered, the intent being that an equitable settlement will be made with the Contractor.

Acceptable materials, obtained or ordered by the Contractor for the work and that are not incorporated in the work shall, at the option of the Contractor, be purchased from the Contractor at actual cost as shown by receipted bills and actual cost records at such points of delivery as may be designated by the Engineer.

Termination of the contract or a portion thereof shall neither relieve the Contractor of his/her responsibilities for the completed work nor shall it relieve his/her surety of its obligation for and concerning any just claim arising out of the work performed.

SECTION 90

MEASUREMENT AND PAYMENT

90-01 GENERAL. Wherever it is provided in the Contract that certain work is a subsidiary obligation or it is stated that certain provisions or work be without extra compensation; it is understood in both cases that the Contractor's compensation for such work is to be included in the payment for other items of work.

Lump sum items will not be measured for payment. The bid amount is complete payment for all work described in the Contract and necessary to complete that item. Quantities shown for lump sum items are approximate. Unless otherwise stated, no adjustment in the lump sum price to be paid will be made if the quantity furnished is more or less than the estimated quantity.

90-02 MEASUREMENT OF QUANTITIES. All work completed under the Contract will be measured using the US Customary system of measure. Unless otherwise specified, work will be measured as follows:

- Foot. Measurement will be from end to end, in place, parallel to the centerline of the item or ground surface upon which such items are placed.

- Station (100 feet). Measurement will be made horizontally and parallel to centerline.

- Square Foot. Measurement will be made parallel to the surface being measured. No deductions will be made for individual fixtures having an area of 9 square feet or less. Transverse measurement for area computations will be the neat dimensions shown on the Plans or ordered in writing.

- Acre. Measurement will be made horizontally, unless specified on the ground surface. No deductions will be made for individual fixtures having an area of 500 square feet or less.

- Cubic Yard. Measurement will be made at the location specified and using one of the following methods:

Average end area. End areas are calculated as the area between original ground cross section and the final cross section. Volume of material is calculated using the average of end areas multiplied by the distance along centerline between end areas.

Where it is impractical to measure material by cross sectioning due to erratic location of isolated deposits, acceptable methods involving three-dimensional measurements may be used.

Structures will be measured according to neat lines shown on the Plans or as altered to fit field conditions.

When requested by the Contractor and approved in writing, material specified to be measured by the cubic yard may be weighed and such weights will be converted to cubic yards for payment purposes. Factors for conversion from weight measurement to volume measurement will be determined by the Engineer and shall be agreed to by the Contractor before such method of measurement of pay quantities is used.

When liquid asphalt is a pay item, use ASTM D 4311 to convert from weight to volume at 60 °F.

Material to be measured by volume in the hauling vehicle will be measured by the cubic yard at the point of delivery. Vehicles for this purpose may be of any acceptable size or type provided that the body is of such shape that the actual contents may be readily and accurately determined. Vehicles shall be loaded to and payment made on the measured vehicle volume and loads shall be leveled when directed. When legal loads are applicable, the approved volume measurement shall not exceed the legal capacity of the vehicle.

f.	Gallon. Measurement will be made by one of the following methods:

- Measured or calibrated volume tank.

- Metered volume.

- Weighed under this subsection and converted to volume, using the specified conversion factor.

g.	Pound. Measurement will be made using a certified scale or the net weight of packaged material as labeled by the manufacturer.

h.	Ton. (Short ton consisting of 2000 pounds avoirdupois). Measurement will be made by one of the following methods:

- Commercial weighing system. Use permanently installed and certified commercial scales.

- Project weighing system. As specified under Subsection G-130.

- Invoices. If bulk material is shipped by truck or rail and is not passed through a mixing plant, furnish a supplier’s invoice with net weight or volume converted to weight. Periodic check weighing may be required.

Trucks used to haul material being paid for by weight shall be weighed empty at least once daily and at such times as directed. Each truck shall bear a plainly legible identification mark.

Due to possible variations in the specific gravity of the aggregates, the weight used may vary from the bid quantities and no adjustment in contract unit price will be made because of such variation.

If material is shipped by rail, the car weight may be accepted provided that only the actual weight of material is paid for. Car weights will not be acceptable for material to be passed through mixing plants.

Net certified scale weights or weights based on certified volumes in the case of rail shipments may be used as a basis of measurement, subject to correction when asphalt material has been lost, wasted, or otherwise not incorporated into the work.

When asphalt materials are shipped by truck or transport, net certified weights or volume, subject to correction for loss or foaming, may be used for computing quantities.

- Barge Displacement Method. When the barge displacement method is proposed the Contractor shall furnish fresh water loading charts, certified by a Professional Engineer for all barges utilized in the hauling of the material. If barge hauled material is stockpiled, loss shall be estimated by the Engineer and shall be deducted from the total weight measured to allow for stockpile loss. Any material wasted or lost between the barge and the point where it is placed in final position shall be estimated and the loss deducted by the Engineer.

When standard manufactured items are specified such as fence, wire, plates, rolled shapes, pipe conduit, etc., and these items are identified by unit weight, section dimensions, etc., such identification will be considered to be nominal weights or dimensions. Unless more stringently controlled by tolerances in cited specifications, manufacturing tolerances established by the industries involved will be accepted.

90-03 SCOPE OF PAYMENT. The Contractor shall receive and accept compensation provided for in the Contract as full payment for furnishing all equipment, materials, tools, and labor necessary to complete the work under the Contract in a complete and acceptable manner and for all risk, loss, damage, or expense of whatever character arising out of the nature of the work or the prosecution thereof, subject to the provisions of Subsection 70-19.

If the "Basis of Payment" clause for a contract item requires that the unit price include compensation for certain work or material essential to the item, this same work or material will not also be measured or paid for under any other contract item which may appear elsewhere in the Specifications.

If changes or additions in the work are ordered which will vary the quantity of work to be paid under a lump sum pay item, the lump sum payment will be increased or decreased in amount determined by multiplying the changed quantity by the contract lump sum priced divided by the estimated quantity shown on the Plans.

When an item is listed under one or more Additive Alternates, numerical suffixes will be included as part of the pay item numbers for the Additive Alternates in order to differentiate between the Basic Bid and Additive Alternates.

The numerical suffix .1 is for Additive Alternate 1.

The numerical suffix .2 is for Additive Alternate 2.

90-04 COMPENSATION FOR ALTERED QUANTITIES. Payment to the Contractor for unit price items shall be made only for the actual quantities of work performed and accepted or materials furnished, in conformance with the Contract. When the accepted quantities of work or materials vary from the quantities stated in the bid schedule, the Contractor shall accept as payment in full, payment at the original contract unit prices for the quantities of work and materials furnished, completed and accepted; except as provided below:

Where the final quantity of a major contract item varies more than 25% above or below the bid quantity, either party to the contract may request an equitable adjustment in the contract unit price of that item.

When the final quantity of work is greater than 125% of the bid quantity, the equitable adjustment shall be made only for those units which are in excess of 125% of the bid quantity.

When the final quantity of work is less than 75% of the bid quantity, the equitable adjustment shall be made for those units of work done and accepted, except that the total payment for the item shall not exceed 75% of the total amount bid for the item.

Except as provided above and in Subsection 40-02, no allowance shall be made for any increased expenses, loss of expected reimbursement or loss of anticipated profits suffered or claimed, either directly from such alterations in quantities or indirectly from unbalanced allocations among the contract items on the part of the bidder and subsequent loss of expected reimbursements therefor, or any other causes.

90-05 COMPENSATION FOR EXTRA WORK. Extra work will be paid for at the unit prices or lump sum stipulated in the change document authorizing the work, or the Engineer may compensate the Contractor for such work on a time and materials basis to be computed in the following manner:

a.	Labor. Compensation will be the sum of (1) through (6), computed by the Engineer as follows:

- Total hours worked times the straight time rate of pay. For all labor and foremen in direct charge of the specific operations, the Contractor shall be paid at the rates indicated on the certified payroll, but at rates not to exceed those for comparable labor currently employed on the project.

- Overtime hours worked times the difference between the overtime rate and straight time rate.

- Fringe benefit rate times the total hours worked. Fringe benefits include Health and Welfare, Pension Fund, etc., when such amounts are required by collective bargaining agreement or other employment contract generally applicable to the classes of labor employed on the project.

- Workers' Compensation Insurance at 8% of (1). The actual net rate may be used if it exceeds 10% and if proof of rates are furnished within 30 days of the completion of the extra work.

- Either subsistence and travel allowances or prorated camp costs. If any employee is due and receives subsistence or camp privileges on his days off, this amount shall be divided by the number of days worked that week and shall be added to his daily subsistence for time and materials entitlement. If the employee did not work an entire day on time and materials work, that day's entitlement shall be in direct proportion to the hours worked on time and materials.

- Labor markup at 35% of the sum of (1), (3), (4), and (5). Labor markup covers additional bond, property damage liability insurance, unemployment insurance contributions, social security and other taxes, administrative overhead costs and profit.

b.	Materials. For materials accepted by the Engineer and used in the work, the Contractor shall receive the actual cost of such materials including transportation charges paid by him (exclusive of equipment rentals as hereinafter set forth) to which cost 15% will be added.

The Contractor shall furnish to the Engineer invoices for all materials used in the work plus applicable freight charges. If materials used on the time and materials work are taken from the Contractor's stock, then the Contractor shall furnish to the Engineer a certified statement showing the actual direct cost to the Contractor of said materials and the quantities used in the work.

c.	Equipment. For any machinery or special equipment (other than small tools) which has been authorized by the Engineer, compensation shall be determined as follows:

- Hourly rental rate. The Contractor shall receive the rental rates in the current edition and appropriate volume of the Rental Rate Blue Book for Construction Equipment, published by PRIMEDIA Information, Inc., 1735 Technology Drive, Suite 410, San Jose, CA 95110-1313.

The regular hourly rental rate shall be equal to the adjusted monthly rate for the basic equipment plus the adjusted monthly rate for applicable attachments, both divided by 176, and multiplied by the area adjustment factor, plus the estimated hourly operating cost. These rates shall apply for equipment used during the Contractor's regular shift of 10 hours per day.

The adjusted monthly rate is that resulting from application of the rate adjustment formula in order to eliminate replacement cost allowances in machine depreciation and contingency cost allowances.

Attachments shall not be included unless required for the time and materials work.

- Hourly overtime rate. Where the equipment is used more than 10 hours per day, either on the Contractor's normal work or on time and materials, and either on single or multiple shifts, the overtime rate shall be 1/2 of the regular hourly rental rate.

- Hourly standby rate. Equipment ordered to be on a stand-by basis shall be paid for at the stand-by rental rate during the Contractor's normal work shift, but not to exceed 8 hours per day.

The stand-by rental rate shall be equal to the adjusted monthly rate for the basic equipment plus the adjusted monthly rate for applicable attachments, both divided by 352, all multiplied by the area adjustment factor.

- Unlisted equipment. For equipment not listed in The Blue Book, the Contractor shall receive a rental rate as agreed upon before such work is begun. If agreement cannot be reached, the Department reserves the right to establish a rate based on similar equipment in The Blue Book or prevailing commercial rates in the area.

- Leased or rented equipment. Equipment which must be rented or leased specifically for work required under this section shall be authorized in writing by the Engineer. The Contractor shall be paid invoice price plus 15%.

- Transportation of equipment. When it is necessary to obtain equipment from sources beyond the project limits exclusively for time and materials work, the actual cost of transferring the equipment to the site of the work and return will be reimbursed. Where the move is made by common carrier, the move-in allowance will be limited to the amount of the paid freight bill or invoice. If the Contractor hauls the equipment with his own forces, the allowance will be limited to the rental rate for the hauling unit plus operator wages. In the event that the equipment is transferred under its own power, the moving allowance will be limited to one-half of the normal hourly rental rate plus operator's wages. In the event that the move-out is to a different location, payment will in no instance exceed the amount of the move-in. Move-in allowance shall not be made for equipment brought to the project for time and materials work which is subsequently retained on the project and utilized for completion of contract items, camp maintenance, or related work.

Time will be recorded to the nearest one-quarter hour for purposes of computing compensation to the Contractor for equipment utilized under these rates.

The equipment rates as determined above shall be full compensation for providing the required equipment and no additional compensation will be made for other costs such as, but not limited to, overhead and profit, fuels, lubricants, replacement parts or maintenance costs. Cost of repairs, both major and minor, as well as charges for mechanic's time utilized in servicing equipment to ready it for use prior to moving to the project and similar charges will not be allowed.

d.	Miscellaneous. No additional allowance will be made for general superintendence, the use of small tools, or other costs for which no specific allowance is herein provided.

e.	Work by a Subcontractor. The Contractor will receive a 5% markup on the total time and materials work defined in a through d above which is performed by an approved subcontractor or owner-operator. This markup will be for administrative expenses incurred in connection with the work. No percentage will be paid on work covered under bid items in the original Contract. No percentage over the amount covered above will be paid if the work is done by a lower tier subcontractor.

f.	Work by a Specialty Contractor. When the Engineer and the Contractor agree that a certain item or service cannot be satisfactorily performed by the forces of the Contractor or his subcontractors, such item or service may be performed by a specialist. Invoices for such item or service on the basis of the current market price thereof may be accepted without complete itemization of labor, material and equipment costs when such itemization is impracticable or not customary under the circumstances. The Contractor will be paid the invoice cost of the service plus 15%.

g.	Records. The Engineer will maintain a daily record of labor, equipment and materials utilized in the work and will present this record to the Contractor at the end of each day's work for verification and signature.

h.	Compensation. Payment for time and materials work will be made in the progress estimate following receipt of the verified daily records and all required supporting information from the Contractor. If, at any time, a unit price or lump sum basis of compensation can be agreed to for work being performed under this subsection, such compensation may be set forth in writing as a Change Order.

90-06 PROGRESS PAYMENTS. Progress payments will be made to the Contractor at least once each month as the work progresses. Progress payments will be made twice each month if the value of the estimate for the semi-monthly interval is equal to or in excess of $10,000. Such payments will be based on estimates of the value of the work performed and the materials delivered in accordance with Subsection 90-07.

Progress payments at 100% of the estimated value of the work accomplished, less all previous payments, shall be made to the Contractor, except as provided hereinafter:

At any time the Engineer finds that satisfactory progress is not being made he may retain an amount equal to 10% of the total amount earned from all subsequent progress payments. This retainage may be released at such time as the Engineer finds that satisfactory progress is being made.

90-07 PAYMENT FOR MATERIALS ON HAND. Payment may be made for materials meeting the applicable specifications and stockpiled on the project or stored in acceptable storage facilities off the limits of the project for future incorporation into the work.

Payment for materials on hand will not be made unless requested in writing by the Contractor. The Contractor's request must include a certification that the materials meet the applicable contract specifications, a summary of the items stockpiled, the quantity of each and the stockpile location(s), all of which shall be subject to verification by the Engineer prior to acceptance for payment.

Payment for materials purchased by the Contractor may be made to the extent of the delivered cost as evidenced by copies of invoices and freight bills, along with other information the Engineer may require. In no case shall payments for stockpiled materials exceed 85% of the contract amount for those items.

Materials produced by the Contractor may be included in the payment for materials on hand provided the materials meet the applicable specifications as evidenced by an acceptable number of process quality control test results. Quantities may be based on production statements submitted by the Contractor and approved by the Engineer. Payment for Contractor-produced materials shall be in the amounts determined by the Engineer not to exceed 50% of the applicable contract prices.

No payment for stockpiled materials will be made for perishable materials such as portland cement, emulsified asphalt, and others that could be rendered useless because of long storage periods. No payment for living plant materials will be made until planted.

Payment for materials on hand will not constitute final acceptance. It shall be the Contractor's responsibility to protect the material from damage or loss while in storage.

Stockpiled materials payments will be included in the progress estimate following receipt of the Contractor's request and all required documentation. Deductions will be made from stockpiled materials quantities appearing on the estimate as the materials are incorporated into the work.

Project materials shall be physically separated from the other materials stored at the storage location. Materials shall be clearly labeled with the project name and number. Store materials per the manufacturer's published recommendations. A copy of any such recommendations shall be provided to the Engineer.

Should storage conditions become unsatisfactory, any payments made for the materials will be classified as unearned. If the Contractor has not earned sufficient funds to cover the cost of a deduction on the next progress payment, a request for repayment will be sent to the Contractor. The Contractor agrees to repay the Department within 30 days from the date of a request to refund payment when the storage conditions have become unsatisfactory. Unsatisfactory storage conditions include, but are not limited to:

- Storage not in accordance with the manufacturer's recommendations;

- Commingling or storage of other materials where any element of doubt exists as to which materials belong in which lot;

- Unsatisfactory labeling of materials;

- Any liens filed on the materials for storage or transport, or by the supplier or manufacturer of the material;

- Change of the storage location without obtaining prior approval of the Engineer;

- Damage to all or part of the materials by fire, theft, or other peril.

Should labor, travel, or any other costs be incurred for inspection off the limits of the project, the Contractor shall reimburse the Department for these costs.

The Contractor releases and discharges the Department from any liability arising out of, or in any way related to, the payment for materials on hand and/or to the storage or transport of these materials. The Contractor is responsible for damages or delays which may relate to the storage or transport of the materials.

90-08 ACCEPTANCE AND FINAL PAYMENT. Final acceptance of the work shall be withheld until the Contractor furnishes all certificates, guarantees, releases, affidavits, etc., required by these Specifications or the Special Provisions.

When the project has been completed as provided in Subsection 50-17, the Engineer will prepare the final estimate of the quantities of the various classes of work performed. All prior progress estimates and payments shall be subject to correction in the final estimate and payment.

If the Contractor approves the estimate, or if he files no claim within 90 days of receiving the final estimate, the estimate shall be processed for final payment. Final payment shall consist of the entire sum found to be due after deducting all previous payments and all amounts to be retained or deducted under the provisions of the Contract.

The execution of the final estimate by the Contractor shall constitute acceptance by him of the total amount shown as payment in full for the amount due him under the Contract. This, however, does not exclude any claims timely filed in accordance with the terms of the Contract prior to the signing of the final estimate by the Contractor. Any timely filed claims must be listed as exceptions to the final estimate by the Contractor. Any claims listed as exceptions on the final estimate that have not been timely filed (as provided under the terms of the Contract) prior to the signing of the final estimate by the Contractor will be considered null and void. Any claims timely filed under the terms of the contract and not listed as exceptions on the final estimate shall be considered null and void and not subject to further consideration or legal action.

If the Contractor fails or declines to approve the final estimate within 90 days and files no claim, the Department will consider the estimate approved and process the estimate for final payment.

90-09 ELIMINATED ITEMS. When the Contractor is notified of the elimination of a minor contract item, he will be reimbursed for actual work done and all direct costs incurred, including mobilization of materials prior to said notification. In no case will any allowance be made for anticipated profits or overhead.

Should it become necessary to eliminate a major contract item, an equitable adjustment will be made and the Contract modified in writing accordingly.

SECTION 100

CONTRACTOR QUALITY CONTROL PROGRAM

100-01 GENERAL. The Contractor shall assure that all materials and completed construction conform to contract Plans, technical specifications and other requirements, whether manufactured by the Contractor, or procured from subcontractors or vendors. When required, the Contractor shall establish, provide, and maintain an effective Quality Control Program that details the methods and procedures that will be used. Although guidelines are established and certain minimum requirements are specified herein and elsewhere in the contract technical specifications, the Contractor shall assume full responsibility for accomplishing the stated purpose.

The intent of this section is to enable the Contractor to establish a necessary level of control that will:

- Adequately provide for the production of acceptable quality materials.

- Provide sufficient information to assure both the Contractor and the Engineer that the specification requirements can be met.

- Allow the Contractor as much latitude as possible to develop his or her own standard of control.

The Contractor shall be prepared to discuss and present, at the preconstruction conference, his/her understanding of the quality control requirements. The Contractor shall not begin any construction or production of materials to be incorporated into the completed work until the Quality Control Program has been reviewed by the Engineer. No partial payment will be made for materials subject to specific quality control requirements until the Quality Control Program has been reviewed.

The quality control requirements contained in this section and elsewhere in the contract technical specifications are in addition to and separate from the acceptance testing requirements. Acceptance testing requirements are the responsibility of the Engineer.

100-02 DESCRIPTION OF PROGRAM.

- General Description. The Contractor shall establish a Quality Control Program to perform inspection and testing of each item of work for which it is required by the technical specifications, including those performed by subcontractors. This Quality Control Program shall ensure conformance to applicable specifications and Plans with respect to materials, workmanship, construction, finish, and functional performance. The Quality Control Program shall be effective for control of all construction work performed under this Contract and shall specifically include surveillance and tests required by the technical specifications, in addition to other requirements of this section and any other activities deemed necessary by the Contractor to establish an effective level of quality control.

- Quality Control Program. The Contractor shall describe the Quality Control Program in a written document which shall be reviewed by the Engineer prior to the start of any production, construction, or off-site fabrication. The written Quality Control Program shall be submitted to the Engineer for review at least 5 calendar days before the preconstruction conference.

The Quality Control Program shall be organized to address, as a minimum, the following items:

a.	Quality control organization;

b.	Project progress schedule;

c.	Submittals schedule;

d.	Inspection requirements;

e.	Quality control testing plan;

f.	Documentation of quality control activities; and

g.	Requirements for corrective action when quality control and/or acceptance criteria are not met.

The Contractor is encouraged to add any additional elements to the Quality Control Program that he/she deems necessary to adequately control all production and/or construction processes required by this contract.

100-03 QUALITY CONTROL ORGANIZATION. The Contractor's Quality Control Program shall be implemented by the establishment of a separate quality control organization. An organizational chart shall be developed to show all quality control personnel and how these personnel integrate with other management/production and construction functions and personnel.

The organizational chart shall identify all quality control staff by name and function, and shall indicate the total staff required to implement all elements of the Quality Control Program, including inspection and testing for each item of work. If necessary, different technicians can be utilized for specific inspection and testing functions for different items of work. If an outside organization or independent testing laboratory is used for implementation of all or part of the Quality Control Program, the personnel assigned shall be subject to the qualification requirements of paragraph 100-03a and 100-03b. The organizational chart shall indicate which personnel are Contractor employees and which are provided by an outside organization.

The quality control organization shall consist of the following minimum personnel:

- Program Administrator. The Program Administrator shall be a full-time employee of the Contractor, or a consultant engaged by the Contractor. The Program Administrator shall have a minimum of 5 years of experience in airport and/or highway construction and shall have had prior quality control experience on a project of comparable size and scope as the contract.

Additional qualifications for the Program Administrator shall include at least one of the following requirements:

(1)	Professional engineer with 1 year of airport paving experience acceptable to the Engineer.

(2)	Engineer-in-training with 2 years of airport paving experience acceptable to the Engineer.

(3)	An individual with 3 years of highway and/or airport paving experience acceptable to the Engineer, with a Bachelor of Science Degree in Civil Engineering, Civil Engineering Technology or Construction.

(4)	Construction materials technician certified at Level III by the National Institute for Certification in Engineering Technologies (NICET).

(5)	Highway materials technician certified at Level III by NICET.

(6)	Highway construction technician certified at Level III by NICET.

(7)	A NICET certified engineering technician in Civil Engineering Technology with 5 years of highway and/or airport paving experience acceptable to the Engineer.

The Program Administrator shall have full authority to institute any and all actions necessary for the successful implementation of the Quality Control Program to ensure compliance with the contract Plans and technical specifications. The Program Administrator shall report directly to a responsible officer of the construction firm. The Program Administrator may supervise the Quality Control Program on more than one project provided that person can be at the job site within 2 hours after being notified of a problem.

b.	Quality Control Technicians. A sufficient number of quality control technicians necessary to adequately implement the Quality Control Program shall be provided. These personnel shall be either engineers, engineering technicians, or experienced craftsman with qualifications in the appropriate field equivalent to NICET Level II or higher construction materials technician or highway construction technician and shall have a minimum of 2 years of experience in their area of expertise.

The quality control technicians shall report directly to the Program Administrator and shall perform the following functions:

- Inspection of all materials, construction, plant, and equipment for conformance to the technical specifications, and as required by Section 100-05.

- Performance of all quality control tests as required by the technical specifications and Section 100-06.

Certification at an equivalent level, by a state or nationally recognized organization will be acceptable in lieu of NICET certification.

c.	Staffing Levels. The Contractor shall provide sufficient qualified quality control personnel to monitor each work activity at all times. Where material is being produced in a plant for incorporation into the work, separate plant and field technicians shall be provided at each plant and field placement location. The scheduling and coordinating of all inspection and testing must match the type and pace of work activity. The Quality Control Program shall state where different technicians will be required for different work elements.

100-04 SUBMITTALS SCHEDULE. The Contractor shall submit a detailed listing of all submittals (e.g., mix designs, material certifications) and shop drawings required by the technical specifications. The listing can be developed in a spreadsheet format and shall include:

a.	Specification item number;

b.	Item description;

c.	Description of submittal;

d.	Specification paragraph requiring submittal; and

e.	Scheduled date of submittal.

100-05 INSPECTION REQUIREMENTS. Quality control inspection functions shall be organized to provide inspections for all definable features of work, as detailed below. All inspections shall be documented by the Contractor as specified by Section 100-07.

Inspections shall be performed daily to ensure continuing compliance with contract requirements until completion of the particular feature of work. These shall include the following minimum requirements:

- During plant operation for material production, quality control test results and periodic inspections shall be utilized to ensure the quality of aggregates and other mix components, and to adjust and control mix proportioning to meet the approved mix design and other requirements of the technical specifications. All equipment utilized in proportioning and mixing shall be inspected to ensure its proper operating condition. The Quality Control Program shall detail how these and other quality control functions will be accomplished and utilized.

- During field operations, quality control test results and periodic inspections shall be utilized to ensure the quality of all materials and workmanship. All equipment utilized in placing, finishing, and compacting shall be inspected to ensure its proper operating condition and to ensure that all such operations are in conformance to the technical specifications and are within the plan dimensions, lines, grades, and tolerances specified. The Program shall document how these and other quality control functions will be accomplished and utilized.

100-06 QUALITY CONTROL TESTING PLAN. As a part of the overall Quality Control Program, the Contractor shall implement a quality control testing plan, as required by the technical specifications. The testing plan shall include the minimum tests and test frequencies required by the technical specification Item, as well as any additional quality control tests that the Contractor deems necessary to adequately control production and/or construction processes.

The testing plan can be developed in a spreadsheet fashion and shall, as a minimum, include the following:

a.	Specification item number (e.g., P-401);

b.	Item description (e.g., Plant Mix Bituminous Pavements);

c.	Test type (e.g., gradation, grade, asphalt content);

d.	Test standard (e.g., ASTM or AASHTO test number, as applicable);

e.	Test frequency (e.g., as required by technical specifications or minimum frequency when requirements are not stated);

f.	Responsibility (e.g., plant technician); and

g.	Control requirements (e.g., target, permissible deviations).

The testing plan shall contain a statistically-based procedure of random sampling for acquiring test samples in accordance with ASTM D 3665. The Engineer shall be provided the opportunity to witness quality control sampling and testing.

All quality control test results shall be documented by the Contractor as required by Section 100-07.

100-07 DOCUMENTATION. The Contractor shall maintain current quality control records of all inspections and tests performed. These records shall include factual evidence that the required inspections or tests have been performed, including type and number of inspections or tests involved; results of inspections or tests; nature of defects, deviations, causes for rejection, etc.; proposed remedial action; and corrective actions taken.

These records must cover both conforming and defective or deficient features, and must include a statement that all supplies and materials incorporated in the work are in full compliance with the terms of the contract. Legible copies of these records shall be furnished to the Engineer daily. The records shall cover all work placed subsequent to the previously furnished records and shall be verified and signed by the Contractor's Program Administrator.

Specific Contractor quality control records required for the contract shall include, but are not necessarily limited to, the following records:

a.	Daily Inspection Reports. Each Contractor quality control technician shall maintain a daily log of all inspections performed for both Contractor and subcontractor operations on a form acceptable to the Engineer. These technician's daily reports shall provide factual evidence that continuous quality control inspections have been performed and shall, as a minimum, include the following:

(1)	Technical specification item number and description;

(2)	Compliance with approved submittals;

(3)	Proper storage of materials and equipment;

(4)	Proper operation of all equipment;

(5)	Adherence to Plans and technical specifications;

(6)	Review of quality control tests; and

(7)	Safety inspection.

The daily inspection reports shall identify inspections conducted, results of inspections, location and nature of defects found, causes for rejection, and remedial or corrective actions taken or proposed.

The daily inspection reports shall be signed by the responsible quality control technician and the Program Administrator. The Engineer shall be provided at least one copy of each daily inspection report on the work day following the day of record.

b.	Daily Test Reports. The Contractor shall be responsible for establishing a system which will record all quality control test results. Daily test reports shall document the following information:

(1)	Technical specification item number and description;

(2)	Test designation;

(3)	Location;

(4)	Date of test;

(5)	Control requirements;

(6)	Test results;

(7)	Causes for rejection;

(8)	Recommended remedial actions; and

(9)	Retests.

Test results from each day's work period shall be submitted to the Engineer prior to the start of the next day's work period. When required by the technical specifications, the Contractor shall maintain statistical quality control charts. The daily test reports shall be signed by the responsible quality control technician and the Program Administrator.

100-08 CORRECTIVE ACTION REQUIREMENTS. The Quality Control Program shall indicate the appropriate action to be taken when a process is deemed, or believed, to be out of control (out of tolerance) and detail what action will be taken to bring the process into control. The requirements for corrective action shall include both general requirements for operation of the Quality Control Program as a whole, and for individual items of work contained in the technical specifications.

The Quality Control Program shall detail how the results of quality control inspections and tests will be used for determining the need for corrective action and shall contain clear sets of rules to gauge when a process is out of control and the type of correction to be taken to regain process control.

When applicable or required by the technical specifications, the Contractor shall establish and utilize statistical quality control charts for individual quality control tests. The requirements for corrective action shall be linked to the control charts.

100-09 SURVEILLANCE BY THE ENGINEER. All items of material and equipment shall be subject to surveillance by the Engineer at the point of production, manufacture or shipment to determine if the Contractor, producer, manufacturer or shipper maintains an adequate quality control system in conformance with the requirements detailed herein and the applicable technical specifications and Plans. In addition, all items of materials, equipment and work in place shall be subject to surveillance by the Engineer at the site for the same purpose.

Surveillance by the Engineer does not relieve the Contractor of performing quality control inspections of either on-site or off-site Contractor's or subcontractor's work.

100-10 NONCOMPLIANCE.

- The Engineer will notify the Contractor of any noncompliance with any of the foregoing requirements. The Contractor shall, after receipt of such notice, immediately take corrective action. Any notice, when delivered by the Engineer or his/her authorized representative to the Contractor or his/her authorized representative at the site of the work, shall be considered sufficient notice.

- In cases where quality control activities do not comply with either the Contractor's Quality Control Program or the contract provisions, or where the Contractor fails to properly operate and maintain an effective Quality Control Program, as determined by the Engineer, the Engineer may:

- Order the Contractor to replace ineffective or unqualified quality control personnel or subcontractors.

- Order the Contractor to stop operations until appropriate corrective action is taken.

SECTION 110

METHOD OF ESTIMATING

PERCENTAGE OF MATERIAL WITHIN SPECIFICATION LIMITS (PWL)

110-01 GENERAL. When the Specifications provide for acceptance of material based on the method of estimating percentage of material within specification limits (PWL), the PWL will be determined in accordance with this section. All test results for a lot will be analyzed statistically to determine the total estimated percent of the lot that is within specification limits. The PWL is computed using the sample average (X) and sample standard deviation (Sn) of the specified number (n) of sublots for the lot and the specification tolerance limits, L for lower and U for upper, for the particular acceptance parameter. From these values, the respective Quality index(s), QL for Lower Quality Index and/or QU for Upper Quality Index, is computed and the PWL for the lot for the specified n is determined from Table 1. Analysis of test results will be based on an Acceptable Quality Level (AQL) of 95.0% and a contractor's risk of 5.0% unless otherwise specified. AQL may be viewed as the lowest percent within the specification limits of a material that is acceptable as a process average and receive 100% pay. The Contractor's risk is the probability that when the Contractor is producing material at exactly the AQL, the materials will receive less than 1.00 pay factor.

There is some degree of uncertainty (risk) in the measurement for acceptance because only a small fraction of production material (the population) is sampled and tested. This uncertainty exists because all portions of the production material have the same probability to be randomly sampled. The Contractor's risk is the probability that material produced at the acceptable quality level is rejected or subjected to a pay adjustment. The Department’s risk is the probability that material produced at the rejectable quality level is accepted.

IT IS THE INTENT OF THIS SECTION TO INFORM THE CONTRACTOR THAT, IN ORDER TO CONSISTENTLY OFFSET THE CONTRACTOR’S RISK FOR MATERIAL EVALUATED, PRODUCTION QUALITY (USING POPULATION AVERAGE AND POPULATION STANDARD DEVIATION) MUST BE MAINTAINED AT THE ACCEPTABLE QUALITY SPECIFIED OR HIGHER. IN ALL CASES, IT IS THE RESPONSIBILITY OF THE CONTRACTOR TO PRODUCE AT QUALITY LEVELS THAT WILL MEET THE SPECIFIED ACCEPTANCE CRITERIA WHEN SAMPLED AND TESTED AT THE FREQUENCIES SPECIFIED.

110-02 METHOD FOR COMPUTING PWL. The computational sequence for computing PWL is as follows:

a.	Divide the lot into n sublots in accordance with the acceptance requirements of the specification.

b.	Locate the random sampling position within the sublot in accordance with the requirements of the specification.

c.	Make a measurement at each location, or take a test portion and make the measurement on the test portion in accordance with the testing requirements of the specification.

d.	Find the sample average (X) for all sublot values within the lot by using the following formula:

X = (x1 + x2 + x3 + . . .xn) / n

Where:		X	= Sample average of all sublot values within a lot

x1, x2	= Individual sublot values

n	= Number of sublots

e.	Find the sample standard deviation (Sn) by use of the following formula:

Sn = [(d12 + d22 + d32 + . . .dn2)/(n-1)]1/2

Where:	Sn 	= Sample standard deviation of the number of sublot values in the set

d1, d2, …= Deviations of the individual sublot values x1, x2, … from the average value X

that is: d1 = (x1 - X), d2 = (x2 - X) … dn = (xn - X)

n 	= Number of sublots

If the computed sample standard deviation (Sn) is <0.020, and the average (X) is between the Upper Specification Limit (U) and Lower Specification Limit (L), set the Upper Quality Index (QU) and Lower Quality Index (QL) equal to 10 in steps f. and g. respectively. If the computed standard deviation (Sn) is <0.020 and the average (X) is outside the U or L, then use 0.020 for the standard deviation.

f.	For single sided specification limits (i.e., L only), compute the Lower Quality Index QL by use of the following formula:

QL = (X - L) / Sn

Where:	L = specification lower tolerance limit

Estimate the percentage of material within limits (PWL) by entering Table 1 with QL, using the column appropriate to the total number (n) of measurements. If the value of QL falls between values shown on the table, use the next higher value of PWL. QL is rounded to the nearest hundredth.

g.	For double sided specification limits (i.e. L and U), compute the Quality Indexes QL and QU by use of the following formulas:

QL = (X - L) / Sn 	and 	QU = (U - X) / Sn

Where:	L and U = specification lower and upper tolerance limits

QL and QU are rounded to the nearest hundredth.

Estimate the percentage of material between the lower (L) and upper (U) tolerance limits (PWL) by entering Table 1 separately with QL and QU, using the column appropriate to the total number (n) of measurements, and determining the percent of material above PL and percent of material below PU for each tolerance limit. If the values of QL fall between values shown on the table, use the next higher value of PL or PU. Determine the PWL by use of the following formula:

PWL = (PU + PL) - 100

Where:

PL = percent within lower specification limit

PU = percent within upper specification limit

EXAMPLE OF PWL CALCULATION

(This is an example PWL determination of five random samples from Lot 1. Cores for mat density are used for this example. Follow the same basic procedure for all acceptance criteria requiring a PWL calculation.)

Project:	Example Project

Test Item:	Item 401a,  Lot 1

- Densities of five random core samples from Lot 1  (n = 5).

x1  (D-1)  =  93

x2  (D-2)  =  94

x3  (D-3)  =  92

x4  (D-4)  =  95

x5  (D-5)  =  95

- Calculate average density (X) for Lot 1.

X = (x1 + x2 + x3 + x4 + x5)/n

X = (93 + 94 + 92 + 95 + 95)/5

X = 93.8 percent density

- Calculate the standard deviation (Sn) for Lot 1.

Sn = [({x1-X}2+{x2-X}2+{x3-X}2+{x4-X}2+{x5-X}2)/n-1)]1/2

S5 = [({93-93.8}2+{94-93.8}2+{92-93.8}2+{95-93.8}2+{95-93.8}2)/5-1]1/2

S5 = [(0.64+0.04+3.24+1.44+1.44)/4]1/2

S5 = [1.70]1/2

S5 = 1.30

- Calculate the lower Quality Index (QL) for Lot 1.  (L = Lower specification limit.)

QL = (X - L)/Sn

QL = (93.8-92)/1.30

QL = 1.38

- Calculate the upper Quality Index (QU) for Lot 1.  (U = Upper specification limit.)

QU = (U – X)/Sn

QU = (98-93.8)/1.30

QU = 3.23

- Determine the percent within lower specification limits (PL) from Table 1.

For n = 5 and QL = 1.38,  PL = 94

- Determine the percent within upper specification limits (PU) from Table 1.

For n = 5 and QU = 3.23,  PU = 100

- Calculate mat density PWL for LOT 1.

PWL = (PL + PU) –100

PWL = (94 + 100) – 100

PWL = 94

# TABLE 1.    Table for Estimating Percent of Lot Within Limits (PWL)

Positive Values of QU or QL

| PU or PL | n = 3 | n = 4 | n = 5 | n = 6 | n = 7 |
| --- | --- | --- | --- | --- | --- |
| 100 | 1.16-50.0 | 1.48-50.0 | 1.68-50.0 | 1.81-50.0 | 1.90-50.0 |
| 99 | - | 1.45-1.47 | 1.61-1.67 | 1.71-1.80 | 1.77-1.89 |
| 98 | 1.15 | 1.42-1.44 | 1.55-1.60 | 1.63-1.70 | 1.68-1.76 |
| 97 | - | 1.39-1.41 | 1.50-1.54 | 1.56-1.62 | 1.60-1.67 |
| 96 | 1.14 | 1.36-1.38 | 1.45-1.49 | 1.50-1.55 | 1.53-1.59 |
| 95 | - | 1.33-1.35 | 1.40-1.44 | 1.44-1.49 | 1.47-1.52 |
| 94 | 1.13 | 1.30-1.32 | 1.36-1.39 | 1.39-1.43 | 1.41-1.46 |
| 93 | - | 1.27-1.29 | 1.32-1.35 | 1.34-1.38 | 1.36-1.40 |
| 92 | 1.12 | 1.24-1.26 | 1.28-1.31 | 1.30-1.33 | 1.31-1.35 |
| 91 | 1.11 | 1.21-1.23 | 1.24-1.27 | 1.25-1.29 | 1.26-1.30 |
| 90 | 1.10 | 1.18-1.20 | 1.20-1.23 | 1.21-1.24 | 1.21-1.25 |
| 89 | 1.08-1.09 | 1.15-1.17 | 1.16-1.19 | 1.17-1.20 | 1.17-1.20 |
| 88 | 1.07 | 1.12-1.14 | 1.13-1.15 | 1.13-1.16 | 1.13-1.16 |
| 87 | 1.05-1.06 | 1.09-1.11 | 1.09-1.12 | 1.09-1.12 | 1.09-1.12 |
| 86 | 1.04 | 1.06-1.08 | 1.06-1.08 | 1.05-1.08 | 1.05-1.08 |
| 85 | 1.02-1.03 | 1.03-1.05 | 1.02-1.05 | 1.02-1.04 | 1.01-1.04 |
| 84 | 1.01 | 1.00-1.02 | 0.99-1.01 | 0.98-1.01 | 0.98-1.00 |
| 83 | 0.98-1.00 | 0.97-0.99 | 0.96-0.98 | 0.95-0.97 | 0.94-0.97 |
| 82 | 0.97 | 0.94-0.96 | 0.92-0.95 | 0.91-0.94 | 0.91-0.93 |
| 81 | 0.94-0.96 | 0.91-0.93 | 0.89-0.91 | 0.88-0.90 | 0.87-0.90 |
| 80 | 0.92-0.93 | 0.88-0.90 | 0.86-0.88 | 0.85-0.87 | 0.84-0.86 |
| 79 | 0.90-0.91 | 0.85-0.87 | 0.83-0.85 | 0.81-0.84 | 0.81-0.83 |
| 78 | 0.88-0.89 | 0.82-0.84 | 0.79-0.82 | 0.78-0.80 | 0.77-0.80 |
| 77 | 0.85-0.87 | 0.79-0.81 | 0.76-0.78 | 0.75-0.77 | 0.74-0.76 |
| 76 | 0.83-0.84 | 0.76-0.78 | 0.73-0.75 | 0.72-0.74 | 0.71-0.73 |
| 75 | 0.80-0.82 | 0.73-0.75 | 0.70-0.72 | 0.69-0.71 | 0.68-0.70 |
| 74 | 0.77-0.79 | 0.70-0.72 | 0.67-0.69 | 0.66-0.68 | 0.65-0.67 |
| 73 | 0.75-0.76 | 0.67-0.69 | 0.64-0.66 | 0.63-0.65 | 0.62-0.64 |
| 72 | 0.72-0.74 | 0.64-0.66 | 0.61-0.63 | 0.60-0.62 | 0.59-0.61 |
| 71 | 0.69-0.71 | 0.61-0.63 | 0.58-0.60 | 0.57-0.59 | 0.56-0.58 |
| 70 | 0.66-0.68 | 0.58-0.60 | 0.55-0.57 | 0.54-0.56 | 0.53-0.55 |
| 69 | 0.63-0.65 | 0.55-0.57 | 0.52-0.54 | 0.51-0.53 | 0.50-0.52 |
| 68 | 0.60-0.62 | 0.52-0.54 | 0.48-0.51 | 0.48-0.50 | 0.47-0.49 |
| 67 | 0.57-0.59 | 0.49-0.51 | 0.46-0.47 | 0.45-0.47 | 0.45-0.46 |
| 66 | 0.53-0.56 | 0.46-0.48 | 0.44-0.45 | 0.42-0.44 | 0.42-0.44 |
| 65 | 0.50-0.52 | 0.43-0.45 | 0.41-0.43 | 0.40-0.41 | 0.39-0.41 |
| 64 | 0.47-0.49 | 0.40-0.42 | 0.38-0.40 | 0.37-0.39 | 0.36-0.38 |
| 63 | 0.44-0.46 | 0.37-0.39 | 0.35-0.37 | 0.34-0.36 | 0.33-0.35 |
| 62 | 0.40-0.43 | 0.34-0.36 | 0.32-0.34 | 0.31-0.33 | 0.31-0.32 |
| 61 | 0.37-0.39 | 0.31-0.33 | 0.29-0.31 | 0.28-0.30 | 0.28-0.30 |
| 60 | 0.33-0.36 | 0.28-0.30 | 0.26-0.28 | 0.26-0.27 | 0.25-0.27 |
| 59 | 0.30-0.32 | 0.25-0.27 | 0.24-0.25 | 0.23-0.25 | 0.22-0.24 |
| 58 | 0.26-0.29 | 0.22-0.24 | 0.21-0.23 | 0.20-0.22 | 0.20-0.21 |
| 57 | 0.23-0.25 | 0.19-0.21 | 0.18-0.20 | 0.17-0.19 | 0.17-0.19 |
| 56 | 0.19-0.22 | 0.16-0.18 | 0.15-0.17 | 0.15-0.16 | 0.14-0.16 |
| 55 | 0.15-0.18 | 0.13-0.15 | 0.12-0.14 | 0.12-0.14 | 0.12-0.13 |
| 54 | 0.12-0.14 | 0.10-0.12 | 0.09-0.11 | 0.09-0.11 | 0.09-0.11 |
| 53 | 0.08-0.11 | 0.07-0.09 | 0.07-0.08 | 0.06-0.08 | 0.06-0.08 |
| 52 | 0.05-0.07 | 0.04-0.06 | 0.04-0.06 | 0.04-0.05 | 0.04-0.05 |
| 51 | 0.01-0.04 | 0.01-0.03 | 0.01-0.03 | 0.01-0.03 | 0.01-0.03 |
| 50 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 |

| PU or PL | n = 8 | n = 9 | n = 10 to 11 | n = 12 to 14 | n = 15 to 18 |
| --- | --- | --- | --- | --- | --- |
| 100 | 1.96-50.0 | 2.01-50.0 | 2.05-50.0 | 2.10-50.0 | 2.15-50.0 |
| 99 | 1.82-1.95 | 1.85-2.00 | 1.87-2.04 | 1.92-2.09 | 1.94-2.14 |
| 98 | 1.71-1.81 | 1.73-1.84 | 1.75-1.86 | 1.78-1.91 | 1.80-1.93 |
| 97 | 1.62-1.70 | 1.64-1.72 | 1.66-1.74 | 1.68-1.77 | 1.69-1.79 |
| 96 | 1.55-1.61 | 1.56-1.63 | 1.57-1.65 | 1.59-1.67 | 1.60-1.68 |
| 95 | 1.48-1.54 | 1.49-1.55 | 1.50-1.56 | 1.51-1.58 | 1.52-1.59 |
| 94 | 1.42-1.47 | 1.43-1.48 | 1.44-1.49 | 1.45-1.50 | 1.45-1.51 |
| 93 | 1.37-1.41 | 1.37-1.42 | 1.38-1.43 | 1.38-1.44 | 1.39-1.44 |
| 92 | 1.31-1.36 | 1.32-1.36 | 1.32-1.37 | 1.33-1.37 | 1.33-1.38 |
| 91 | 1.26-1.30 | 1.27-1.31 | 1.27-1.31 | 1.27-1.32 | 1.28-1.32 |
| 90 | 1.22-1.25 | 1.22-1.26 | 1.22-1.26 | 1.22-1.26 | 1.23-1.27 |
| 89 | 1.17-1.21 | 1.17-1.21 | 1.18-1.21 | 1.18-1.21 | 1.18-1.22 |
| 88 | 1.13-1.16 | 1.13-1.16 | 1.13-1.17 | 1.13-1.17 | 1.13-1.17 |
| 87 | 1.09-1.12 | 1.09-1.12 | 1.09-1.12 | 1.09-1.12 | 1.09-1.12 |
| 86 | 1.05-1.08 | 1.05-1.08 | 1.05-1.08 | 1.05-1.08 | 1.05-1.08 |
| 85 | 1.01-1.04 | 1.01-1.04 | 1.01-1.04 | 1.01-1.04 | 1.01-1.04 |
| 84 | 0.97-1.00 | 0.97-1.00 | 0.97-1.00 | 0.97-1.00 | 0.97-1.00 |
| 83 | 0.94-0.96 | 0.94-0.96 | 0.93-0.96 | 0.93-0.96 | 0.93-0.96 |
| 82 | 0.90-0.93 | 0.90-0.93 | 0.90-0.92 | 0.90-0.92 | 0.89-0.92 |
| 81 | 0.87-0.89 | 0.87-0.89 | 0.86-0.89 | 0.86-0.89 | 0.86-0.88 |
| 80 | 0.83-0.86 | 0.83-0.86 | 0.83-0.85 | 0.83-0.85 | 0.82-0.85 |
| 79 | 0.80-0.82 | 0.80-0.82 | 0.80-0.82 | 0.79-0.82 | 0.79-0.81 |
| 78 | 0.77-0.79 | 0.77-0.79 | 0.76-0.79 | 0.76-0.78 | 0.76-0.78 |
| 77 | 0.74-0.76 | 0.73-0.76 | 0.73-0.75 | 0.73-0.75 | 0.72-0.75 |
| 76 | 0.71-0.73 | 0.70-0.72 | 0.70-0.72 | 0.70-0.72 | 0.69-0.71 |
| 75 | 0.67-0.70 | 0.67-0.69 | 0.67-0.69 | 0.67-0.69 | 0.66-0.68 |
| 74 | 0.64-0.66 | 0.64-0.66 | 0.64-0.66 | 0.63-0.66 | 0.63-0.65 |
| 73 | 0.61-0.63 | 0.61-0.63 | 0.61-0.63 | 0.60-0.62 | 0.60-0.62 |
| 72 | 0.58-0.60 | 0.58-0.60 | 0.58-0.60 | 0.58-0.59 | 0.57-0.59 |
| 71 | 0.56-0.57 | 0.55-0.57 | 0.55-0.57 | 0.55-0.57 | 0.54-0.56 |
| 70 | 0.53-0.55 | 0.52-0.54 | 0.52-0.54 | 0.52-0.54 | 0.51-0.53 |
| 69 | 0.50-0.52 | 0.49-0.51 | 0.49-0.51 | 0.49-0.51 | 0.49-0.50 |
| 68 | 0.47-0.49 | 0.47-0.48 | 0.46-0.48 | 0.46-0.48 | 0.46-0.48 |
| 67 | 0.44-0.46 | 0.44-0.46 | 0.44-0.45 | 0.43-0.45 | 0.43-0.45 |
| 66 | 0.41-0.43 | 0.41-0.43 | 0.41-0.43 | 0.41-0.42 | 0.40-0.42 |
| 65 | 0.39-0.40 | 0.38-0.40 | 0.38-0.40 | 0.38-0.40 | 0.38-0.39 |
| 64 | 0.36-0.38 | 0.36-0.37 | 0.35-0.37 | 0.35-0.37 | 0.35-0.37 |
| 63 | 0.33-0.35 | 0.33-0.35 | 0.33-0.34 | 0.32-0.34 | 0.32-0.34 |
| 62 | 0.30-0.32 | 0.30-0.32 | 0.30-0.32 | 0.30-0.31 | 0.30-0.31 |
| 61 | 0.28-0.29 | 0.27-0.29 | 0.27-0.29 | 0.27-0.29 | 0.27-0.29 |
| 60 | 0.25-0.27 | 0.25-0.26 | 0.25-0.26 | 0.24-0.26 | 0.24-0.26 |
| 59 | 0.22-0.24 | 0.22-0.24 | 0.22-0.24 | 0.22-0.23 | 0.22-0.23 |
| 58 | 0.20-0.21 | 0.19-0.21 | 0.19-0.21 | 0.19-0.21 | 0.19-0.21 |
| 57 | 0.17-0.19 | 0.17-0.18 | 0.17-0.18 | 0.17-0.18 | 0.16-0.18 |
| 56 | 0.14-0.16 | 0.14-0.16 | 0.14-0.16 | 0.14-0.16 | 0.14-0.15 |
| 55 | 0.12-0.13 | 0.11-0.13 | 0.11-0.13 | 0.11-0.13 | 0.11-0.13 |
| 54 | 0.09-0.11 | 0.09-0.10 | 0.09-0.10 | 0.09-0.10 | 0.09-0.10 |
| 53 | 0.06-0.08 | 0.06-0.08 | 0.06-0.08 | 0.06-0.08 | 0.06-0.08 |
| 52 | 0.04-0.05 | 0.04-0.05 | 0.04-0.05 | 0.04-0.05 | 0.04-0.05 |
| 51 | 0.01-0.03 | 0.01-0.03 | 0.01-0.03 | 0.01-0.03 | 0.01-0.03 |
| 50 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 |

PART II – EARTHWORK

ITEM P-151	CLEARING AND GRUBBING

DESCRIPTION

151-1.1 This item shall consist of clearing or clearing and grubbing, including the disposal of materials, for all areas within the limits designated on the Plans or as required by the Engineer.

Clearing shall consist of the cutting and removal of all trees, stumps, brush, logs, hedges, the removal of fences and other loose or projecting material from the designated areas. The grubbing of stumps and roots will not be required.

Clearing and grubbing shall consist of clearing the surface of the ground of the designated areas of all trees, stumps, down timber, logs, snags, brush, undergrowth, hedges, heavy growth of grass or weeds, fences, structures, debris, and rubbish of any nature, natural obstructions or such material which in the opinion of the Engineer is unsuitable for the foundation of strips, pavements, or other required structures, including the grubbing of stumps, roots, matted roots, foundations, and the disposal from the project of all spoil materials resulting from clearing and grubbing by burning or otherwise.

CONSTRUCTION METHODS

151-2.1 GENERAL. The areas denoted on the Plans to be cleared or cleared and grubbed shall be staked or otherwise marked on the ground at the direction of the Engineer. The clearing and grubbing shall be done far enough ahead of the earthwork operation to permit cross-sectioning prior to excavation or embankment. Mechanical brush cutting equipment may be used for clearing. Dozers or other mechanical equipment not specifically designed for brush cutting may not be used.

Debris from mechanical brush cutting equipment less than 4 feet long by 4 inches in diameter may remain in place outside of Runway and Taxiway Safety Area surfaces except as specified in areas to be embanked. All other spoil materials generated by clearing or by clearing and grubbing shall be disposed of by burning, when permitted by local laws, or by removal to approved disposal areas. When burning of material is permitted, it shall be burned under the constant care of competent watchmen so that the surrounding vegetation and other adjacent property will not be jeopardized. Burning shall be done in accordance with all applicable laws, ordinances, and regulations. Before starting any burning operations, the Contractor shall notify the agency having jurisdiction.

As far as practicable, waste concrete and masonry shall be placed on slopes of embankments or channels. When embankments are constructed of such material, this material shall be placed in accordance with requirements for formation of embankments. Any broken concrete or masonry which cannot be used in construction, and all other materials not considered suitable for use elsewhere, shall be disposed of by the Contractor. In no case shall any discarded materials be left in windrows or piles adjacent to or within the airport limits. The manner and location of disposal of materials shall be subject to the approval of the Engineer and shall not create an unsightly or objectionable view. When the Contractor is required to locate a disposal area outside the airport property limits at his/her own expense, he shall obtain and file with the Engineer, permission in writing from the property owner for the use of private property for this purpose.

If the Plans or the Specifications require the saving of merchantable timber, the Contractor shall trim the limbs and tops from designated trees, saw them into suitable lengths, and make the material available for removal by others.

Any blasting necessary shall be done at the Contractor's responsibility, and the utmost care shall be taken not to endanger life or property.

The removal of existing structure and utilities required to permit orderly progress of work shall be accomplished by local agencies, unless otherwise shown on the Plans. Whenever a telephone or telegraph pole, pipeline, conduit, sewer, roadway, or other utility is encountered and must be removed or relocated the Contractor shall advise the Engineer who will notify the proper local authority or owner and attempt to secure prompt action.

151-2.2 CLEARING. The Contractor shall clear the staked or indicated area of all objectionable materials. Trees unavoidably falling outside the specified limits must be cut up, removed, and disposed of in a satisfactory manner. In order to minimize damage to trees that are to be left standing, trees shall be felled toward the center of area being cleared. The Contractor shall preserve and protect from injury all trees not to be removed. The trees, stumps, and brush shall be cut to a height of not more than 12 inches above the ground. The grubbing of stumps and roots will not be required.

Fences shall be removed and disposed of when directed by the Engineer. Fence wire shall be neatly rolled and the wire and posts stored on the airport if they are to be used again, or stored at a designated location if the fence is to remain the property of a local owner.

151-2.3 CLEARING AND GRUBBING. In areas designated to be cleared and grubbed, all stumps, roots, buried logs, brush, grass, and other unsatisfactory materials shall be removed, except where embankments exceeding 3.5 feet in depth are to be made outside of paved areas. In cases where such depth of embankments is to be made, all unsatisfactory materials shall be removed, but sound trees, stumps, and brush can be cut off within 6 inches above the ground and allowed to remain. Tap roots and other projections over 1.5 inches in diameter shall be grubbed out to a depth of at least 18 inches below the finished subgrade or slope elevation.

Any buildings and miscellaneous structures that are shown on the Plans to be removed shall be demolished or removed, and all materials therefrom shall be disposed of either by burning or otherwise removed from the site. The remaining or existing foundations, wells, cesspools, and all like structures shall be destroyed by breaking down the materials of which the foundations, wells, cesspools, etc., are built to a depth at least 2 feet below the existing surrounding ground. Any broken concrete, blocks, or other objectionable material which cannot be used in backfill shall be removed and disposed of. The holes or openings shall be backfilled with acceptable material and properly compacted.

All holes remaining after the grubbing operation in embankment areas shall have the sides broken down to flatten out the slopes, and shall be filled with acceptable material, moistened and properly compacted in layers to the density required in Item P-152. The same construction procedure shall be applied to all holes remaining after grubbing in excavation areas where the depth of holes exceeds the depth of the proposed excavation.

METHOD OF MEASUREMENT

151-3.1 The quantities of clearing or clearing and grubbing as shown by the limits on the Plans or as ordered by the Engineer will be the number of acres of land specifically cleared or cleared and grubbed.

Islands of existing cleared areas, such as lakes, ponds, existing stream beds, and roads and trails within the clearing limits of more than 60 square yards will not be included as pay areas.

BASIS OF PAYMENT

151-4.1 The accepted quantities of clearing or clearing and grubbing will be paid for at the contract unit price, per unit of measurement, for each of the pay items listed below that are shown in the bid schedule.

Payment will be made under:

Item P-151a	Clearing - per acre

Item P-151b	Clearing - lump sum

Item P-151c	Clearing & Grubbing - per acre

Item P-151d	Clearing & Grubbing - lump sum

ITEM P-152	EXCAVATION AND EMBANKMENT

DESCRIPTION

152-1.1 This item covers excavation, embankment , disposal, placement, and compaction of all materials within the limits of the work required to construct Runway Safety Areas, runways, taxiways, aprons, and intermediate as well as other areas for drainage, building construction, parking, or other purposes in accordance with these specifications and in conformance to the dimensions and typical section shown on the Plans.

152-1.2 CLASSIFICATION. All material excavated shall be classified as defined below:

a.	Unclassified Excavation. Unclassified excavation shall consist of the excavation and disposal of all material, regardless of its nature, which is not otherwise classified and paid for under the following items.

b.	Rock Excavation. Rock excavation shall include all solid rock in ledges, in bedded deposits, in unstratified masses, and conglomerate deposits which are so firmly cemented they cannot be removed without blasting or using rippers. All boulders containing a volume of more than 0.5 cubic yard will be classified as rock excavation.

c.	Muck Excavation. Muck excavation shall consist of the removal and disposal of deposits of mixtures of soils and organic matter not suitable for foundation material. Muck shall include materials which will decay or produce subsidence in the embankment. It may be made up of decaying stumps, roots, logs, humus, or other material not satisfactory for incorporation into the embankment.

d.	Drainage Excavation. Drainage excavation shall consist of all excavation made for the primary purpose of drainage and includes drainage ditches, such as intercepting, inlet or outlet; temporary levee construction; or any other type as shown on the Plans.

e.	Borrow Excavation. Borrow excavation shall consist of approved material required for the construction of embankment or for other portions of the work in excess of the quantity of usable material available from required excavations. Borrow material shall be obtained from areas within the limits of the airport property but outside the normal limits of necessary grading, or from areas outside the airport.

f.	Embankment. Suitable material obtained from areas of excavation placed as shown on the Plans or as directed by the Engineer. Suitable material may include sand, silt, and other inorganic material acceptable to the Engineer.

g.	Borrow Embankment. Suitable material obtained from on or off of airport property placed as shown on the Plans or as directed by the Engineer. Suitable material may include sand, silt, and other inorganic material acceptable to the Engineer.

152-1.3 Unsuitable Excavation. Any material containing vegetable or organic matter, such as muck, peat, organic silt, or sod shall be considered unsuitable for use in embankment construction. Material, when approved by the Engineer, may be used on the embankment slope.

CONSTRUCTION METHODS

152-2.1 General. Before beginning excavation, grading, and embankment operations in any area, the area shall be cleared and grubbed in accordance with Item P-151 where shown on the Plans or as specified, and surveyed in accordance with Item G-135.

The suitability of material to be placed in embankments shall be subject to approval by the Engineer. All unsuitable material shall be disposed of in waste areas shown on the Plans or locations acceptable to the Engineer. The Contractor shall obtain all permits required for placing waste in areas he chooses which are not covered by Department obtained permits. All waste areas shall be graded to allow positive drainage of the area and of adjacent areas. The surface elevation of waste areas shall not extend above the surface elevation of adjacent usable areas of the airport, unless specified on the Plans or approved by the Engineer.

Areas where seeding is called for, in which the top layer of soil material has become compacted, by hauling or other activities of the Contractor shall be scarified and disked to a depth of 4 inches, in order to loosen and pulverize the soil.

If it is necessary to interrupt existing surface drainage, sewers or under-drainage, conduits, utilities, or similar underground structures the Contractor shall be responsible for and shall take all necessary precautions to preserve them or provide temporary services. When such facilities are encountered, the Contractor shall notify the Engineer, who shall arrange for their removal if necessary. The Contractor shall, at no additional cost to the Department, satisfactorily repair or pay the cost of all damage to such facilities or structures which may result from any of the Contractor's operations during the period of the contract.

152-2.2 EXCAVATION. No excavation shall be started until the work has been staked out by the Contractor and the Engineer has reviewed elevations and measurements of the ground surface. All suitable excavated material shall be used in the formation of embankment, subgrade, or for other purposes shown on the Plans. All unsuitable material shall be disposed of as shown on the Plans.

When the volume of the excavation exceeds that required to construct the embankments to the grades indicated, the excess shall be used to grade the areas of ultimate development or disposed of as directed. When the volume of excavation is not sufficient for constructing the fill to the grades indicated, the deficiency shall be obtained from borrow areas.

The grade shall be maintained so that the surface is well drained at all times. When necessary, temporary drains and drainage ditches shall be installed to intercept or divert surface water which may affect the work.

a.	Selective Grading. When selective grading is required, the more suitable material as designated by the Engineer shall be used in constructing the embankment or in capping the pavement subgrade. If, at the time of excavation, it is not possible to place this material in its final location, it shall be stockpiled in approved areas.

b.	Undercutting. Rock, shale, hardpan, loose rock, boulders, or other material unsatisfactory for Runway Safety Areas, subgrades, roads, shoulders, or any areas intended for turfing shall be excavated to a minimum depth of 12 inches, or to the depth specified by the Engineer, below the subgrade. Muck, peak, matted roots, or other yielding material, unsatisfactory for subgrade foundation, shall be removed to the depth specified. Unsuitable materials shall be disposed of at locations shown on the Plans. This excavated material shall be paid for as stated in the Special Provisions. The excavated area shall be refilled with suitable material, obtained from the grading operations or borrow areas and thoroughly compacted by rolling. The necessary refilling will constitute a part of the embankment. Where rock cuts are made and refilled with selected material, any pockets created in the rock surface shall be drained in accordance with the details shown on the Plans.

c.	Overbreak. Overbreak, including slides, is that portion of any material displaced or loosened beyond the finished work as planned or authorized by the Engineer. The Engineer shall determine if the displacement of such material was unavoidable and his/her decision shall be final. All overbreak shall be graded or removed by the Contractor and disposed of as directed; however, payment will not be made for the removal and disposal of overbreak which the Engineer determines as avoidable. Unavoidable overbreak will be classified as Unclassified Excavation.

d.	Removal of Utilities. The removal of existing structures and utilities required to permit the orderly progress of work will be accomplished by someone other than the Contractor, e.g., the utility unless otherwise shown on the Plans. All existing foundations shall be excavated for at least 2 feet below the top of subgrade or as indicated on the Plans, and the material disposed of as directed. All foundations thus excavated shall be backfilled with suitable material and compacted as specified herein.

e.	Compaction Requirements. In areas of excavation, the subgrade under areas serving aircraft or vehicle traffic loadings shall be compacted to the depth shown on the Plans and to a density of not less than 100% for non-cohesive soils (95% for cohesive soils) of the maximum density as determined by ASTM D 1557. The in-place field density shall be determined in accordance with ASTM D 2922 or ASTM D 2167. ASTM D 3017 shall be used to test moisture when ASTM D 2922 is used for density measurement. The in place moisture shall be determined by ASTM D 2216 when using other than the nuclear gauge method for density.

Stones or rock fragments larger than 3 inches in their greatest dimension will not be permitted in top 6 inches of the subgrade. The finished grading operations, conforming to the typical cross section, shall be completed and maintained at least 1,000 feet ahead of the paving operations or as directed by the Engineer.

In cuts, all loose or protruding rocks on the back slopes shall be scaled or otherwise removed to line of finished grade of slope. All cut-and-fill slopes shall be uniformly dressed to the slope, cross section, and alignment shown on the Plans or as directed by the Engineer.

Blasting will be permitted only when proper precautions are taken for the safety of all persons, the work, and the property. All damage done to the work or property shall be repaired at the Contractor's expense. All operations of the Contractor in connection with the transportation, storage, and use of explosives shall conform to all state and local regulations and explosive manufacturers' instructions, with applicable approved permits reviewed by the Engineer. Any approval given, however, will not relieve the Contractor of his/her responsibility in blasting operations.

In each distinct blasting area, where pertinent factors affecting blast vibrations and their effects in the area remain the same, the Contractor shall submit a blasting plan of the initial blasts to the Engineer for approval. This plan must consist of hole size, depth, spacing, burden, type of explosives, type of delay sequence, maximum amount of explosive on any one delay period, depth of rock, and depth of overburden if any. The maximum explosive charge weights per delay included in the plan shall not be increased without the approval of the Engineer.

The Contractor shall keep a record of each blast fired, its date, time, and location; the amount of explosives used, maximum explosive charge weight per delay period, and, where necessary, seismograph records identified by instrument number and location. These records shall be made available daily to the Engineer.

152-2.3 BORROW EXCAVATION. Borrow area(s) within the airport property are indicated on the Plans. Borrow excavation shall be made only at these designated locations and within the horizontal and vertical limits as staked or as directed.

152-2.4 DRAINAGE EXCAVATION. Drainage excavation shall consist of excavating for drainage ditches such as intercepting, inlet or outlet, for temporary levee construction; or for any other type as designed or as shown on the Plans. The work shall be performed in the proper sequence with the other construction. All satisfactory material shall be placed in fills; unsuitable material shall be placed in waste areas or as directed. Intercepting ditches shall be constructed prior to starting adjacent excavation operations. All necessary work shall be performed to secure a finish true to line, elevation, and cross section.

The Contractor shall maintain ditches constructed on the project to the required cross section and shall keep them free of debris or obstructions until the project is accepted.

152-2.5 PREPARATION OF EMBANKMENT AREA. Except as shown or otherwise specified, where an embankment is to be constructed to a height of 4 feet or less, all sod and vegetable matter shall be removed from the surface upon which the embankment is to be placed, and the cleared surface shall be completely broken up by plowing or scarifying to a minimum depth of 6 inches. This area shall then be compacted as indicated in paragraph 2.6.

When new embankment is placed against existing embankments or on slopes steeper than 3:1, the existing ground shall be continuously benched over the areas as the work is brought up in layers. Benching shall be of sufficient width to permit placing of material and the compacting operations. Each horizontal cut shall begin at the intersection of the original ground and the vertical side of the previous bench. Material thus cut out and deemed suitable shall be blended and incorporated into the new embankment.

No direct payment shall be made for the work performed under this section. The necessary clearing and grubbing and the quantity of excavation removed will be paid for under the respective items of work.

152-2.6 FORMATION OF EMBANKMENTS. Embankments shall be formed in successive horizontal layers of not more than 8 inches in loose depth for the full width of the cross section, unless otherwise approved by the Engineer.

When embankments are to be constructed across wet or swampy ground, which will not support the weight of heavy hauling and spreading equipment, the Contractor shall choose such methods of embankment construction and use such hauling and spreading equipment as will least disturb the soft foundation. When soft foundations are encountered, and when approved by the Engineer, the lower part of the fill may be constructed by dumping and spreading successive vehicle loads in a uniformly distributed layer of a thickness not greater than that necessary to support the vehicle while placing subsequent layers, after which the remainder of the embankment shall be constructed in layers and compacted as specified.

The grading operations shall be conducted, and the various soil strata shall be placed, to produce a soil structure as shown on the typical cross section or as directed. Materials such as brush, hedge, roots, stumps, grass and other organic matter, shall not be incorporated or buried in the embankment.

Operations on earthwork shall be suspended at any time when satisfactory results cannot be obtained because of rain, freezing, or other unsatisfactory conditions of the field. The Contractor shall drag, blade, or slope the embankment to provide proper surface drainage.

The material in the layer shall be within ±2% of optimum moisture content before rolling to obtain the prescribed compaction. In order to achieve a uniform moisture content throughout the layer, wetting or drying of the material and manipulation shall be required when necessary. Should the material be too wet to permit proper compaction or rolling, all work on all of the affected portions of the embankment shall be delayed until the material has dried to the required moisture content. Watering of dry material to obtain the proper moisture content shall be done with approved equipment that will sufficiently distribute the water. Sufficient equipment to furnish the required water shall be available at all times.

Rolling operations shall be continued until the embankment is compacted to not less than 95% of maximum density as determined by ASTM D 1557. Under all areas serving aircraft or vehicle traffic loadings, the embankment shall be compacted to the depth shown on the Plans and to a density of not less than 100% of the maximum density as determined by ASTM D 1557. The in-place field density shall be determined in accordance with ASTM D 1556, ASTM D 2167 or ASTM D 2922. ASTM D 3017 shall be used to test for moisture content when ASTM D 2922 is used to measure density. The in place moisture shall be determined by ASTM D 2216 when using other than the nuclear gauge method for density.

Compaction areas shall be kept separate, and no layer shall be covered by another until the proper density is obtained.

During construction of the embankment, the Contractor shall route his/her equipment at all times, both when loaded and when empty, over the layers as they are placed and shall distribute the travel evenly over the entire width of the embankment. The equipment shall be operated in such a manner that hardpan, cemented gravel, clay, or other chunky soil material will be broken up into small particles and become incorporated with the other material in the layer.

In the construction of embankments, layer placement shall begin in the deepest portion of the fill and progress in layers approximately parallel to the finished pavement grade line.

Stones or fragmentary rock larger than 3 inches in their greatest dimensions will not be allowed in the top 6 inches of the subgrade. Rockfill shall be brought up in layers as specified or as directed and every effort shall be exerted to fill the voids with the finer material forming a dense, compact mass. Rock or boulders shall not be disposed of outside the excavation or embankment areas, except at places and in the manner designated by the Engineer.

When the excavated material consists predominantly of rock fragments of such size that the material cannot be placed in layers of the prescribed thickness without crushing, pulverizing or further breaking down the pieces, such material may be placed in the embankment as directed in layers not exceeding 2 feet in thickness. Each layer shall be leveled and smoothed with suitable leveling equipment and by distribution of spalls and finer fragments of rock. These type lifts shall not be constructed above an elevation 4 feet below the finished subgrade. Density requirements will not apply to portions of embankments constructed of materials which cannot be tested in accordance with specified methods.

Frozen material shall not be placed in the embankment nor shall embankment be placed upon frozen material.

There will be no separate measurement or payment for compacted embankment, and all costs incidental to placing in layers, compacting, disking, watering, mixing, sloping, and other necessary operations for construction of embankments will be included in the contract price for excavation, borrow, or other items.

152-2.7 FINISHING AND PROTECTION OF SUBGRADE. After the subgrade has been substantially completed the full width shall be conditioned by removing any soft or other unstable material which will not compact properly. The resulting areas and all other low areas, holes or depressions shall be brought to grade with suitable select material. Scarifying, blading, rolling and other methods shall be performed to provide a thoroughly compacted subgrade shaped to the lines and grades shown on the Plans.

Grading of the subgrade shall be performed so that it will drain readily. The Contractor shall take all precautions necessary to protect the subgrade from damage. He/she shall limit hauling over the finished subgrade to that which is essential for construction purposes.

All ruts or rough places that develop in a completed subgrade shall be smoothed and recompacted.

No subbase, or surface course shall be placed on the subgrade until the subgrade has been approved by the Engineer.

152-2.8 HAUL. All hauling will be considered a necessary and incidental part of the work. Its cost shall be considered by the Contractor and included in the contract unit price for the pay of items of work involved. No payment will be made separately or directly for hauling on any part of the work.

152-2.9 TOLERANCES. In those areas upon which a subbase or base course is to be placed, the top of the subgrade shall be of such smoothness that, when tested with a 16-foot straightedge applied parallel and at right angles to the centerline, it shall not show any deviation in excess of 1/2 inch, or shall not be more than 0.05 foot from true grade as established by grade hubs or pins. Any deviation in excess of these amounts shall be corrected by loosening, adding, or removing materials; reshaping; and recompacting by watering and rolling.

On Runway Safety Areas, intermediate and other designated areas, the surface shall be of such smoothness that it will not vary more than 0.10 foot from true grade as established by grade hubs. Any deviation in excess of this amount shall be corrected by loosening, adding or removing materials, and reshaping.

METHOD OF MEASUREMENT

152-3.1 The quantity of excavation to be paid for will be the number of cubic yards measured in its original position. Pay quantities will be computed to the neat lines staked, by the method of average end areas of materials acceptably excavated as specified. Measurement will not include the quantity of materials excavated without authorization beyond normal slope lines, or the quantity of material used for purposes other than those directed.

152-3.2 Borrow Excavation material will be paid for on the basis of the number of cubic yards measured in its original position at the borrow pit. Pay quantities will be computed by the method of average end areas from cross sections taken before and after borrow excavation.

152-3.3 The quantity of Embankment or Borrow Embankment material to be paid for will be by the method of measurement as stated in the Bid. If by volume, pay quantities will be computed by the method of average end areas as determined from original ground cross sections before placement and to the neat lines staked and verified by the Engineer after placement. No allowance will be made for subsidence of the subgrade or for material placed outside the staked neat line limits. The quantity to be paid for will be the cubic yards of material placed and accepted in the completed embankment.

BASIS OF PAYMENT

152-4.1 For “Unclassified Excavation” payment will be made at the contract unit price per cubic yard.

152-4.2 For “Rock Excavation” payment will be made at the contract unit price per cubic yard.

152-4.3 For “Muck Excavation” payment will be made at the contract unit price per cubic yard.

152-4.4 For “Drainage Excavation” payment will be made at the contract unit price per cubic yard.

152-4.5 For “Borrow Excavation” payment will be made at the contract unit price per cubic yard.

152-4.6 For “Embankment” payment will be made at the contract unit price per cubic yard. If by weight, payment will be made at the contract unit price per ton. Due to variations in the specific gravity of the aggregates, the weight used may vary from the Bid quantities and no adjustment in contract unit price will be made because of such variation.

152-4.7 For “Borrow Embankment” payment will be made at the contract unit price per cubic yard. If by weight, payment will be made at the contract unit price per ton. Due to variations in the specific gravity of the aggregates, the weight used may vary from the Bid quantities and no adjustment in contract unit price will be made because of such variation.

Payment will be made under:

Item P-152a	Unclassified Excavation - per cubic yard

Item P-152b	Rock Excavation - per cubic yard

Item P-152c	Muck Excavation - per cubic yard

Item P-152d	Drainage Excavation - per cubic yard

Item P-152e	Borrow Excavation - per cubic yard

Item P-152f	Embankment - per cubic yard

Item P-152g	Embankment - per ton

Item P-152h	Borrow Embankment - per cubic yard

Item P-152i	Borrow Embankment - per ton

TESTING REQUIREMENTS

ASTM D 1557	Moisture-Density Relations of Soils and Soil-Aggregate Mixtures, Using 10-pound Rammer and 18-inch Drop

ASTM D 2167	Density of Soil In-Place by the Rubber Balloon Method

ASTM D 2216	Laboratory Determination of Water (Moisture) Content of Soil and Rock

ASTM D 2922	Density of Soil and Soil-Aggregate In Place by Nuclear Methods (Shallow Depth)

ASTM D 3017	Water Content of Soil and Rock in Place by Nuclear Methods (Shallow Depth)

ITEM P-154	SUBBASE COURSE

DESCRIPTION

154-1.1 This item shall consist of a subbase course composed of granular materials constructed on a prepared subgrade or underlying course in accordance with these Specifications, and in conformity with the dimensions and typical cross section shown on the Plans.

MATERIALS

154-2.1 MATERIALS. The subbase material shall consist of hard durable particles or fragments of granular aggregates. This material will be mixed or blended with fine sand, clay, stone dust, or other similar binding or filler materials produced from approved sources. This mixture must be uniform and shall comply with the requirements of these Specifications as to gradation, soil constants, and shall be capable of being compacted into a dense and stable subbase. the material shall be free from vegetable matter, lumps or excessive amounts of clay, and other objectionable or foreign substances. Pit-run material may be used, provided the material meets the requirements specified.

TABLE 1.    GRADATION REQUIREMENTS

| Sieve designation as per ASTM C 136 | Percentage by weight passing sieves |
| --- | --- |
| 3 inch | 100 |
| No. 10 | 30-70 |
| No. 50 | 0-30 |
| No. 200 | 0-6 |

The portion of the material passing the No. 40 sieve shall have a liquid limit of not more than 25 and a plasticity index of not more than 6 when tested in accordance with ASTM D 4318.

The gradations shall be well graded from coarse to fine and shall not vary from the low limit on one sieve to the high limit on the adjacent sieves, or vice versa.

CONSTRUCTION METHODS

154-3.1 GENERAL. The subbase course shall be placed where designated on the Plans or as directed by the Engineer. The material shall be shaped and thoroughly compacted within the tolerances specified.

Granular subbases which, due to grain sizes or shapes, are not sufficiently stable to support without movement the construction equipment, shall be mechanically stabilized to the depth necessary to provide such stability as directed by the Engineer. The mechanical stabilization shall principally include the addition of a fine-grained medium to bind the particles of the subbase material sufficiently to furnish a bearing strength, so that the course will not deform under the traffic of the construction equipment. The addition of the binding medium to the subbase material shall not increase the soil constants of that material above the limits specified.

154-3.2 PREPARING UNDERLYING COURSE. Before any subbase material is placed, the underlying course shall be prepared and conditioned as specified. The course shall be checked and accepted by the Engineer before placing and spreading operations are started.

To protect the subgrade and to ensure proper drainage, the spreading of the subbase shall begin along the centerline of the pavement on a crowned section or on the high side of pavements with a one-way slope.

154-3.3 MATERIALS ACCEPTANCE IN EXISTING CONDITION. When the entire subbase material is secured in a uniform and satisfactory condition, such approved material may be moved directly to the spreading equipment for placing. The material may be obtained from gravel pits, stockpiles, or may be produced from a crushing and screening plant with the proper blending. The materials from these sources shall meet the requirements for gradation, quality, and consistency. The moisture content of the material shall be approximately that required to obtain maximum density. The final operation shall be blading or dragging, if necessary, to obtain a smooth uniform surface true to line and grade.

154-3.4 GENERAL METHODS FOR PLACING. When materials from several sources are to be blended and mixed, the subbase material, together with any blended material, shall be thoroughly mixed prior to placing on grade.

The subbase course shall be constructed in layers. Any layer shall be not less than 3 inches nor more than 8 inches of compacted thickness. The material, as spread, shall be of uniform gradation with no pockets of fine or coarse materials. No material shall be placed in snow or on a soft, muddy, or frozen course.

When more than one layer is required, the construction procedure described herein shall apply similarly to each layer.

During the placing and spreading, sufficient caution shall be exercised to prevent the incorporation of subgrade, shoulder, or foreign material in the subbase course mixture.

154-3.5 FINISHING AND COMPACTING. After spreading or mixing, the subbase material shall be thoroughly compacted. Sufficient compactors shall be furnished to adequately handle the rate of placing and spreading of the subbase course. The moisture content of the material shall be approximately that required to obtain maximum density.

The field density of the compacted material shall be at least 100% of the maximum density of laboratory specimens prepared from samples of the subbase material delivered to the jobsite. The laboratory specimens shall be compacted and tested in accordance with ASTM D 1557. The in-place field density shall be determined in accordance with ASTM D 2922 or ASTM D 2167.

The course shall not be rolled when the underlying course is soft or yielding or when the rolling causes undulation in the subbase. When the rolling develops irregularities that exceed 1/2 inch when tested with a 16-foot straightedge, the irregular surface shall be loosened and then refilled with the same kind of material as that used in constructing the course and again rolled as required above.

Along places inaccessible to rollers, the subbase material shall be tamped thoroughly with mechanical or hand tampers.

Watering during rolling, if necessary, shall be in the amount and by equipment approved by the Engineer. Water shall not be added in such a manner or quantity that free water will reach the underlying layer and cause it to become soft.

154-3.6 SURFACE TEST. After the course is completely compacted, the surface shall be tested for smoothness and accuracy of grade and crown; any portion found to lack the required smoothness or to fail in accuracy of grade or crown shall be scarified, reshaped, recompacted, and otherwise manipulated as the Engineer may direct until the required smoothness and accuracy re obtained. The finished surface shall not vary more than 1/2 inch when tested with a 16-foot straightedge applied parallel with, and at right angles to, the centerline.

154-3.7 PROTECTION. Work on subbase course shall not be conducted during freezing temperature nor when the subgrade is wet. When the subbase material contains frozen material or when the underlying course is frozen, the construction shall be stopped.

154-3.8 MAINTENANCE. Following the final shaping of the material, the subbase shall be maintained throughout its entire length by the use of standard motor graders and rollers until, in the judgment of the Engineer, the subbase meets all requirements and is acceptable for the construction of the next course.

METHOD OF MEASUREMENT

154-4.1 Subbase Course will be weighed by the ton or measured by the cubic yard in final position in accordance with Subsection 90-02.

Subbase materials will not be included in any other excavation quantities.

# BASIS OF PAYMENT

154-5.1 Subbase Course will be paid for at the contract price, per unit of measurement, accepted in place.

Hauling and placing of these materials is subsidiary.

Payment will be made under:

Item P-154a	Subbase Course - per cubic yard

# Item P-154b	Subbase Course - per ton

TESTING REQUIREMENTS

ASTM C 136	Sieve or Screen Analysis of Fine and Coarse Aggregate

ASTM D 1557	Moisture-Density Relations of Soils and Soil-Aggregate Mixtures Using 10-lb. Rammer and 18-in Drop

ASTM D 2167	Density of Soil in Place by the Rubber-Balloon Method

ASTM D 2216	Laboratory Determination of Water (Moisture) Content of Soil and Rock

ASTM D 2922	Density of Soil and Soil-Aggregate In Place by Nuclear Methods (Shallow Depth)

ASTM D 3017	Water Content of Soil and Rock in Place by Nuclear Methods (Shallow Depth)

ASTM D 4318	Liquid Limit, Plastic Limit, and Plasticity Index of Soils

ITEM P-157 EROSION, SEDIMENT, AND POLLUTION CONTROL

(Over 5 acres)

157-1.1 DESCRIPTION. This work consists of planning, providing, inspecting and maintaining control of erosion, sedimentation, water pollution and hazardous materials contamination.

157-1.2 DEFINITIONS.

- BMP (Best Management Practices). A wide range of project management practices, schedules, activities, or prohibition of practices, that when used alone or in combination, prevent or reduce erosion, sedimentation, and/or pollution of adjacent water bodies and wetlands. BMP include temporary or permanent structural and non-structural devices and practices. The Department describes common BMP in its SWPPP Guide.

- ESCP (Erosion and Sediment Control Plan). The general plan for control of project-related erosion and sedimentation. The ESCP normally consists of a general narrative and a map or site plan. It is developed by the Department and included in the project Plans and specifications. It serves as a resource for bid estimation and a framework from which the Contractor develops the project SWPPP.

- Final Stabilization. A point in time when all ground-disturbing activities are complete and permanent erosion and sediment controls are established and functional. The stabilized site is protected from erosive forces of raindrop impact and water flow. Typically, all unpaved areas except graveled shoulders, crushed aggregate base course, or other areas not covered by permanent structures are protected by either a uniform blanket of perennial vegetation (at least 70% cover density) or equivalent permanent stabilization measures such as riprap, gabions or geotextiles.

- HMCP (Hazardous Material Control Plan). The Contractor's detailed plan for prevention of pollution that stems from the use, containment, cleanup, and disposal of hazardous material, including petroleum products generated by construction activities and equipment.

- NOI. Notice of Intent to commence ground-disturbing activities under the NPDES General Permit.

- NOT. Notice of Termination of coverage under the NPDES General Permit.

- NPDES General Permit. The General Permit for Stormwater Discharges from Construction Activities, issued by the Environmental Protection Agency (EPA) under the National Pollutant Discharge Elimination System (NPDES). It requires a SWPPP prior to ground-disturbing activities for the project.

- SWPPP (Storm Water Pollution Prevention Plan). The Contractor’s plan for erosion and sediment control and storm water management under the NPDES General Permit. The SWPPP is developed by the Contractor and describes site-specific controls and management of issues identified for the project. The approved SWPPP replaces the ESCP.

157-1.3 SUBMITTALS. Submit 3 copies each of your SWPPP and HMCP for approval no less than 5 calendar days prior to the preconstruction conference.

The Department will review the above submittals within 14 calendar days. Submittals that do not meet Department approval will be returned to you for modification.

The approved, the SWPPP must be signed by you and the Engineer in accordance with the NPDES General Permit.

Submit your signed NOI (use EPA Form 3510-9) to the Engineer no later than 10 working days before you intend to commence ground-disturbing activities.

The approved SWPPP and HMCP become the basis of the work required for the project erosion, sediment, and pollution control.

157-2.1 STORM WATER POLLUTION PREVENTION PLAN (SWPPP) REQUIREMENTS. Use the Department's ESCP to develop a SWPPP based on your scheduling, equipment, and use of alternative BMP. The plan must consider first preventing erosion, then minimizing erosion, and finally trapping sediment before it enters waterways.

The plan must address your site-specific controls and management plan for the construction site as well as for all material sites, waste disposal sites, haul roads, and other affected areas, public or private. The plan must also incorporate all the requirements of the project permits.

Have the SWPPP prepared under the direction of and sealed by a professional engineer currently registered in the State of Alaska. Include all requirements of the NPDES General Permit.

157-2.2 HAZARDOUS MATERIAL CONTROL PLAN (HMCP) REQUIREMENTS. Prepare a HMCP for the handling, storage, cleanup, and disposal of petroleum products and other hazardous substances. (See 40 CFR 117 and 302 for listing of hazardous materials.)

List and give the location of all hazardous materials, including office materials, to be used and/or stored on site, and their estimated quantities. Detail your plan for storing these materials as well as disposing of waste petroleum products and other hazardous materials generated by the project.

Identify the locations where fueling and maintenance activities will take place, describe the maintenance activities, and list all controls to prevent the accidental spillage of petroleum products and other hazardous materials.

Detail your procedures for containment and cleanup of hazardous substances, including a list of the types and quantities of equipment and materials available on site to be used.

Detail your plan for the prevention, containment, cleanup and disposal of soil and water contaminated by accidental spills. Detail your plan for dealing with unexpected contaminated soil and water encountered during construction.

Specify the line of authority and designate your field representative for spill response and one representative for each subcontractor.

157-3.1 CONSTRUCTION REQUIREMENTS.

Do not begin ground-disturbing work until you are notified by the Engineer that 48 hours have passed since the NOIs were mailed to the EPA and DEC.

Post at the construction site, the

- NPDES Permit number, if available, and a copy of the NOI,

- name and phone number of your local contact person, and

- location of a SWPPP available for viewing by the public.

Comply with all requirements of the NPDES General Permit, implement all temporary and permanent erosion and sediment control measures identified in the SWPPP, and ensure that the SWPPP remains current.

Maintain all temporary and permanent erosion and sediment control measures in effective operating condition.

Comply with all requirements of the approved HMCP and all state and federal regulations which pertain to the handling, storage, cleanup, and disposal of petroleum products or other hazardous substances. Contain, clean up, and dispose of all discharges of petroleum products and/or other materials hazardous to the land, air, water, and organic life forms. Perform all fueling operations in a safe and environmentally responsible manner. Comply with 18 AAC 75 and AS 46, Oil and Hazardous Substances Pollution Control.

Perform inspections and prepare inspection reports in compliance with the project SWPPP and the NPDES General Permit.

- Joint Inspections. Prior to start of construction conduct a joint on-site inspection with the Engineer and the professional engineer who stamped the SWPPP to discuss the implementation of the SWPPP.

Conduct the following additional joint on-site inspections with the Engineer:

(1) During construction, inspect the following at least once every 7 calendar days and within 24 hours of the end of a storm event exceeding 0.5 inch in 24 hrs. (as recorded at or near the project site).

- Disturbed areas that have not been finally stabilized.

- Areas used for storage of erodible materials that are exposed to precipitation.

- Sediment and erosion control measures.

- Locations where vehicles enter or exit the site.

- Prior to winter shutdown, to ensure that the site has been adequately stabilized.

- At project completion, to ensure final stabilization of the project.

- Winter Inspections. During winter shutdown, conduct inspections at least once every month and within 24 hours of a storm resulting in rainfall of 0.5 inch or greater. Monthly inspection requirements may be waived by the Engineer until one month before thawing conditions are expected to result in a discharge, if all of the following requirements are met:

- Below-freezing conditions are anticipated to continue for more than one month.

- Land disturbance activities have been suspended.

- The beginning and ending dates of the waiver period are documented in the SWPPP.

- Inspection Reports. Prepare and submit, within 3 calendar days of each inspection, a report with the following information:

- A summary of the scope of the inspection.

- Name(s) of personnel making the inspection.

- The date of the inspection.

- Observations relating to the implementation of the SWPPP.

- Any actions taken as the result of the inspection.

- Incidents of non-compliance.

Where a report does not identify any incidents of non-compliance, include certification that the facility is in compliance with the SWPPP and NPDES General Permit. Sign the report in accordance with Part VI. Standard Permit Conditions of the NPDES General Permit. All certifications shall be included as an appendix to the SWPPP.

Retain copies of the SWPPP, and all other records required by the NPDES General Permit, for at least 3 years from the date of final stabilization.

If unanticipated or emergency conditions threaten water quality, take immediate suitable action to preclude erosion and pollution.

Submit amendments to the SWPPP, to correct problems identified as a result of any

- storm event or other circumstance that threatens water quality, and

- inspection which identifies existing or potential problems.

Submit SWPPP amendments to the Engineer, within 7 calendar days following the storm event or inspection. Detail additional emergency measures required and taken, to include additional or modified measures. If modifications to existing measures are necessary, complete implementation within 7 days.

Stabilize all areas disturbed after the seeding deadline within 7 calendar days of the temporary or permanent cessation of ground-disturbing activities.

Submit a signed NOT (use EPA Form 3510-7) to the Engineer

- when the project site (including all material sources, disposal sites, etc.) has been finally stabilized and all storm water discharges from construction activities authorized by this permit have ceased, or

- when the construction activity Operator (as defined in the NPDES General Permit) has changed.

If you fail to coordinate temporary or permanent stabilization measures with the earthwork operations in a manner to effectively control erosion and prevent water pollution, the Engineer may suspend your earthwork operations and withhold monies due on current estimates for such earthwork items until all aspects of the work are coordinated in a satisfactory manner.

If you fail to:

- pursue work required by the approved SWPPP,

- respond to inspection recommendations and/or deficiencies in the SWPPP, or

- implement erosion and sedimentation controls identified by the Engineer,

the Engineer may, after giving you written notice, proceed to perform such work and deduct the cost thereof, including project engineering costs, from your progress payments.

157-4.1 METHOD OF MEASUREMENT. Items P-157a and P-157c will not be measured for payment.

Item P-157b and P-157d will be measured in the manner specified in the Contract or Directive authorizing the work.

157-5.1 BASIS OF PAYMENT. The Bid Schedule will include either items P-157a and P-157b or items P-157a, P-157c, and P-157d.

- Item P-157a Erosion and Pollution Control Administration. At the contract lump sum price for administration of all work under this section. Includes, but is not limited to, plan preparation, plan amendments and updates, inspections, monitoring, reporting and record keeping.

- Item P-157b Temporary Erosion and Pollution Control. At the prices specified to install and maintain temporary erosion, sedimentation, and pollution control measures.

- Item P-157c Temporary Erosion and Pollution Control. At the lump sum price shown on the bid schedule to install and maintain temporary erosion, sedimentation, and pollution control measures in accordance with the original approved SWPPP and HMCP.

- Item P-157d Temporary Erosion and Pollution Control Amendments. At the prices specified to install and maintain temporary erosion, sedimentation, and pollution control measures for extra, additional, or unanticipated work. All work paid under this item shall be shown as amendments to the original approved SWPPP or HMCP.

Temporary erosion and pollution control measures that are required at Contractor-furnished sites are subsidiary.

Temporary erosion and pollution control measures that you perform, that are required due to your negligence, carelessness, or failure to install permanent controls as a part of the work as scheduled or ordered by the Engineer, or for your convenience, will not be paid for.

Permanent erosion and pollution control measures will be measured and paid for under other contract items, when shown on the bid schedule.

Payment will be made under:

Item P-157a	Erosion and Pollution Control Administration - lump sum

Item P-157b	Temporary Erosion and Pollution Control - contingent sum

Item P-157c	Temporary Erosion and Pollution Control - lump sum

Item P-157d	Temporary Erosion and Pollution Control Amendments - contingent sum

ITEM P-158 EROSION, SEDIMENT, AND POLLUTION CONTROL

(5 acres or Less)

158-1.1 DESCRIPTION. This work consists of planning, providing, inspecting and maintaining control of erosion, sedimentation, water pollution and hazardous materials contamination.

158-1.2 DEFINITIONS.

- BMP (Best Management Practices). A wide range of project management practices, schedules, activities, or prohibition of practices, that when used alone or in combination, prevent or reduce erosion, sedimentation, and/or pollution of adjacent water bodies and wetlands. BMP include temporary or permanent structural and non-structural devices and practices. The Department describes common BMP in its SWPPP Guide.

- ESCP (Erosion and Sediment Control Plan). The general plan for control of project-related erosion and sedimentation. The ESCP normally consists of a general narrative and a map or site plan. It is developed by the Department and included in the project Plans and specifications. It serves as a resource for bid estimation and a framework from which the Contractor develops the project SWPPP.

- Final Stabilization. A point in time when all ground-disturbing activities are complete and permanent erosion and sediment controls are established and functional. The stabilized site is protected from erosive forces of raindrop impact and water flow. Typically, all unpaved areas except graveled shoulders, crushed aggregate base course, or other areas not covered by permanent structures are protected by either a uniform blanket of perennial vegetation (at least 70% cover density) or equivalent permanent stabilization measures such as riprap, gabions or geotextiles.

- HMCP (Hazardous Material Control Plan). The Contractor's detailed plan for prevention of pollution that stems from the use, containment, cleanup, and disposal of hazardous material, including petroleum products generated by construction activities and equipment.

- SWPPP (Storm Water Pollution Prevention Plan). The Contractor’s plan for erosion and sediment control and permanent storm water management. The SWPPP is developed by the Contractor and describes site-specific controls and management of issues identified for the project. The approved SWPPP replaces the ESCP.

158-1.3 SUBMITTALS. Submit 3 copies each of your SWPPP and HMCP for approval no less than 5 calendar days prior to the preconstruction conference.

The Department will review the above submittals within 14 calendar days. Submittals that do not meet Department approval will be returned to you for modification.

The approved SWPPP and HMCP become the basis of the work required for the project erosion, sedimentation, and pollution control.

158-2.1 STORM WATER POLLUTION PREVENTION PLAN (SWPPP) REQUIREMENTS. Use the Department's ESCP to develop a SWPPP based on your scheduling, equipment, and use of alternative BMP. The plan must consider first preventing erosion, then minimizing erosion, and finally trapping sediment before it enters waterways.

The plan must address your site-specific controls and management plan for the construction site as well as for all material sites, waste disposal sites, haul roads, and other affected areas, public or private. The plan must also incorporate all the requirements of the project permits.

Have the SWPPP prepared under the direction of and sealed by a professional engineer currently registered in the State of Alaska. Follow the format presented in the Department’s SWPPP Guide, for projects disturbing 5 acres or less.

158-2.2 HAZARDOUS MATERIAL CONTROL PLAN (HMCP) REQUIREMENTS. Prepare a HMCP for the handling, storage, cleanup, and disposal of petroleum products and other hazardous substances. (See 40 CFR 117 and 302 for listing of hazardous materials.)

List and give the location of all hazardous materials, including office materials, to be used and/or stored on site, and their estimated quantities. Detail your plan for storing these materials as well as disposing of waste petroleum products and other hazardous materials generated by the project.

Identify the locations where fueling and maintenance activities will take place, describe the maintenance activities, and list all controls to prevent the accidental spillage of petroleum products and other hazardous materials.

Detail your procedures for containment and cleanup of hazardous substances, including a list of the types and quantities of equipment and materials available on site to be used.

Detail your plan for the prevention, containment, cleanup and disposal of soil and water contaminated by accidental spills. Detail your plan for dealing with unexpected contaminated soil and water encountered during construction.

Specify the line of authority and designate your field representative for spill response and one representative for each subcontractor.

158-3.1 CONSTRUCTION REQUIREMENTS.

Do not begin ground-disturbing work until you receive written approval of the SWPPP and HMCP.

Post at the construction site, the

- name and phone number your local contact person, and

- location of a SWPPP available for viewing by the public.

Implement all temporary and permanent erosion and sediment control measures identified in the SWPPP, and ensure that the SWPPP remains current.

Comply with all requirements of the approved HMCP and all state and federal regulations which pertain to the handling, storage, cleanup, and disposal of petroleum products or other hazardous substances. Contain, clean up, and dispose of all discharges of petroleum products and/or other materials hazardous to the land, air, water, and organic life forms. Perform all fueling operations in a safe and environmentally responsible manner. Comply with 18 AAC 75 and AS 46, Oil and Hazardous Substances Pollution Control.

If unanticipated or emergency conditions threaten water quality, take immediate suitable action to preclude erosion and pollution.

Submit amendments to the SWPPP, to correct problems identified as a result of any

- storm event or other circumstance that threatens water quality, and

- inspection which identifies existing or potential problems.

Submit SWPPP amendments to the Engineer, within 7 calendar days following the storm event or inspection. Detail additional emergency measures required and taken, to include additional or modified measures. If modifications to existing measures are necessary, complete implementation within 7 days.

Stabilize all areas disturbed after the seeding deadline within 7 calendar days of the temporary or permanent cessation of ground-disturbing activities.

If you fail to coordinate temporary or permanent stabilization measures with the earthwork operations in a manner to effectively control erosion and prevent water pollution, the Engineer may suspend your earthwork operations and withhold monies due on current estimates for such earthwork items until all aspects of the work are coordinated in a satisfactory manner.

If you fail to:

- pursue work required by the approved SWPPP,

- respond to inspection recommendations and/or deficiencies in the SWPPP, or

- implement erosion and sedimentation controls identified by the Engineer,

the Engineer may, after giving you written notice, proceed to perform such work and deduct the cost thereof, including project engineering costs, from your progress payments.

158-4.1 METHOD OF MEASUREMENT. Items P-158a and P-158c will not be measured for payment.

Item P-158b and P-158d will be measured in the manner specified in the Contract or the Directive authorizing the work.

158-5.1 BASIS OF PAYMENT. The Bid Schedule will include either items P-158a and P-158b or items P-158a, P-158c, and P-158d.

- Item P-158a Erosion and Pollution Control Administration. At the contract lump sum price for administration of all work under this section. Includes, but is not limited to, plan preparation, plan amendments and updates, inspections, monitoring, reporting and record keeping.

- Item P-158b Temporary Erosion and Pollution Control. At the prices specified to install and maintain temporary erosion, sedimentation, and pollution control measures.

- Item P-158c Temporary Erosion and Pollution Control. At the lump sum price shown on the bid schedule to install and maintain temporary erosion, sedimentation, and pollution control measures in accordance with the original approved SWPPP and HMCP.

- Item P-158d Temporary Erosion and Pollution Control Amendments. At the prices specified to install and maintain temporary erosion, sedimentation, and pollution control measures for extra, additional, or unanticipated work. All work paid under this item shall be shown as amendments to the original approved SWPPP or HMCP.

Temporary erosion and pollution control measures that are required at Contractor-furnished sites are subsidiary.

Temporary erosion and pollution control measures that you perform, that are required due to your negligence, carelessness, or failure to install permanent controls as a part of the work as scheduled or ordered by the Engineer, or for your convenience, will not be paid for.

Permanent erosion and pollution control measures will be measured and paid for under other contract items, when shown on the bid schedule.

Payment will be made under:

Item P-158a 	Erosion and Pollution Control Administration - lump sum

Item P-158b 	Temporary Erosion and Pollution Control - contingent sum

Item P-158c 	Temporary Erosion and Pollution Control - lump sum

Item P-158d	Temporary Erosion and Pollution Control Amendments - contingent sum

PART III - AGGREGATE BASE & SURFACE COURSES

# ITEM P-208	AGGREGATE SURFACE COURSE

# DESCRIPTION

208-1.1 This item consists of an aggregate surface course composed of crushed or uncrushed coarse aggregate bonded with either soil or fine aggregate or both. It shall be constructed on a prepared course in accordance with these Specifications and to the dimensions and typical cross section shown on the Plans.

# MATERIALS

208-2.1 GENERAL. Aggregates shall consist of hard, durable particles or fragments of stone or gravel mixed or blended with sand, stone dust, or other similar binding or filler materials produced from approved sources. The aggregate shall be free from vegetation, lumps, or excessive amounts of clay and other objectionable substances. The coarse aggregate shall have a minimum degradation value of 45 when tested in accordance with ATM 313. The aggregate shall have a percent of wear not more than 50 at 500 revolutions as determined by ASTM C 131 and shall not show evidence of disintegration nor show loss greater than 12% when subjected to 5 cycles of sodium sulfate accelerated soundness test using AASHTO T 104.

208-2.2 CRUSHED AGGREGATE SURFACE COURSE. The aggregates shall consist of both fine and coarse fragments of crushed stone or crushed gravel mixed or blended with sand, screenings, or other similar approved materials. The material shall consist of hard, durable particles or fragments of stone and shall be free from excess soft or disintegrated pieces, dirt, or other objectionable matter.

The fractured particles in the finished product shall be as uniform as practicable. At least 75% by weight of material retained on the No. 4 sieve shall have one or more fractured faces, when tested in accordance with WAQTC TM 1.

If necessary to meet this requirement, or to eliminate an excess of fine, uncrushed particles, the gravel shall be screened before crushing.

208-2.3 UNCRUSHED AGGREGATE SURFACE COURSE. This material may consist of natural pit-run aggregate. However, screening, blending, ripping, washing, and/or necessary mixing of the material or other processing may be necessary to meet the gradation and performance requirements of this specification.

208-2.4 GRADATION. The gradation of the uncrushed or crushed material shall meet the requirements of the gradations given in the Special Provisions, when tested in accordance with ASTM C 117 and C 136.

The specified gradations represent the limits of suitability of aggregate for use from the sources of supply. The final gradations decided on, within the specified limits, shall be well graded from coarse to fine and shall not vary from the low limit on one sieve to the high limit on the adjacent sieves, or vice versa.

The portion of the material passing the No. 40 sieve shall have a liquid limit not more than 25 and a plasticity index not more than 6, when tested in accordance with ASTM D 4318.

208-2.5 FINES FOR BLENDING. If additional fine material is necessary, it shall be obtained from approved sources and uniformly blended with the aggregate at the crushing plant, the mixing plant, or as approved by the Engineer. Silt, stone dust, or other similar fine material may be used as binder.

# CONSTRUCTION METHODS

208-3.1 (Not Used)

208-3.2 PREPARING UNDERLYING COURSE. The underlying course will be checked and accepted by the Engineer before placing and spreading operations are started. Any ruts or soft areas shall be corrected and compacted to the required density before placing aggregate surface course.

To protect the underlying course and to ensure proper drainage, the spreading of the aggregate surface course shall begin along the centerline on a crowned section or on the high side of sections with a one-way slope.

208-3.3 METHODS OF PRODUCTION.

a.	Plant Mix. When selected by the Contractor and approved by the Engineer, the material shall be uniformly mixed in an approved plant.

b.	Travel Plant. When the use of a traveling plant is approved by the Engineer, the plant shall mix the materials in a single pass. If needed to achieve optimum moisture, water shall be thoroughly mixed with the aggregates during this operation.

If using a windrow-type of travel plant, the windrows shall be placed parallel to the embankment centerline. The windrow volume shall be sufficient to cover exact areas as planned. The windrow contents shall produce a mixture of the required gradation and bonding qualities.

If using a travel plant that mixes previously spread aggregates in-place, the material shall have been spread in such thickness and proportions as may be handled by the machine to develop a course of the thickness of each layer and of the gradation required.

c.	Materials of Proper Gradation. Material which meets the requirements for quality, gradation, and consistency, and which contains approximately the proper moisture for compaction, may be placed directly on the grade, without further mixing.

Any minor deficiency or excess of moisture may be corrected by surface watering or by aeration. Some mixing or manipulation may be required immediately preceding compacting to obtain the required moisture content.

208-3.4 PLACING. The surface course shall be constructed without segregation of the aggregate. The material shall be placed in uniform, equal-depth layers, each not exceeding 6 inches of compacted depth. No material shall be placed in snow or on a soft uncompacted, muddy, or frozen course.

During the mixing and spreading process, sufficient caution shall be exercised to prevent the incorporation of subgrade, subbase, or shoulder material in the surface course mixture.

The Contractor shall install test strips of aggregate surface course with minimum dimensions of 100 feet by 16 feet by typical section thickness in an area heavily traveled by construction equipment, as approved by the Engineer. The stability and compaction characteristics of the material will be observed. The percentage of material passing the No. 200 sieve will be varied within the limits specified in the gradation in the Special Provisions while the stability and compaction are investigated.

The test strip results will be used to define the final gradation to be placed on the project based on the stability characteristics. Once the optimum percentage of fines passing the No. 200 sieve has been determined, it shall not vary more than ±2% from the optimum. Separate test strips are required for aggregate surface course from each materials source, if more than one source is used.

No aggregate surface course shall be placed on the project, other than in the test strips, until the Engineer has determined which percentage of fines performs most satisfactorily and results in the best stability. Test strip material accepted by the Engineer will be measured for payment.

208-3.5 COMPACTION. Immediately upon completion of the spreading operations, the aggregate shall be thoroughly compacted to the required density. The moisture content of the material shall be approximately that required to obtain maximum density.

208-3.6 ACCEPTANCE SAMPLING AND TESTING FOR DENSITY. The surface course will be accepted for density when the field density is at least 97% of the maximum density of laboratory specimens prepared from samples of the material delivered to the job site. The specimens will be compacted and tested in accordance with ASTM D 1557 or ATM 212. The in-place field density will be determined in accordance with ASTM D 2167 (or ASTM D 2922 and ASTM D 3017). If the specified density is not attained, the material shall be reworked and/or recompacted until the specified density is reached.

208-3.7 FINISHING. The surface of the aggregate surface course shall be finished by blading or with automated equipment specifically designed for this purpose.

In no case shall thin layers of material be added to the top of surface course to meet grade. If the compacted elevation of the top layer is 0.05 foot or more below grade, it shall be scarified to a depth of at least 3 inches, new material added, and the layer shall be blended and compacted to bring it to grade. If the finished surface is above plan grade, it shall be cut back to grade and recompacted.

208-3.8 SURFACE TEST. After the course has been completely compacted, the surface will be tested by the Engineer for smoothness and accuracy of grade and crown. The finished grade elevation shall not vary more than 0.05 foot from the design elevation. The finished surface shall not vary more than 3/8 inch from a 16-foot straightedge when applied to the surface parallel with, and at right angles to, the centerline. Any portion lacking the required smoothness or failing in accuracy of grade or crown shall be corrected to within the specified tolerances.

208-3.9 PROTECTION. Work on the surface course shall not be accomplished during freezing temperatures or when the subgrade is wet. When the aggregates contain frozen materials or when the underlying course is frozen, the construction shall be stopped.

Hauling equipment may be routed over completed portions of the surface course, provided no damage results and provided that such equipment is routed over the full width of the surface course to avoid rutting or uneven compaction. However, the Engineer in charge will have full and specific authority to stop all hauling over completed or partially completed surface course when, in his/her opinion, such hauling is causing damage. Any damage resulting to the surface course from routing equipment over the surface course shall be repaired by the Contractor at his/her own expense.

208-3.10 MAINTENANCE. Following the completion of the aggregate surface course, the Contractor shall satisfactorily remove all blue tops, fill and compact the voids, and perform all maintenance work on this surface until final acceptance unless otherwise stated in the Specifications. The surface course shall be properly drained at all times.

# METHOD OF MEASUREMENT

208-4.1 Aggregate Surface Course will be weighed by the ton or measured by the cubic yard in final position in accordance with Subsection 90-02.

BASIS OF PAYMENT

208-5.1 Aggregate Surface Course will be paid for at the contract price, per unit of measurement, accepted in place.

Payment will be made under:

Item P-208a	Crushed Aggregate Surface Course - per cubic yard

Item P-208b	Uncrushed Aggregate Surface Course - per cubic yard

Item P-208c	Crushed Aggregate Surface Course - per ton

Item P-208d	Uncrushed Aggregate Surface Course - per ton

# TESTING REQUIREMENTS

AASHTO T 104	Soundness of Aggregate by Use of Sodium Sulfate or Magnesium Sulfate

ASTM C 29	Unit Weight of Aggregate

ASTM C 117	Materials Finer than 75um (No. 200) Sieve in Mineral Aggregates by Washing

ASTM C 131	Resistance to Abrasion of Small Size Coarse Aggregate by Use of the Los Angeles Machine

ASTM C 136	Sieve or Screen Analysis of Fine and Coarse Aggregate

ASTM D 1557	Moisture-Density Relations of Soils and Soil-Aggregate Mixtures Using 10-lb. Rammer and 18-in Drop

ASTM D 2167	Density of Soil in Place by the Rubber-Balloon Method

ASTM D 2216	Laboratory Determination of Water (Moisture) Content of Soil and Rock

ASTM D 2922	Density of Soil and Soil-Aggregate In Place by Nuclear Methods (Shallow Depth)

ASTM D 3017	Water Content of Soil and Rock in Place by Nuclear Methods (Shallow Depth)

ASTM D 4318	Liquid Limit, Plastic Limit, and Plasticity Index of Soils

ATM 212	The Standard Density of Coarse Granular Materials Using the Vibratory Compactor

ATM 313	The Degradation Value of Aggregates

WAQTC TM 1	Determining the Percentage of Fracture in Coarse Aggregate

WAQTC Field Operating Procedure (FOP) for AASHTO T 27 and T 11 Coarse and Fine Aggregate Gradation

# ITEM P-209	CRUSHED AGGREGATE BASE COURSE

# DESCRIPTION

209-1.1 This item consists of a base course composed of crushed aggregates constructed on a prepared course in accordance with these Specifications and to the dimensions and typical cross section shown on the Plans.

# MATERIALS

209-2.1 AGGREGATE. Aggregates shall consist of clean, sound, durable particles of crushed stone or crushed gravel and shall be free from vegetable matter, excess coatings of clay, silt, and other objectionable materials and shall contain no clay balls.

Fine aggregate passing the No. 4 sieve shall consist of fines from the operation of crushing the coarse aggregate. If necessary, fine aggregate may be added to produce the correct gradation. The fine aggregate shall be produced by crushing stone and gravel that meet the requirements for wear and soundness specified for coarse aggregate.

The crushed aggregate portion which is retained on the No. 4 sieve shall have at least 75% by weight with 2 fractured faces as determined by WAQTC TM 1.

The percentage of wear shall not be greater than 45% when tested in accordance with ASTM C 131. The sodium sulfate soundness loss shall not exceed 12%, after 5 cycles, when tested in accordance with ASTM C 88. Aggregates shall have a minimum degradation value of 45 when tested in accordance with ATM 313.

The fraction passing the No. 40 sieve shall have a liquid limit no greater than 25 and a plasticity index of not more than 4 when tested in accordance with ASTM D 4318. The fine aggregate shall have a minimum sand equivalent value of 35 when tested in accordance with ASTM D 2419.

# a.	Sampling and Testing. Aggregates for preliminary testing shall be furnished by the Contractor prior to the start of production. All tests for initial aggregate submittals necessary to determine compliance with the specification requirements will be made by the Engineer at no expense to the Contractor.

Samples of aggregates shall be furnished by the Contractor at the start of production and at intervals during production. The sampling points and intervals will be designated by the Engineer. The samples will be the basis of approval of aggregates.

Samples of aggregates to check gradation will be taken by the Engineer in accordance with ASTM D 75, and tested in accordance with ASTM C 136 and C 117.

b.	Gradation Requirements. The gradation (job mix) of the final mixture shall fall within the design range indicated in Table 1, when tested in accordance with ASTM C 117 and C 136. The final gradation shall be continuously well graded from coarse to fine and shall not vary from the low limit on one sieve to the high limit on an adjacent sieve or vice versa.

# TABLE 1.    REQUIREMENTS FOR GRADATION OF AGGREGATE

| Sieve Designation (Square Openings) | Percentage by weight passing sieves |
| --- | --- |
|  | C-1 | D-1 |
| 1-1/2 in | 100 |  |
| 1.00 in | 70-100 | 100 |
| 3/4 in | 60-90 | 70-100 |
| 3/8 in | 45-75 | 50-80 |
| No.4 | 30-60 | 35-65 |
| No. 8 | 22-52 | 20-50 |
| No. 40 | 8-30 | 8-30 |
| No. 200 | 0-6 | 0-6 |

Note: Unless otherwise specified, Gradation C-1 shall be used.

# CONSTRUCTION METHODS

209-3.1 PREPARING UNDERLYING COURSE. Placing and spreading operations shall not commence until the underlying course has been accepted, in writing, by the Engineer. Any ruts or soft areas shall be corrected and compacted to the required density before placing the base course. Material shall not be placed on frozen subgrade.

209-3.2 MIXING. The aggregate shall be uniformly blended during crushing operations or mixed in a plant. The plant shall blend and mix the materials to meet the Specifications.

209-3.3 PLACING. The crushed aggregate base material shall be placed on the approved subgrade in uniform, equal-depth layers, each not exceeding 6 inches of compacted depth.

The previously constructed layer shall be cleaned of loose and foreign material prior to placing the next layer. The surface of the compacted material shall be kept moist until covered with the next layer.

209-3.4 COMPACTION. Immediately upon completion of the spreading operations, the aggregate shall be thoroughly compacted to the required density. The moisture content of the material shall be approximately that required to obtain maximum density.

209-3.5 ACCEPTANCE SAMPLING AND TESTING FOR DENSITY. Base course will be accepted for density when the field density is at least 100% of the maximum density of laboratory specimens prepared from samples of the material delivered to the job site. The specimens will be compacted and tested in accordance with ASTM D 1557 or ATM 212. The in-place field density will be determined in accordance with ASTM D 2167 (or ASTM D 2922 and ASTM D 3017). If the specified density is not attained, the material shall be reworked and/or recompacted until the specified density is reached.

209-3.6 FINISHING. The surface of the aggregate base course shall be finished by blading or with automated equipment specifically designed for this purpose.

In no case shall thin layers of material be added to the top of base course to meet grade. If the compacted elevation of the top layer is 0.05 foot or more below grade, it shall be scarified to a depth of at least 3 inches, new material added, and the layer shall be blended and compacted to bring it to grade. If the finished surface is above plan grade, it shall be cut back to grade and recompacted.

209-3.7 SURFACE TEST. After the course has been completely compacted, the surface will be tested by the Engineer for smoothness and accuracy of grade and crown. The finished surface shall not vary more than 3/8 inch from a 16-foot straightedge when applied to the surface parallel with, and at right angles to, the centerline. Any portion lacking the required smoothness or failing in accuracy of grade or crown shall be corrected to within the specified tolerances.

209-3.8 THICKNESS CONTROL. The thickness of the finished base course will be determined by the Engineer by taking before and after elevation measurements, or by depth tests, at random locations, each representing no more than 500 yd2. The completed thickness of the base course shall be within 1/2 inch of the design thickness. Where the thickness is deficient by more than 1/2 inch, it shall be corrected to within the specified tolerances.

209-3.9 MAINTENANCE. The base course shall be maintained in a condition that will meet all specification requirements until the work is accepted. Equipment used in the construction of an adjoining section may be routed over completed portions of the base course, provided no damage results and provided that the equipment is routed over the full width of the base course to avoid rutting or uneven compaction.

# METHOD OF MEASUREMENT

209-4.1 Crushed Aggregate Base Course will be weighed by the ton or measured by the cubic yard in final position in accordance with Subsection 90-02.

BASIS OF PAYMENT

209-5.1 Crushed Aggregate Base Course will be paid for at the contract price, per unit of measurement, accepted in place.

# Payment will be made under:

# Item P-209a	Crushed Aggregate Base Course - per cubic yard

# Item P-209b	Crushed Aggregate Base Course - per ton

# TESTING REQUIREMENTS

ASTM C 88	Soundness of Aggregates by Use of Sodium Sulfate or Magnesium Sulfate

ASTM C 117	Materials Finer than 75 um (No. 200) Sieve in Mineral Aggregates by Washing

ASTM C 131	Resistance to Abrasion of Small Size Coarse Aggregate by Use of the Los Angeles Machine

ASTM C 136	Sieve or Screen Analysis of Fine and Coarse Aggregate

ASTM D 75	Sampling Aggregate

ASTM D 1557	Moisture-Density Relations of Soils and Soil-Aggregate Mixtures Using 10-lb. Rammer and 18 in drop

ASTM D 2167	Density of Soil in Place by the Rubber-Balloon Method

ASTM D 2216	Laboratory Determination of Water (Moisture) Content of Soil and Rock

ASTM D 2419	Sand Equivalent Value of Soils and Fine Aggregate

ASTM D 2922	Density of Soil and Soil-Aggregate in Place by Nuclear Methods

ASTM D 3017	Moisture Content of Soil and Soil-Aggregate in Place by Nuclear Methods

ASTM D 4318	Liquid Limit, Plastic Limit, and Plasticity Index of Soils

ASTM D 4643	Determination of Water (Moisture) Content of Soil by the Microwave Oven Method

ASTM D 4959	Determination of Water (Moisture) Content of Soil by Direct Heating Method

ATM 212	Determining the Standard Density of Coarse Granular Materials Using the Vibratory Compactor

ATM 313 	Degradation of Aggregates

WAQTC TM 1	Determining the Percentage of Fracture in Coarse Aggregate

PART V - FLEXIBLE SURFACE COURSES

ITEM P-401 PLANT MIX BITUMINOUS PAVEMENT

DESCRIPTION

401-1.1 This item shall consist of a surface course composed of mineral aggregate and bituminous material mixed in a central mixing plant and placed on a prepared course in accordance with these Specifications and shall conform to the lines, grades, thicknesses, and typical cross sections shown on the Plans. Each course shall be constructed to the depth, typical section, or elevation required by the Plans and shall be rolled, finished, and approved before the placement of the next course.

MATERIALS

401-2.1 AGGREGATE. Aggregates shall consist of crushed stone or crushed gravel with or without sand or other inert finely divided mineral aggregate. The portion of materials retained on the No. 4 sieve is coarse aggregate. The portion passing the No. 4 sieve and retained on the No. 200 sieve is fine aggregate, and the portion passing the No. 200 sieve is mineral filler.

a.	Coarse Aggregate. Coarse aggregate shall consist of sound, tough, durable particles, free from adherent films of matter that would prevent thorough coating and bonding with the bituminous material and be free from organic matter and other deleterious substances. The percentage of wear shall not be greater than 40% when tested in accordance with ASTM C 131. The sodium sulfate soundness loss shall not exceed 10%, or the magnesium sulfate soundness loss shall not exceed 13%, after 5 cycles, when tested in accordance with ASTM C 88. The aggregate shall have a minimum degradation value of 30 when tested in accordance with ATM 313.

The crushed aggregate portion which is retained on the No. 4 sieve shall have at least 75% by weight 2 fractured faces as determined by WAQTC TM 1.

The aggregate shall not contain more than 8%, by weight, of flat or elongated pieces, when tested in accordance with ASTM D 4791. The ratio of the calipers shall be set to 1:5.

b.	Fine Aggregate. Fine aggregate shall consist of clean, sound, durable, angular shaped particles produced by crushing stone, slag, or gravel that meets the requirements for wear and soundness specified for coarse aggregate. The aggregate particles shall be free from coatings of clay, silt, or other objectionable matter and shall contain no clay balls. The fine aggregate, including any blended material for the fine aggregate, shall have a plasticity index of not more than 6 and a liquid limit of not more than 25 when tested in accordance with ASTM D 4318.

Natural (nonmanufactured) sand may be used to obtain the gradation of the aggregate blend or to improve the workability of the mix. The amount of sand to be added will be adjusted to produce mixtures conforming to requirements of this specification. The fine aggregate shall not contain more than 20% natural sand by weight of total aggregates.

The aggregate shall have sand equivalent values of 35 or greater when tested in accordance with ASTM D 2419.

c.	Sampling. ASTM D 75 shall be used in sampling coarse and fine aggregate, and ASTM C 183 shall be used in sampling mineral filler.

401-2.2 MINERAL FILLER. If filler, in addition to that naturally present in the aggregate, is necessary, it shall meet the requirements of ASTM D 242.

401-2.3 BITUMINOUS MATERIAL. Bituminous material shall conform to the following requirements:

Viscosity Grade	Specification

AC-5	ASTM D 3381

The Contractor shall furnish vendor's certified test reports for each lot of bituminous material shipped to the project. The vendor's certified test report for the bituminous material can be used for acceptance or tested independently by the Engineer.

All excess asphalt cement shall remain the property of the Contractor. Removal of excess asphalt cement from the project area shall be incidental to the contract and no separate payment will be made.

401-2.4 PRELIMINARY MATERIAL ACCEPTANCE. Prior to delivery of materials to the job site, the Contractor shall submit certified test reports to the Engineer for the following materials:

- Coarse Aggregate.

- Percent of wear.

- Soundness.

- Fine Aggregate.

- Liquid limit.

- Plastic index.

- Sand equivalent.

c.	Mineral Filler.

d.	Bituminous Material. The certification(s) shall show the appropriate ASTM test(s) for each material, the test results, and a statement that the material meets the specification requirement.

The Engineer may request samples for testing, prior to and during production, to verify the quality of the materials and to ensure conformance with the applicable specifications.

COMPOSITION

401-3.1 COMPOSITION OF MIXTURE. The bituminous plant mix shall be composed of a mixture of well-graded aggregate, filler if required, and bituminous material. The several aggregate fractions shall be sized, handled in separate size groups, and combined in such proportions that the resulting mixture meets the grading requirements of the job mix formula (JMF).

401-3.2 JOB MIX FORMULA. No bituminous mixture for payment shall be produced until a JMF has been approved by the Engineer. The bituminous mixture shall be designed using procedures contained in ATM 417, “Chapter 5, Marshall Method of Mix Design, of the Asphalt Institute's Manual Series No. 2 (MS-2), Mix Design Methods for Asphalt Concrete”, and shall meet the requirements of Tables 1 and 2.

If material variability exceeds the standard deviations indicated, the JMF and subsequent production targets should be based on a stability greater than shown in Table 1, and the flow and air voids should be targeted close to the mid-range of the criteria in order meet the acceptance requirements.

If the Tensile Strength Ratio (TSR) of the composite mixture, as determined by ASTM D 4867, is less than 75, the aggregates shall be rejected or the asphalt treated with an approved anti-stripping agent. The amount of anti-stripping agent added to the asphalt shall be sufficient to produce a TSR of not less than 75. If an antistrip agent is required, it will be provided by the Contractor at no additional cost.

The JMF shall be submitted in writing by the Contractor to the Engineer at least 15 calendar days prior to the start of paving operations and shall include as a minimum:

- Percent passing each sieve size.

- Percent of asphalt cement.

- Asphalt viscosity or penetration grade.

- Number of blows of hammer compaction per side of molded specimen.

- Mixing temperature.

- Compaction temperature.

- Temperature of mix when discharged from the mixer.

- Temperature-viscosity relationship of the asphalt cement.

- Plot of the combined gradation on the Federal Highway Administration (FHWA) 45 power gradation curve.

- Graphical plots of stability, flow, air voids, voids in the mineral aggregate, and unit weight verses asphalt content.

- Percent natural sand.

- Percent fractured faces.

- Percent elongated particles.

- Tensile Strength Ratio (TSR).

- Antistrip agent (if required).

The JMF may be designed by the Department. The Contractor shall submit samples to the Engineer, upon request, for JMF verification testing.

The JMF for each mixture shall be in effect until modified in writing by the Engineer. Should a change in sources of materials be made, a new JMF must be approved by the Engineer before the new material is used.

TABLE 1.    MIX DESIGN REQUIREMENTS

| Test Property | Pavements Designed for Aircraft Gross Weights of 60,000 Lbs. or More or Tire Pressures of 100 Psi or More | Pavements Designed for Aircraft Gross Weight Less Than 60,000 Lbs. or Tire Pressure Less Than 100 Psi |
| --- | --- | --- |
| Number of blows | 75 | 50 |
| Stability, pounds | 2150 | 1350 |
| Flow, 0.01 inch | 10-14 | 10-18 |
| Air voids % | 2.8-4.2 | 2.8-4.2 |
| Voids in mineral aggregate, %, min. | See Table 2 | See Table 2 |

TABLE 2.    MINIMUM PERCENT VOIDS IN MINERAL AGGREGATE

| Maximum Particle Size inch | Voids in Mineral Aggregate, %, Minimum |
| --- | --- |
| 1/2 | 14.0 |
| 3/4 | 13.0 |
| 1 | 12.0 |
| 1-1/4 | 11.0 |

The mineral aggregate shall be of such size that the percentage composition by weight, as determined by laboratory screens, will conform to the gradation or gradations specified in Table 3 when tested in accordance with ASTM Standard C 136 and C 117.

The gradations in Table 3 represent the limits which shall determine the suitability of aggregate for use from the sources of supply. The aggregate, as selected (and used in the JMF), shall have a gradation within the limits designated in Table 3 and shall not vary from the low limit on one sieve to the high limit on the adjacent sieve, or vice versa, but shall be well graded from coarse to fine when tested in accordance with WAQTC FOP for AASHTO T 27 and T 11.

For acceptance testing, deviations from the final approved mix design for bitumen content and gradation of aggregates shall be within the tolerance limits for individual measurements as specified in Table 5. The limits still will apply if they fall outside the master grading band in Table 3. Limits do not apply to the largest sieve specified.

The maximum size aggregate used shall not be more than one-half of the thickness of the course being constructed.

TABLE 3.    AGGREGATE - BITUMINOUS PAVEMENTS

| Sieve Size | Percentage by Weight Passing Sieves |
| --- | --- |
|  | 1-1/4 in.max | 1.00 in. max | 3/4 in. max | 1/2 in. max |
| 1-1/4 in. | 100 | -- | -- | -- |
| 1 in. | 86-98 | 100 | -- | -- |
| 3/4 in. | 68-93 | 76-98 | 100 | -- |
| 1/2 in. | 57-81 | 66-86 | 75-90 | 100 |
| 3/8 in. | 49-69 | 57-77 | 60-84 | 80-90 |
| No. 4 | 34-54 | 40-60 | 33-70 | 4-81 |
| No.8 | 22-42 | 26-46 | 19-56 | 26-70 |
| No.16 | 13-33 | 17-37 | 10-44 | 16-59 |
| No.30 | 8-24 | 11-27 | 7-34 | 9-49 |
| No.50 | 6-18 | 7-19 | 5-24 | 6-36 |
| No.100 | 4-12 | 6-16 | 4-16 | 4-22 |
| No.200 | 3-6 | 3-6 | 3-7 | 3-7 |
| Asphalt % | 4.5-7.0 | 4.5-7.0 | 5.0-7.5 | 5.5-8.0 |

The aggregate gradations shown are based on aggregates of uniform specific gravity. The percentages passing the various sieves shall be corrected when aggregates of varying specific gravities are used, as indicated in the Asphalt Institute Manual Series No. 2 (MS-2), Appendix A.

401-3.3 RECYCLED ASPHALT CONCRETE. Recycled asphalt concrete shall consist of reclaimed asphalt pavement (RAP), coarse aggregate, fine aggregate, mineral filler, asphalt cement, and recycling agent, if necessary. Reclaimed asphalt pavement may be used for all courses.

The RAP shall be of a consistent gradation and asphalt content. The Contractor may obtain the RAP from the job site or an existing source.

All new aggregates used in the recycled mix shall meet the requirements of paragraph 401-2.1. New bituminous material shall meet the requirements of paragraph 401-2.3. Recycling agents shall meet the requirements of ASTM D 4552.

The recycled asphalt concrete mix shall be designed using procedures contained in the Asphalt Institute's Manual Series Number 20 (MS-20), Asphalt Hot-Mix Recycling, in conjunction with MS-2 and ATM 417. The job mix shall meet the requirements of paragraph 401-3.2. In addition to the requirements of paragraph 401-3.2, the JMF shall indicate the percent of RAP, the percent and viscosity grade of new asphalt, the percent and grade of hot-mix recycling agent (if used), and the properties (including viscosity and penetration) of the asphalt blend.

The Contractor shall submit documentation to the Engineer, indicating that the mixing equipment proposed for use is adequate to mix the percent of RAP shown in the JMF and meet all local and national environmental regulations.

401-3.4 TEST SECTION. Prior to full production, the Contractor shall prepare and place a quantity of bituminous mixture according to the JMF. The amount of mixture should be sufficient to construct a test section 300 feet long and at least 20 to 30 feet wide placed in two lanes, with a longitudinal cold joint, and shall be of the same depth specified for the construction of the course which it represents. The underlying grade or pavement structure upon which the test section is to be constructed shall be the same as the remainder of the course represented by the test section. The equipment used in construction of the test section shall be the same type and weight to be used on the remainder of the course represented by the test section.

Three random 6 inch diameter core samples, randomly selected in accordance with ASTM D 3665, shall be cut from the finished pavement mat by the Contractor. The samples will be tested for density from the bulk specific gravity (BSG) in accordance with ASTM D 2726 or D 1188 whichever is applicable and evaluated in accordance with Section 401-5.2. The Target Value for density will be 94% of the theoretical maximum specific gravity (MSG), as determined by ASTM D 2041. The sample used to determine the theoretical MSG will be randomly selected from the material in the test section. The relative density in percent equals the BSG times 100 divided by the maximum specific gravity for the lot and rounded to the nearest whole percent.

Three random samples of the mixture will be taken in accordance with 401-5.1a(1) and (2) and tested for aggregate gradation and asphalt cement content in accordance with Section 401-5.1 and evaluated in accordance with Section 401-5.2. Joint density will be evaluated in accordance with paragraph 401-5.2f(3). The Target Value for joint density shall be 93% of the theoretical MSG as determined by ASTM D 2041, Type C, D, or E container.

If the initial test section should prove to be unacceptable, the necessary adjustments to the JMF, plant operation, placing procedures, and/or rolling procedures shall be made. A second test section shall then be placed. If the second test section also does not meet specification requirements, both sections shall be removed at the Contractor's expense. Additional test sections, as required, shall be constructed and evaluated for conformance to the Specifications. Any additional sections that are not acceptable shall be removed at the Contractor's expense. Full production shall not begin until an acceptable section has been constructed and accepted by the Engineer. The initial test section, whether acceptable or unacceptable, and any subsequent section that meets specification requirements will be paid for in accordance with paragraph 401-8.1.

Job mix control testing shall be performed by the Contractor at the start of plant production and in conjunction with the calibration of the plant for the JMF. It should be recognized that the aggregates produced by the plant may not satisfy the gradation requirements or produce a mix that exactly meets the JMF. In those instances, it will be necessary to reevaluate and redesign the mix using plant-produced aggregates. Specimens should be prepared and the optimum bitumen content determined in the same manner as for the original design tests.

401-3.5 TESTING LABORATORY. The laboratory used to develop the JMF shall meet the requirements of ASTM D 3666. A certification signed by the manager of the laboratory stating that it meets these requirements shall be submitted to the Engineer prior to the start of construction. The certification shall contain as a minimum:

- Qualifications of personnel; laboratory manager, supervising technician, and testing technicians.

- A listing of equipment to be used in developing the job mix.

- A copy of the laboratory's quality control system.

- Evidence of participation in the AASHTO Materials Reference Laboratory (AMRL) program

CONSTRUCTION METHODS

401-4.1 WEATHER LIMITATIONS. The bituminous mixture shall not be placed upon a wet surface or when the surface temperature of the underlying course is less than specified in Table 4. The temperature requirements may be waived by the Engineer, if requested; however, all other requirements including compaction shall be met.

TABLE 4.    BASE TEMPERATURE LIMITATIONS

| Mat Thickness | Base Temperature (Minimum) |
| --- | --- |
| 3 inches or greater | 40 °F |
| Greater than 1 inch but less than 3 inches | 42 °F |
| 1 inch or less | 50 °F |

401-4.2 BITUMINOUS MIXING PLANT. Plants used for the preparation of bituminous mixtures shall conform to the requirements of ASTM D 995 with the following changes:

a.	Requirements for All Plants.

- Truck Scales. The bituminous mixture shall be weighed on approved scales furnished by the Contractor, or on certified public scales at the Contractor's expense. Scales shall be inspected and sealed as often as the Engineer deems necessary to assure their accuracy. Scales shall conform to the requirements of Item G-130-2.5.

- Testing Facilities. The Contractor shall provide laboratory facilities at the plant or job site for the Contractor's quality control testing, in accordance with paragraph 401-6.2.

- Inspection of Plant. The Engineer, or Engineer's authorized representative, shall have access, at all times, to all areas of the plant for checking adequacy of equipment; inspecting operation of the plant: verifying weights, proportions, and material properties; and checking the temperatures maintained in the preparation of the mixtures.

- Storage Bins and Surge Bins. Paragraph 4.9 of ASTM D 995 is deleted. Instead, the following applies. Use of surge bins or storage bins for temporary storage of hot bituminous mixtures will be permitted as follows:

- The bituminous mixture may be stored in surge bins for not longer than 3 hours.

- The bituminous mixture may be stored in insulated storage bins for not longer than 24 hours.

The bins shall be such that mix drawn from them meets the same requirements as mix loaded directly into trucks.

If the Engineer determines that there is an excessive amount of heat loss, segregation or oxidation of the mixture due to temporary storage, no overnight storage will be allowed.

401-4.3 HAULING EQUIPMENT. Trucks used for hauling bituminous mixtures shall have tight, clean, and smooth metal beds. To prevent the mixture from adhering to them, the truck beds shall be lightly coated with a minimum amount of paraffin oil, lime solution, or other approved material. Each truck shall have a suitable cover to protect the mixture from adverse weather. When necessary, to ensure that the mixture will be delivered to the site at the specified temperature, truck beds shall be insulated or heated and covers shall be securely fastened.

401-4.4 BITUMINOUS PAVERS. Bituminous pavers shall be self-propelled, with an activated screed, heated as necessary, and shall be capable spreading and finishing courses of bituminous plant mix material which will meet the specified thickness, smoothness, and grade. The paver shall have sufficient power to propel itself and the hauling equipment without adversely affecting the finished surface.

The paver shall have a receiving hopper of sufficient capacity to permit a uniform spreading operation. The hopper shall be equipped with a distribution system to place the mixture uniformly in front of the screed without segregation. The screed shall effectively produce a finished surface of the required evenness and texture without tearing, shoving, or gouging the mixture.

If an automatic grade control device is used, the paver shall be equipped with a control system capable of automatically maintaining the specified screed elevation. The control system shall be automatically actuated from either a reference line and/or through a system of mechanical sensors or sensor-directed mechanisms or devices which will maintain the paver screed at a predetermined transverse slope and at the proper elevation to obtain the required surface. The transverse slope controller shall be capable of maintaining the screed at the desired slope within plus or minus 0.1%.

The controls shall be capable of working in conjunction with any of the following attachments:

- Ski-type device of not less than 30 feet in length.

- Taut stringline (wire) set to grade.

- Short ski or shoe.

- Laser control.

401-4.5 ROLLERS. Rollers of the vibratory, steel wheel, and pneumatic-tired type shall be used. They shall be in good condition, capable of operating at slow speeds to avoid displacement of the bituminous mixture. The number, type, and weight of rollers shall be sufficient to compact the mixture to the required density while it is still in a workable condition.

The use of equipment which causes excessive crushing of the aggregate will not be permitted.

401-4.6 PREPARATION OF BITUMINOUS MATERIAL. The bituminous material shall be heated in a manner that will avoid local overheating and provide a continuous supply of the bituminous material to the mixer at a uniform temperature. The temperature of the bituminous material delivered to the mixer shall be sufficient to provide a suitable viscosity for adequate coating of the aggregate particles, but shall not exceed 325 °F.

401-4.7 PREPARATION OF MINERAL AGGREGATE. The aggregate for the mixture shall be heated and dried prior to introduction into the mixer. The maximum temperature and rate of heating shall be such that no damage occurs to the aggregates. The temperature of the aggregate and mineral filler shall not exceed 350 °F when the asphalt is added. Particular care shall be taken that aggregates high in calcium or magnesium content are not damaged by overheating. The temperature shall not be lower than is required to obtain complete coating and uniform distribution on the aggregate particles and to provide a mixture of satisfactory workability.

401-4.8 PREPARATION OF BITUMINOUS MIXTURE. The aggregates and the bituminous material shall be weighed or metered and introduced into the mixer in the amount specified by the JMF.

The combined materials shall be mixed until the aggregate obtains a uniform coating of bitumen and is thoroughly distributed throughout the mixture. Wet mixing time shall be the shortest time that will produce a satisfactory mixture, but not less than 25 seconds for batch plants. The wet mixing time for all plants shall be established by the Contractor, based on the procedure for determining the percentage of coated particles described in ASTM D 2489, for each individual plant and for each type of aggregate used. The wet mixing time will be set to achieve 95% of coated particles. For continuous mix plants, the minimum mixing time shall be determined by dividing the weight of its contents at operating level by the weight of the mixture delivered per second by the mixer. The moisture content of all bituminous mix upon discharge shall not exceed 0.5% of the total weight of mix, as determined by WAQTC TM 6.

401-4.9 PREPARATION OF THE UNDERLYING SURFACE. Immediately before placing the bituminous mixture, the underlying course shall be cleaned of all dust and debris. A prime coat or tack coat shall be applied in accordance with Item P-602 or P-603, if required by the contract Specifications.

401-4.10 TRANSPORTING, PLACING, AND FINISHING. The bituminous mixture shall be transported from the mixing plant to the site in vehicles conforming to the requirements of paragraph 401-4.3. Deliveries shall be scheduled so that placing and compacting of mixture is uniform with minimum stopping and starting of the paver. Adequate artificial lighting shall be provided for night placements. Hauling over freshly placed material shall not be permitted until the material has been compacted, as specified, and allowed to cool to atmospheric temperature.

The Contractor may elect to use a material transfer vehicle to deliver mix to the paver.

The mix shall be placed and compacted at a temperature not less than 235 °F.

Upon arrival, the mixture shall be placed to the full width by a bituminous paver. It shall be struck off in a uniform layer of such depth that, when the work is completed, it shall have the required thickness and conform to the grade and contour indicated. The speed of the paver shall be regulated to eliminate pulling and tearing of the bituminous mat. Unless otherwise permitted, placement of the mixture shall begin along the centerline of a crowned section or on the high side of areas with a one-way slope. The mixture shall be placed in consecutive adjacent strips having a minimum width of 20 feet except where edge lanes require less width to complete the area. The longitudinal joint in one course shall offset the longitudinal joint in the course immediately below by at least 12 inches; however, the joint in the surface top course shall be at the centerline of the pavement. Transverse joints in one course shall be offset by at least 10 feet from transverse joints in the previous course.

Transverse joints in adjacent lanes shall be offset a minimum of 10 feet.

On areas where irregularities or unavoidable obstacles make the use of mechanical spreading and finishing equipment impractical, the mixture may be spread and compacted by hand tools.

401-4.11 COMPACTION OF MIXTURE. After placing, the mixture shall be thoroughly and uniformly compacted by rolling. The surface shall be compacted as soon as possible when the mixture has attained sufficient stability so that the rolling does not cause undue displacement, cracking or shoving. The sequence of rolling operations and the type of rollers used shall be at the discretion of the Contractor. The speed of the roller shall, at all times, be sufficiently slow to avoid displacement of the hot mixture and be effective in compaction. Any displacement occurring as a result of reversing the direction of the roller, or from any other cause, shall be corrected at once.

Sufficient rollers shall be furnished to handle the output of the plant. Rolling shall continue until the surface is of uniform texture, true to grade and cross section, and the required field density is obtained.

To prevent adhesion of the mixture to the roller, the wheels shall be kept properly moistened (and scrapers used), but excessive water will not be permitted.

In areas not accessible to the roller, the mixture shall be thoroughly compacted with hand tampers.

Any mixture that becomes loose and broken, mixed with dirt, contains check-cracking, or in any way defective shall be removed and replaced with fresh hot mixture and immediately compacted to conform to the surrounding area. This work shall be done at the Contractor's expense. Skin patching shall not be allowed.

401-4.12 JOINTS. The formation of all joints shall be made in such a manner as to ensure a continuous bond between the courses and obtain the required density. All joints shall have the same texture as other sections of the course and meet the requirements for smoothness and grade.

The roller shall not pass over the unprotected end of the freshly laid mixture except when necessary to form a transverse joint. When necessary to form a transverse joint, it shall be made by means of placing a bulkhead or by tapering the course. The tapered edge shall be cut back to its full depth and width on a straight line to expose a vertical face prior to placing the adjacent lane. In both methods, all contact surfaces shall be given a tack coat of bituminous material before placing any fresh mixture against the joint.

All longitudinal joints that have become cold (less than 150 (F) shall be cut back with a cutter mounted on the outside of a power roller as approved by the engineer. After being cut back, the joint will be brushed with a power broom as directed by the engineer to remove all loose asphalt concrete. To ensure a continuous bond between all pavement joints, a tack coat shall be applied to the joint prior to the laydown of the asphalt concrete.

MATERIAL ACCEPTANCE

401-5.1 ACCEPTANCE SAMPLING AND TESTING. All acceptance sampling and testing necessary to determine conformance with the requirements specified in this section will be performed by the Engineer at no cost to the Contractor. Testing organizations performing these tests will meet the requirements of ASTM D 3666.

The quantity of each type of asphalt concrete mixture produced and placed will be divided into lots and the lots evaluated individually for acceptance. The Department has the exclusive right and responsibility for determining the acceptability of all materials incorporated into the project. The results of the acceptance testing performed by the Engineer will be made available to the Contractor within 7 working days from the date of sampling.

A lot will normally be 2,000 tons. The lot will be divided into 5 equal sublots of 400 tons, each randomly sampled and tested for asphalt cement content, density and gradation in accordance with this subsection.

If the total project quantity is between 900 tons and 1,999 tons, the total project quantity will be considered one lot. The lot will be divided into 5 equal sublots and randomly sampled for asphalt cement content, density and gradation in accordance with this subsection. The Engineer will select one sample for every 900 tons of mix, or majority portion thereof, for testing. If the test result(s) conform to the specification limits, the lot will be accepted. If any of the test results fail to conform to specification limits, the remaining samples will be tested and the lot evaluated for price adjustment in accordance with Subsection 401-5.2.

If the total project quantity is less than 900 tons, asphalt concrete pavement will be accepted for payment based on the Engineer's approval of a Job Mix Formula and the placement and compaction of the asphalt concrete pavement to the specified depth and finished surface requirements and tolerances. Any area of finished surfacing that is segregated, fails to meet surface tolerance requirements, cools to below 170 °F prior to completing compaction, or is any other way defective shall be removed and replaced with new asphalt concrete pavement. Removal and replacement of defective pavement shall be at no additional cost to the Department.

If the project has more than 1 lot and if less than 5 sublots have been sampled at the time a lot is terminated, the material in the shortened lot will be included as part of the prior lot and the price adjustment computed for the prior lot will include the samples from the shortened lot.

The lot size for joint density will be the total length of longitudinal joints constructed by a lot of material for the mat completing the joint.

- Sampling.

- Cement Content. Samples taken for the determination of asphalt cement content will be taken from behind the screed prior to initial compaction, from the end of the auger, or from two core samples (minimum diameter of 8 inches) cut from each sublot, randomly in accordance with the procedures contained in ASTM D 3665.

- Gradation. Samples taken for the determination of aggregate gradation will be either of the following as directed by the Engineer, randomly in accordance with the procedures contained in ASTM D 3665.

- The same as specified for the determination of asphalt cement content.

- From the combined aggregate cold feed conveyor via a diversion chute or from the stopped conveyor belt.

On drum mix plants a diverter device for obtaining aggregate samples shall be located on the conveyor system delivering combined aggregates into the drum. The diverter device shall divert aggregate from the full width of the conveyor system and shall be maintained to provide a representative sample of aggregate incorporated in the mix. The plant shall be equipped with a safe and suitable location for obtaining aggregate samples from the diverter device.

- Dry batched aggregates.

- Density. The Contractor shall cut one full depth core sample with a minimum diameter of 6 inches from each sublot, within 24 hours of final rolling for density acceptance testing. The samples shall be neatly cut by a core drill at the randomly selected location designated by the Engineer in accordance with the procedures contained in ASTM D 3665. All voids left by sampling shall be backfilled with new asphalt concrete material and compacted within 24 hours of sampling.

Cores for mat density shall not be taken closer than 1 foot from a transverse or longitudinal joint.

Cores for joint density shall be taken directly on the joint, at locations adjacent to cores taken from the mat completing the joint.

- Testing.

- Cement Content. Asphalt cement content will be determined by WAQTC TM 4 or WAQTC FOP for AASHTO T 308, by total weight of mix.

- Gradation. Cold feed aggregate gradations will be tested in accordance with WAQTC FOP for AASHTO T 27 and T 11 or WAQTC FOP for AASHTO T 30 and evaluated for acceptance in accordance with Subsection 401-5.2. Asphalt concrete mix and core sample gradations will be determined in accordance with WAQTC FOP for AASHTO T 30 from extracted aggregate, or aggregate remaining after the ignition oven (WAQTC FOP for AASHTO T 308) has burned off the asphalt cement.

- Density. The Target Value for mat density shall be 94% of the theoretical MSG as determined by ASTM D 2041, Type C, D, or E container. For the first lot of asphalt concrete pavement, the MSG will be determined by the Job Mix Formula. For additional lots, the MSG will be determined from the randomly selected sample from the first sublot. For joint density lots, the MSG will be MSG of the adjacent mat lot completing the joint. The Target Value for joint density shall be 93% of the theoretical MSG as determined by ASTM D 2041, Type C, D, or E container.

Core samples will be tested for BSG in accordance with ASTM D 2726 or ASTM D 3203 whichever is applicable, and evaluated for acceptance in accordance with Subsection 401-5.2. The relative density equals the BSG times 100 divided by the maximum specific gravity for the lot and rounded to the nearest whole percent.

401-5.2 ACCEPTANCE CRITERIA.

- General. Acceptance will be based on the following characteristics of the bituminous mixture and completed pavement as well as the implementation of the Contractor's Quality Control plan and test results:

- Aggregate gradation

- Asphalt content

- Mat density

- Joint density

- Thickness

- Smoothness

- Grade

Aggregate gradation, asphalt content, mat density, and joint density will be evaluated for acceptance on a lot basis using the method of estimating percentage of material within specification limits (PWL). Acceptance using PWL considers the variability (standard deviation) of the material and the testing procedures, as well as the average (mean) value of the test results to calculate the percentage of material that is above the lower specification tolerance limit (L) or below the upper specification tolerance limit (U).

Thickness will be evaluated by the Engineer for compliance in accordance with paragraph 401-5.2.f(4). Acceptance for smoothness will be based on the criteria contained in paragraph 401-5.2f(5). Acceptance for grade will be based on the criteria contained in paragraph 401-5.2f(6).

The Engineer may at any time, not withstanding previous plant acceptance, reject and require the Contractor to dispose of any batch of bituminous mixture which is rendered unfit for use due to contamination, segregation, incomplete coating of aggregate, or improper mix temperature. Such rejection may be based on only visual inspection or temperature measurements. In the event of such rejection, the Contractor may take a representative sample of the rejected material in the presence of the Engineer, and, if it can be demonstrated in the laboratory, in the presence of the Engineer, that such material was erroneously rejected, payment will be made for the material at the contract unit price.

- Aggregate Gradation, Asphalt Content. Evaluation for acceptance of each lot of plant-produced material for aggregate gradation and asphalt content will be based on PWL.

- Mat Density. Evaluation for acceptance of each lot of in-place pavement for mat density will be based on PWL.

- Joint Density. Evaluation for acceptance of each lot of in-place pavement for joint density will be based on PWL.

- Percentage of Material Within Specification Limits (PWL). The PWL will be determined in accordance with procedures specified in Section 110 of the General Provisions. The sample average (X) is rounded to the nearest tenth for density and all sieves except the No. 200, and to the nearest hundredth for asphalt cement content and the No. 200 sieve. The sample standard deviation (Sn) is rounded to the nearest hundredth for density and all sieve sizes except the No. 200 sieve. The sample standard deviation (Sn) is rounded to the nearest .001 for asphalt content and the No. 200 sieve. The specification tolerance limits (L) and (U) are contained in Table 5.

- Acceptance Criteria.

- Mat Density, Aggregate Gradation, and Asphalt Content. Acceptance and payment for the lot will be determined in accordance with paragraph 401-8.1.

- Intentionally left blank

- Joint Density. If the PWL of the lot equals or exceeds 90%, the lot will be acceptable. If the PWL is less than 90%, the Contractor shall evaluate the method of compacting joints. If the PWL is below 80%, the Contractor shall stop production until the reason for poor compaction can be determined.

- Thickness. Thickness will be evaluated for compliance by the Engineer to the requirements shown on the Plans. Measurements of thickness will be made by the Engineer using the cores extracted from the mat for each sublot for density measurement.

- Smoothness. The finished surfaces of the pavement shall not vary more than 1/4 inch for the surface course. Each lot will be evaluated with a 12-foot straightedge. The lot size will be 2000 yd2. Measurements will be made perpendicular and parallel to the centerline at distances not to exceed 50 feet. When more than 15% of all measurements within a lot exceed the specified tolerance, the Contractor shall remove the deficient area and replace with new material. Sufficient material shall be removed to allow at least 1 inch of asphalt concrete to be placed. Skin patching will not be permitted. High points may be ground off.

- Grade. The finished surface of the pavement shall not vary from the gradeline elevations and cross sections shown on the Plans by more than 0.05 foot. The finished grade of each lot will be determined by running levels at intervals of 50 feet or less longitudinally and transversely to determine the elevation of the completed pavement. The lot size will be 2000 yd2. When more than 15% of all the measurements within a lot are outside the specified tolerance, the Contractor shall remove the deficient area and replace with new material. Sufficient material shall be removed to allow at least 1 inch of asphalt concrete to be placed. Skin patching for correcting low areas will not be permitted. High points may be ground off.

- Outliers. All individual tests for asphalt content, aggregate gradation, and mat and joint density will be checked for outliers (test criterion) in accordance with ATM SP-7. Outliers will be discarded, and the PWL will be determined using the remaining test values.

If any sieve size on a gradation test or the asphalt cement content is an outlier, then the gradation test results and the asphalt cement content results for that sample will not be included in the price adjustment. The density test result for that sample will be included in the price adjustment provided it is not an outlier also.

If the density test result is an outlier, the density test result will not be included in the price adjustment, however, the gradation and asphalt cement content results for that sample will be included provided neither is an outlier.

TABLE 5.    LOWER SPECIFICATION TOLERANCE LIMIT (L)

AND UPPER SPECIFICATION TOLERANCE LIMIT (U)

| Measured Characteristics | L | U |
| --- | --- | --- |
| 3/4 in. | TV -6.0 | TV +6.0 |
| 1/2 in. | TV -6.0 | TV +6.0 |
| 3/8 in. | TV -6.0 | TV +6.0 |
| No. 4 | TV -6.0 | TV +6.0 |
| No. 8 | TV -6.0 | TV +6.0 |
| No. 16 | TV -5.0 | TV +5.0 |
| No. 30 | TV -4.0 | TV +4.0 |
| No. 50 | TV -4.0 | TV +4.0 |
| No. 100 | TV-3.0 | TV +3.0 |
| No. 200 | TV-2.0 | TV +2.0 |
| Asphalt % | TV-0.4 | TV+0.4 |
| Mat Density | 92% | 98% |
| Joint Density | 91% | 98% |

TV (Target Value) = Job Mix Formula value for gradation and asphalt cement content

401-5.3 RETESTS.

- General. Retesting of a sample of pavement, which is outside the limits specified in Table 5, will be allowed if requested by the Contractor, in writing, within 7 days after receiving the written test results from the Engineer. Only one retest per lot will be permitted. The Engineer will select the sample location for the retest. The original test result will be discarded and the retest result will be used in the price adjustment calculation regardless of whether the retest result gives a higher or lower pay factor.

- A redefined PWL will be calculated for the lot.

- The cost for resampling shall be borne by the Contractor.

- Payment for Resampled Lots. The redefined PWL for a lot will be used to calculate the payment for that lot in accordance with Table 6.

401-5.4 LEVELING COURSE. Any course used for truing and leveling shall meet the requirements of paragraph 401-3.2 and 5.2b, but will not be subject to the density requirements of paragraph 401-5.2c and d. The leveling course shall be compacted with the same effort used to achieve density of the test section. The truing and leveling course shall not exceed a nominal thickness of 1-1/2 inches.

CONTRACTOR QUALITY CONTROL

401-6.1 GENERAL. The Contractor shall develop a Quality Control Program in accordance with Section 100 of the General Provisions. The program shall address all elements which affect the quality of the pavement including, but not limited to:

| a. Mix Design | f. Mixing and Transportation |
| --- | --- |
| b. Aggregate Grading | g. Placing and Finishing |
| c. Quality of Materials | h. Joints |
| d. Stockpile Management | i. Compaction |
| e. Proportioning | j. Surface smoothness |

401-6.2 TESTING LABORATORY. The Contractor shall provide a fully equipped asphalt laboratory located at the plant or job site.

The effective working area of the laboratory shall be a minimum of 150 ft2 with a ceiling height of not less than 7.5 feet. Lighting shall be adequate to illuminate all working areas. It shall be equipped with heating and air conditioning units to maintain a temperature of 70 °F ± 5 °F.

Laboratory facilities shall be kept clean and all equipment shall be maintained in proper working condition. The Engineer shall be permitted unrestricted access to inspect the Contractor's laboratory facility and witness quality control activities. The Engineer will advise the Contractor in writing of any noted deficiencies concerning the laboratory facility, equipment, supplies, or testing personnel and procedures. When the deficiencies are serious enough to be adversely affecting test results, the incorporation of the materials into the work will be suspended immediately and will not be permitted to resume until the deficiencies are satisfactorily corrected.

401-6.3 QUALITY CONTROL TESTING. The Contractor shall perform all quality control tests necessary to control the production and construction processes applicable to these Specifications and as set forth in the Quality Control Program. The testing program shall include, but not necessarily limited to, tests for the control of asphalt content, aggregate gradation, temperatures, aggregate moisture, field compaction, and surface smoothness. A Quality Control Testing Plan shall be developed as part of the Quality Control Program.

- Asphalt Content. A minimum of 2 asphalt cement content tests shall be performed per lot in accordance with Subsection 401-5.1b(1).

- Gradation. Aggregate gradations shall be determined a minimum of twice per lot from mechanical analysis of aggregate in accordance with WAQTC FOP for AASHTO T 30 and WAQTC FOP for AASHTO T 27 and T 11. When asphalt content is determined by the nuclear method, aggregate gradation shall be determined from hot bin samples on batch plants, or from the cold feed on drum mix or continuous mix plants, and tested in accordance with WAQTC FOP for AASHTO T 27 and T 11 using actual batch weights to determine the combined aggregate gradation of the mixture.

- Moisture Content of Aggregate. The moisture content of aggregate used for production shall be determined a minimum of once per lot in accordance with ASTM C 566.

- Moisture Content of Mixture. The moisture content of the mixture shall be determined once per lot in accordance with ASTM D 1461 or WAQTC TM 6.

- Temperatures. Temperatures shall be checked, at least 4 times per lot, at necessary locations to determine the temperatures of the dryer, the bitumen in the storage tank, the mixture at the plant, and the mixture at the job site.

- In-Place Density Monitoring. The Contractor shall conduct any necessary testing to ensure that the specified density is being achieved. A nuclear gauge may be used to monitor the pavement density in accordance with ASTM D 2950.

- Additional Testing. Any additional testing that the Contractor deems necessary to control the process may be performed at the Contractor's option.

- Monitoring. The Engineer reserves the right to monitor any or all of the above testing.

401-6.4 SAMPLING. When directed by the Engineer, the Contractor shall sample and test any material which appears inconsistent with similar material being sampled, unless such material is voluntarily removed and replaced or deficiencies corrected by the Contractor. All sampling shall be in accordance with standard procedures specified.

401-6.5 CONTROL CHARTS. The Contractor shall maintain linear control charts both for individual measurements and range (i.e., difference between highest and lowest measurements) for aggregate gradation and asphalt content.

Control charts shall be posted in a location satisfactory to the Engineer and shall be kept current. As a minimum, the control charts shall identify the project number, the contract item number, the test number, each test parameter, the Action and Suspension Limits applicable to each test parameter, and the Contractor's test results. The Contractor shall use the control charts as part of a process control system for identifying potential problems and assignable causes before they occur. If the Contractor's projected data during production indicates a problem and the Contractor is not taking satisfactory corrective action, the Engineer may suspend production or acceptance of the material.

- Individual Measurements. Control charts for individual measurements shall be established to maintain process control within tolerance for aggregate gradation and asphalt content. The control charts shall use the JMF Target values as indicators of central tendency for the following test parameters with associated Action and Suspension Limits:

CONTROL CHART LIMITS FOR INDIVIDUAL MEASUREMENTS

| Sieve | Action Limit | Suspension Limit |
| --- | --- | --- |
| 3/4 in. | 0% | 0% |
| 1/2 in. | +/-6% | +/-9% |
| 3/8 in. | +/-6% | +/-9% |
| No. 4 | +/-6% | +/-9% |
| No. 16 | +/-5% | +/-7.5% |
| No. 50 | +/-3% | +/-4.5% |
| No. 200 | +/-2% | +/-3% |
| Asphalt Content | +/-0.45% | +/-0.70% |

- Range. Control charts for range shall be established to control process variability for the test parameters and Suspension Limits listed below. The range shall be computed for each lot as the difference between the two test results for each control parameter. The Suspension Limits specified below are based on a sample size of n = 2. Should the Contractor elect to perform more than 2 tests per lot, the Suspension Limits shall be adjusted by multiplying the Suspension Limit by 1.18 for n = 3 and by 1.27 for n = 4.

CONTROL CHART LIMITS BASED ON RANGE

(Based on n = 2)

| Sieve | Suspension Limit |
| --- | --- |
| 1/5 in. | 11% |
| 3/8 in. | 11% |
| No. 4 | 11% |
| No. 16 | 9% |
| No. 50 | 6% |
| No. 200 | 3.5% |
| Asphalt Content | 0.8% |

- Corrective Action. The Quality Control Plan shall indicate that appropriate action shall be taken when the process is believed to be out of tolerance. The Plan shall contain sets of rules to gauge when a process is out of control and detail what action will be taken to bring the process into control. As a minimum, a process shall be deemed out of control and production stopped and corrective action taken, if:

- One point falls outside the Suspension Limit line for individual measurements or range; or

- Two points in a row fall outside the Action Limit line for individual measurements.

METHOD OF MEASUREMENT

401-7.1 MEASUREMENT. Bituminous Mixture will be measured by the number of tons used in the accepted work, based on recorded truck scale weights. No deduction will be made for the weight of asphalt cement in the mixture.

Bituminous Material will be measured by the number of tons of asphalt cement used in the accepted pavement determined as follows:

The method of measurement to be used will be based on one of the following procedures. The Engineer will select in writing the procedure to be used.

- Supplier's invoices minus waste, diversion and excess left over. This method may be used on projects where deliveries are made in sealed tankers and the plant is producing material for one project only. Method b. will be used to compute left over. Waste and diversion will be computed in a manner to be determined by the Engineer.

- Volume measure (tank stickings) of actual daily uses. It is the Contractor's responsibility to notify the Engineer whenever material is to be added to the calibrated volume measure or whenever material from the volume measure is to be used for work other than that specified in this contract.

- Percent of asphalt cement for each sublot as determined by WAQTC TM 4 or WAQTC FOP for AASHTO T 308 multiplied by the weight represented by that sublot.

Whichever method is used must be used for the duration of the project. Another method may be used and computed as a check, but only one method will be used for payment computation.

## BASIS OF PAYMENT

401-8.1 PAYMENT. Payment for an accepted lot of bituminous concrete pavement will be made at the contract unit price per ton for bituminous mixture and bituminous material adjusted according to paragraph 401-8.1a.

The price shall be compensation for furnishing all materials, for all preparation, mixing, and placing of these materials, and for all labor, equipment, tools, and incidentals necessary to complete the item.

- Basis of Adjusted Payment. The Asphalt Price Adjustment will be the sum of the price adjustments for each lot.The lot Pay Factors for density, gradation and asphalt cement content are determined from Table 6 using Percent Within Limits (PWL) calculated from Section 110 of the General Provisions. The maximum pay factor for the largest sieve size for gradation will be 1.00. The price adjustment will be based on the Composite Pay Factor (CPF) for asphalt content and aggregate gradation or the Density Pay Factor (DPF) whichever is the lowest value. CPF and DPF is rounded to the nearest hundredth. Table 7 is used to determine the weight factor (f) for each sieve size and asphalt content.

The asphalt concrete mixture Composite Pay Factor (CPF) is computed for asphalt cement content and all sieves using the following formula:

CPF =

TABLE 6.    PRICE ADJUSTMENT SCHEDULE

| Percentage of Material Within the Specification Limit (PWL) | Pay Factor (PF) |
| --- | --- |
| 96-100 | 1.05 |
| 90-95 | 0.01 PWL + 0.10 |
| 75-89 | 0.005 PWL + 0.55 |
| 55-74 | 0.014 PWL - 0.12 |
| Below 55 | 0* |

* If the Composite Pay Factor or the Density Pay Factor falls below 0.65, the lot shall be removed and replaced. However, the Engineer may decide to allow the deficient lot to remain in place. In that case, if the Engineer and Contractor agree in writing that the lot shall not be removed, the Pay Factor for the lot shall be 0.50.

TABLE 7.    WEIGHT FACTORS

| Sieve Size | Factor “ f “ |
| --- | --- |
| 3/4 in. | 4 |
| 1/2 in. | 5 |
| 3/8 in. | 5 |
| No. 4 | 4 |
| No. 8 | 4 |
| No. 16 | 4 |
| No. 30 | 5 |
| No. 50 | 5 |
| No. 100 | 4 |
| No. 200 | 20 |
| Asphalt % | 40 |

The price adjustment for each individual lot will be calculated as follows:

Price Adjustment = [(CPF or DPF)*-1] x (tons in lot) x (PAB)

PAB = Price Adjustment Base = $40.00 per ton

* Composite Pay Factor (CPF) or Density Pay Factor (DPF) whichever is lower value.

- Payment. Payment will be made under:

Item P-401a 	Bituminous Mixture - per ton

Item P-401b 	Bituminous Price Adjustment - contingent sum

Item P-401c 	Bituminous Material [ Grade ] - per ton

Item P-401d 	Bituminous Treated Base - per ton

TESTING REQUIREMENTS

WAQTC FOP for AASHTO T 27 and T 11	Coarse and Fine Aggregate Gradation

WAQTC FOP for AASHTO T 30	Mechanical Analysis of Extracted Aggregate

WAQTC FOP for AASHTO T 308	Determining the Asphalt Concrete of Hot Mix Asphalt (HMA) by Ignition Method

ATM 313	Aggregate Degradation

ATM 417	Marshal Mix Design

ATM SP-7	Outliers

WAQTC TM 1	Determining the Percentage of Fracture in Coarse Aggregate

WAQTC TM 4	Asphalt Binder Content of Bituminous Mixtures by the Nuclear Method

WAQTC TM 6	Moisture Content of Bituminous Mixes by Oven

ASTM C 88	Soundness of Aggregates by Use of Sodium Sulfate or Magnesium Sulfate

ASTM C 117	Materials Finer than 75-um (No.200) Sieve in Mineral Aggregates by Washing

ASTM C 131	Resistance to Abrasion of Small Size Coarse Aggregate by Use of the Los Angeles Machine

ASTM C 136 	Sieve or Screen Analysis of Fine and Coarse Aggregates

ASTM C 183 	Sampling Hydraulic Cement

ASTM C 566 	Total Moisture Content of Aggregate by Drying

ASTM D 75 	Sampling Aggregates

ASTM D 995	Requirements for Mixing Plants for Hot-Mixed Hot-Laid Bituminous Paving Mixtures

ASTM D 1461	Moisture or Volatile Distillates in Bituminous Paving Mixtures

ASTM D 2041	Theoretical Maximum Specific Gravity and Density of Bituminous Paving Mixtures

ASTM D 2419	Sand Equivalent Value of Soils and Fine Aggregate

ASTM D 2489	Degree of Particle Coating of Bituminous-Aggregate Mixtures

ASTM D 2726	Bulk Specific Gravity of Compacted Bituminous Mixtures Using Saturated Surface-Dry Specimens

ASTM D 3203	Percent Air Voids in Compacted Dense and Open Bituminous Paving Mixtures

ASTM D 2950	Density of Bituminous Concrete in Place by Nuclear Method

ASTM D 3665	Random Sampling of Paving Materials

ASTM D 3666	Inspection and Testing Agencies for Bituminous Paving Materials

ASTM D 4318	Liquid Limit, Plastic Limit, and Plasticity Index of Soils

ASTM D 4791	Flat or Elongated Particles in Coarse Aggregate

ASTM D 4867	Effect of Moisture on Asphalt Concrete Paving Mixtures

ASTM E 178	Practice for Dealing With Outlying Observations

The Asphalt Institute	Mix Design Methods for Asphalt Concrete Manual No. 2 (MS-2)

The Asphalt Institute	Hot-Mix Recycling Manual No. 20 (MS-20)

MATERIAL REQUIREMENTS

ASTM D 242	Mineral Filler for Bituminous Paving Mixtures

ASTM D 3381	Viscosity-Graded Asphalt Cement for Use in Pavement Construction

ASTM D 4552	Classifying Hot-Mix Recycling Agents

PART VI - RIGID PAVEMENT

ITEM P-501 PORTLAND CEMENT CONCRETE PAVEMENT

DESCRIPTION

501-1.1 This work shall consist of pavement composed of portland cement concrete, without reinforcement, constructed on a prepared underlying surface in accordance with these specifications and shall conform to the lines, grades, thickness, and typical cross sections shown on the Plans.

MATERIALS

501-2.1 AGGREGATES.

- Fine Aggregate. Fine aggregate shall conform to the requirements of ASTM C 33. Gradation shall meet the requirements of Table 1 when tested in accordance with ASTM C 136, except as may otherwise be qualified under Section 6 of ASTM C 33.

TABLE 1.    GRADATION FOR FINE AGGREGATE

| Sieve Designation (square openings) | Percentage by Weight Passing Sieves |
| --- | --- |
| 3/8 in. | 100 |
| No. 4 | 95-100 |
| No. 8 | 80-100 |
| No. 16 | 50-85 |
| No. 30 | 25-60 |
| No. 50 | 5-30 |
| No. 100 | 0-10 |

- Coarse Aggregate. Coarse aggregate shall conform to the requirements of ASTM C 33. Gradation, within the separated size groups, shall meet the requirements of Table 2 when tested in accordance with ASTM C 136.

Aggregates delivered to the mixer shall consist of crushed stone, crushed or uncrushed gravel, crushed recycled concrete pavement, or a combination thereof. The aggregate shall be composed of clean, hard, uncoated particles and shall meet the requirements for deleterious substances contained in ASTM C 33, Class 4S. Dust and other coating shall be removed from the aggregates by washing, if necessary. The aggregate in any size group shall not contain more than 8% by weight of flat or elongated pieces when tested in accordance with ASTM D 4791. A flat or elongated particle is one having a ratio between the maximum and the minimum dimensions of a circumscribing rectangular prism exceeding 5 to 1. The percentage of wear shall be no more than 40 when tested in accordance with ASTM C 131 or ASTM C 535.

TABLE 2.    GRADATION FOR COARSE AGGREGATE

| Sieve Designations (square openings) | Percentage by Weight Passing Sieves |
| --- | --- |
| 1-1/2 in. | 100 |  |
| 1 in. | 95-100 | 100 |
| 3/4 in. |  | 90-100 |
| 1/2 in. | 25-60 |  |
| 3/8 in. |  | 20-55 |
| No. 4 | 0-10 | 0-10 |
| No. 8 | 0-5 | 0-5 |

501-2.2 CEMENT. Cement shall conform to the requirements of ASTM C 150 Type I, II, or III including the low-alkali requirement shown in Table 2 of ASTM C 150.

If for any reason, cement becomes partially set or contains lumps of caked cement, it shall be rejected. Cement salvaged from discarded or used bags shall not be used.

501-2.3 CEMENTITIOUS MATERIALS. Fly ash shall meet the requirements of ASTM C 618, Class C, F, or N with the exception of loss of ignition, where the maximum shall be less than 6% for Class F or N. The supplementary optional chemical and physical properties of Tables 1A and 2A contained in ASTM C 618 shall apply.

501-2.4 PREMOLDED JOINT FILLER. Premolded joint filler for expansion joints shall conform to the requirements of ASTM D 1751 and shall be punched to admit the dowels where called for on the Plans. The filler for each joint shall be furnished in a single piece for the full depth and width required for the joint, unless otherwise specified by the Engineer. When the use of more than one piece is required for a joint, the abutting ends shall be fastened securely and held accurately to shape by stapling or other positive fastening means satisfactory to the Engineer.

501-2.5 JOINT SEALER. The joint sealer for the joints in the concrete pavement shall meet the requirements of Item P-605 and shall be of the type(s) specified in the Plans.

501-2.6 STEEL REINFORCEMENT. Reinforcing shall consist of Welded Steel Wire Fabric conforming to the requirements of ASTM A 185. Welded wire fabric shall be furnished in flat sheets only.

501-2.7 DOWEL AND TIE BARS. Tie bars shall be deformed steel bars and conform to the requirements of ASTM A 615, ASTM A 616, or ASTM A 617, except that rail steel bars, Grade 50 or 60, shall not be used for tie bars that are to be bent or restraightened during construction. Tie bars designated as Grade 40 in ASTM A 615 can be used for construction requiring bent bars.

Dowel bars shall be plain steel bars conforming to ASTM A 615, ASTM A 616 or ASTM A 617 and shall be free from burring or other deformation restricting slippage in the concrete. High strength dowel bars shall conform to ASTM A 714, Class 2, Type S, Grade I, II or III, Bare Finish. Before delivery to the construction site each dowel bar shall be painted on all surfaces with one coat of paint meeting Federal Specification TT-P-664. If plastic or epoxy-coated steel dowels are used no paint coating is required, except when specified for a particular situation on the contract Plans. Coated dowels shall conform to the requirements of AASHTO M 254.

The sleeves for dowel bars used in expansion joints shall be metal or other type of an approved design to cover 2 to 3 inches of the dowel, with a closed end and with a suitable stop to hold the end of the bar at least 1 inch from the closed end of the sleeve. Sleeves shall be of such design that they will not collapse during construction.

501-2.8 WATER. Water used in mixing or curing shall be clean and free of oil, salt, acid, alkali, sugar, vegetable, or other substances injurious to the finished product. Water will be tested in accordance with the requirements of AASHTO T 26. Water known to be of potable quality may be used without testing.

501-2.9 COVER MATERIAL FOR CURING. Curing materials shall conform to one of the following specifications:

- Liquid membrane-forming compound conforming to ASTM C 309, Type 2, Class B.

- White polyethylene film conforming to ASTM C 171.

- White burlap-polyethylene sheeting conforming to ASTM C 171.

- Waterproof paper conforming to ASTM C 171.

501-2.10 ADMIXTURES. The use of any material added to the concrete mix shall be approved by the Engineer. The Contractor shall submit certificates indicating that the material to be furnished meets all of the requirements indicated below. In addition, the Engineer may require the Contractor to submit complete test data from an approved laboratory showing that the material to be furnished meets all of the requirements of the cited specifications. Subsequent tests may be made of samples taken by the Engineer from the supply of material being furnished or proposed for use on the work to determine whether the admixture is uniform in quality with that approved.

- Air-Entraining Admixtures. Air-entraining admixtures shall meet the requirements of ASTM C 260 and shall consistently entrain the air content in the specified ranges under field conditions. The air-entrainment agent and any chemical admixtures shall be compatible.

- Chemical Admixtures. Water-reducing, set retarding, and set-accelerating admixtures shall meet the requirements of ASTM C 494, including the flexural strength test.

501-2.11 EPOXY-RESIN. Epoxy-resin used to anchor dowels and tie bars in pavements shall conform to the requirements of ASTM C 881, Type I, Grade 3, Class C. Class A or B shall be used when the surface temperature of the hardened concrete is below 60 ºF.

501-2.12 MATERIAL ACCEPTANCE. Prior to use of materials, the Contractor shall submit certified test reports to the Engineer for those materials proposed for use during construction. The certification shall show the appropriate ASTM test(s) for each material, the test results, and a statement that the material passed or failed.

The Engineer may request samples for testing, prior to and during production, to verify the quality of the materials and to ensure conformance with the applicable specifications.

MIX DESIGN

501-3.1 PROPORTIONS. Concrete shall be designed to achieve a 28-day flexural strength of 735 psi. The mix shall be designed using the procedures contained in Chapter 7 of the Portland Cement Association's manual, Design and Control of Concrete Mixtures. Acceptance of the concrete will be based on a flexural strength of 645 psi.

The Contractor shall note that to ensure that the concrete actually produced will meet or exceed the acceptance criteria for the specified strength, the mix design average strength must be higher than the specified strength. The amount of overdesign necessary to meet specification requirements depends on the producer's standard deviation of flexural test results and the accuracy which that value can be estimated from historic data for the same or similar materials.

The minimum cementitious material (cement plus fly ash) shall be 565 lbs/yd3. The ratio of water to cementitious material, including free surface moisture on the aggregates but not including moisture absorbed by the aggregates shall not be more than 0.50 by weight.

Prior to the start of paving operations and after approval of all material to be used in the concrete, the Contractor shall submit a mix design showing the proportions and flexural strength obtained from the concrete at 7 and 28 days. The mix design shall include copies of test reports, including test dates, and a complete list of materials including type, brand, source, and amount of cement, fly ash, coarse aggregate, fine aggregate, water, and admixtures. The fineness modulus of the fine aggregate and the air content shall also be shown. The mix design shall be submitted to the Engineer at least 10 days prior to the start of operations. Production shall not begin until the mix design is approved in writing by the Engineer.

Should a change in sources be made, or admixtures added or deleted from the mix, a new mix design must be submitted to the Engineer for approval.

Flexural strength test specimens shall be prepared in accordance with ASTM C 31 and tested in accordance with ASTM C 78.

501-3.2 CEMENTITIOUS MATERIALS. Fly ash may be used in the mix design. When fly ash is used as a partial replacement for cement, the minimum cement content may be met by considering portland cement plus fly ash as the total cementitious material. The replacement rate shall be determined from laboratory trial mixes, but shall not be less than 10% nor more than 20% by weight of the total cementitious material.

501-3.3 ADMIXTURES.

- Air-Entraining. Air-entraining admixture shall be added in such a manner that will insure uniform distribution of the agent throughout the batch. The air content of freshly mix air-entrained concrete shall be based upon trial mixes with the materials to be used in the work adjusted to produce concrete of the required plasticity and workability. The percentage of air in the mix shall be 5-8. Air content shall be determined by testing in accordance with ASTM C 231 for gravel and stone coarse aggregate and ASTM C 173 for highly porous coarse aggregate.

- Chemical. Water-reducing, set-controlling, and other approved admixtures shall be added to the mix in the manner recommended by the manufacturer and in the amount necessary to comply with the specification requirements. Tests shall be conducted on trial mixes, with the materials to be used in the work, in accordance with ASTM C 494.

501-3.4 TESTING LABORATORY. The laboratory used to develop the mix design shall meet the requirements of ASTM C 1077. A certification that it meets these requirements shall be submitted to the Engineer prior to the start of mix design and shall contain as a minimum:

- Qualifications of personnel; laboratory manager, supervising technician, and testing technicians.

- A statement that the equipment used in developing the mix design is in calibration.

- A statement that each test specified in developing the mix design is offered in the scope of the laboratory's services.

- A copy of the laboratory's quality control system.

CONSTRUCTION METHODS

501-4.1 EQUIPMENT. The Contractor shall furnish all equipment and tools necessary for handling materials and performing all parts of the work.

- Batch Plant and Equipment. The batch plant and equipment shall conform to the requirements of ASTM C 94.

- Mixers and Transportation Equipment.

- General. Concrete may be mixed at a central plant, or wholly or in part in truck mixers. Each mixer shall have attached in a prominent place a manufacturer's nameplate showing the capacity of the drum in terms of volume of mixed concrete and the speed of rotation of the mixing drum or blades.

- Central Plant Mixer. Central plant mixers shall conform to the requirements of ASTM C 94.

The mixer shall be examined daily for changes in condition due to accumulation of hard concrete or mortar or wear of blades. The pickup and throwover blades shall be replaced when they have worn down 3/4 inch or more. The Contractor shall have a copy of the manufacturer's design on hand showing dimensions and arrangement of blades in reference to original height and depth.

- Truck Mixers and Truck Agitators. Truck mixers used for mixing and hauling concrete and truck agitators used for hauling central-mixed concrete shall conform to the requirements of ASTM C 94.

- Nonagitator Trucks. Nonagitating hauling equipment shall conform to the requirements of ASTM C 94.

- Finishing Equipment. The finishing equipment shall be of sufficient weight and power for proper finishing of the concrete. The finishing machine shall be designed and operated to strike off, screed and consolidate the concrete such that laitance on the surface is less than 1/8 inch thick.

- Vibrators. Vibrator shall be either internal type with immersed tube or multiple spuds, or surface type vibrating pan or screed. For pavements 8 inches or more thick, internal vibrators shall be used. They may be attached to the spreader or the finishing machine, or they may be mounted on a separate carriage. Operating frequency for internal vibrators shall be between 8,000 and 12,000 vibrations per minute. Average amplitude for internal vibrators shall be 0.025-0.05 inches. For pavements less than 8 inches thick, vibrating surface pans or screeds shall be allowed. Operating frequencies for surface vibrators shall be between 3,000 and 6,000 vibrations per minute.

The number, spacing, and frequency shall be as necessary to provide a dense and homogeneous pavement. Adequate power to operate all vibrators shall be available on the paver. The vibrators shall be automatically controlled so that they shall be stopped as forward motion ceases.

Hand held vibrators may be used in irregular areas.

- Concrete Saws. The Contractor shall provide sawing equipment adequate in number of units and power to complete the sawing to the required dimensions. The Contractor shall provide at least one standby saw in good working order and a supply of saw blades at the site of the work at all times during sawing operations.

- Side Forms. Straight side forms shall be made of steel and shall be furnished in sections not less than 10 feet in length. Forms shall have a depth equal to the pavement thickness at the edge. Flexible or curved forms of proper radius shall be used for curves of 100 foot radius or less. Forms shall be provided with adequate devices for secure settings so that when in place they will withstand, without visible spring or settlement, the impact and vibration of the consolidating and finishing equipment. Forms with battered top surfaces and bent, twisted or broken forms shall not be used. Built-up forms shall not be used, except as approved by the Engineer. The top face of the form shall not vary from a true plane more than 1/8 inch in 10 feet, and the upstanding leg shall not vary more than 1/4 inch. The forms shall contain provisions for locking the ends of abutting sections together tightly for secure setting. Wood forms may be used under special conditions, when approved by the Engineer.

- Pavers. The paver shall be fully energized, self-propelled, and designed for the specific purpose of placing, consolidating, and finishing the concrete pavement, true to grade, tolerances, and cross section. It shall be of sufficient weight and power to construct the maximum specified concrete paving lane width as shown in the Plans, at adequate forward speed, without transverse, longitudinal or vertical instability or without displacement. The paver shall be equipped with electronic or hydraulic horizontal and vertical control devices.

501-4.2 FORM SETTING. Forms shall be set sufficiently in advance of the concrete placement to insure continuous paving operation. After the forms have been set to correct grade, the underlying surface shall be thoroughly tamped, either mechanically or by hand, at both the inside and outside edges of the base of the forms. Forms shall be staked into place sufficiently to maintain the form in position for the method of placement.

Form sections shall be tightly locked and shall be free from play or movement in any direction. The forms shall not deviate from true line by more than 1/8 inch at any joint. Forms shall be so set that they will withstand, without visible spring or settlement, the impact and vibration of the consolidating and finishing equipment. Forms shall be cleaned and oiled prior to the placing of concrete.

The alignment and grade elevations of the forms shall be checked and corrections made by the Contractor immediately before placing the concrete.

501-4.3 CONDITIONING OF UNDERLYING SURFACE, SLIP-FORM CONSTRUCTION. The compacted underlying surface on which the pavement will be placed shall be widened approximately 3 feet to extend beyond the paving machine track to support the paver without any noticeable displacement. After the underlying surface has been placed and compacted to the required density, the areas which will support the paving machine and the area to be paved shall be trimmed or graded to the plan grade elevation and profile by means of a properly designed machine. The grade of the underlying surface shall be controlled by a positive grade control system using lasers, stringlines, or guide wires. If the density of the underlying surface is disturbed by the trimming operations, it shall be corrected by additional compaction and retested at the option of the Engineer before the concrete is placed except when stabilized subbases are being constructed. If damage occurs on a stabilized subbase, it shall be corrected full depth by the Contractor. If traffic is allowed to use the prepared grade, the grade shall be checked and corrected immediately before the placement of concrete. The prepared grade shall be moistened with water, without saturating, immediately ahead of concrete placement to prevent rapid loss of moisture from concrete. The underlying surface shall be protected so that it will be entirely free of frost when concrete is placed.

501-4.4 CONDITIONING OF UNDERLYING SURFACE, SIDE-FORM AND FILL-IN LANE CONSTRUCTION. The prepared underlying surface shall be moistened with water, without saturating, immediately ahead of concrete placement to prevent rapid loss of moisture from the concrete. Damage caused by hauling or usage of other equipment shall be corrected and retested at the option of the Engineers. If damage occurs to a stabilized subbase, it shall be corrected full depth by the Contractor. A template shall be provided and operated on the forms immediately in advance of the placing of all concrete. The template shall be propelled only by hand and not attached to a tractor or other power unit. Templates shall be adjustable so that they may be set and maintained at the correct contour of the underlying surface. The adjustment and operation of the templates shall be such as will provide an accurate retest of the grade before placing the concrete thereon. All excess material shall be removed and wasted. Low areas shall be filled and compacted to a condition similar to that of the surrounding grade. The underlying surface shall be protected so that it will be entirely free from frost when the concrete is placed. The use of chemicals to eliminate frost in the underlying surface shall not be permitted.

The template shall be maintained in accurate adjustment, at all times by the Contractor, and shall be checked daily.

501-4.5 HANDLING, MEASURING, AND BATCHING MATERIAL. The batch plant site, layout, equipment, and provisions for transporting material shall assure a continuous supply of material to the work. Stockpiles shall be constructed in such a manner that prevents segregation and intermixing of deleterious materials.

Aggregates that have become segregated or mixed with earth or foreign material shall not be used. All aggregates produced or handled by hydraulic methods, and washed aggregates, shall be stockpiled or binned for draining at least 12 hours before being batched. Rail shipments requiring more than 12 hours will be accepted as adequate binning only if the car bodies permit free drainage.

Batching plants shall be equipped to proportion aggregates and bulk cement, by weight, automatically using interlocked proportioning devices of an approved type. When bulk cement is used, the Contractor shall use a suitable method of handling the cement from weighing hopper to transporting container or into the batch itself for transportation to the mixer, such as a chute, boot, or other approved device, to prevent loss of cement. The device shall be arranged to provide positive assurance that the cement content specified is present in each batch.

501-4.6 MIXING CONCRETE. The concrete may be mixed at the work site, in a central mix plant or in truck mixers. The mixer shall be of an approved type and capacity. Mixing time shall be measured from the time all materials, except water, are emptied into the drum. All concrete shall be mixed and delivered to the site in accordance with the requirements of ASTM C 94. Mixed concrete from the central mixing plant shall be transported in truck mixers, truck agitators, or nonagitating trucks. The elapsed time from the addition of cementitious material to the mix until the concrete is deposited in place at the work site shall not exceed 30 minutes when the concrete is hauled in nonagitating trucks, nor 90 minutes when the concrete is hauled in truck mixers or truck agitators. Retempering concrete by adding water or by other means will not be permitted, except when concrete is delivered in transit mixers. With transit mixers additional water may be added to the batch materials and additional mixing performed to increase the slump to meet the specified requirements provided the addition of water is performed within 45 minutes after the initial mixing operations and provided the water/cementitious ratio specified in the mix design is not exceeded.

501-4.7 LIMITATIONS ON MIXING AND PLACING. No concrete shall be mixed, placed, or finished when the natural light is insufficient, unless an adequate and approved artificial lighting system is operated.

Unless authorized in writing by the Engineer, mixing and concreting operations shall be discontinued when a descending air temperature in the shade and away from artificial heat reaches 40 ºF and shall not be resumed until an ascending air temperature in the shade and away from artificial heat reaches 35 ºF.

The aggregate shall be free of ice, snow, and frozen lumps before entering the mixer. The temperature of the mixed concrete shall not be less than 50 ºF at the time of placement. Concrete shall not be placed on frozen material nor shall frozen aggregates be used in the concrete.

When concreting is authorized during cold weather, water and/or the aggregates may be heated to not more than 150 ºF. The apparatus used shall heat the mass uniformly and shall be arranged to preclude the possible occurrence of overheated areas which might be detrimental to the materials.

501-4.8 PLACING CONCRETE. The Contractor has the option of side (fixed) form or slip-form paving. At any point in concrete conveyance, the free vertical drop of the concrete from one point to another or to the underlying surface shall not exceed 3 feet.

Hauling equipment or other mechanical equipment can be permitted on adjoining previously constructed lots of pavement when the concrete strength reaches a flexural strength of 550 psi, based on the average of three specimens, with no individual specimen below 525 psi when tested in accordance with ASTM C 78. Subgrade and subbase planers, concrete pavers, and concrete finishing equipment may be permitted to ride upon the edges of previously constructed pavement when the concrete has attained a minimum flexural strength of 400 psi.

- Side-form Method. For the side-form method, the concrete shall be deposited on the moistened grade to require as little rehandling as possible. Unless truck mixers, truck agitators, or nonagitating hauling equipment are equipped with means for discharge of concrete without segregation of the materials, the concrete shall be placed and spread using an approved mechanical spreading device that prevents segregation of the materials. Placing shall be continuous between transverse joints without the use of intermediate bulkheads. Necessary hand spreading shall be done with shovels--not rakes. Workers shall not be allowed to walk in the freshly mixed concrete with boots or shoes coated with earth or foreign substances.

Concrete shall be deposited as near to expansion and contraction joints as possible without disturbing them but shall not be dumped from the discharge bucket or hopper onto a joint assembly unless the hopper is centered above the joint assembly.

Concrete shall be thoroughly consolidated against and along the faces of all forms and previously placed concrete and along the full length and on both sides of all joint assemblies by means of vibrators inserted in the concrete. Vibrators shall not be permitted to come in contact with a joint assembly, the grade, or a side form. In no case shall the vibrator be operated longer than 20 seconds in any one location, nor shall the vibrators be used to move the concrete.

- Slip-form Method. For the slip-form method, the concrete shall be placed with an approved crawler-mounted, slip-form paver designed to spread, consolidate and shape the freshly placed concrete in one complete pass of the machine so that a minimum of hand finishing will be necessary to provide a dense and homogeneous pavement in conformance with requirements of the Plans and specifications. The concrete shall be placed directly on top of the joint assemblies to prevent them from moving when the paver moves over them. Side forms and finishing screeds shall be adjustable to the extent required to produce the specified pavement edge and surface tolerance. The side forms shall be of dimensions, shape, and strength to support the concrete laterally for a sufficient length of time so that no edge slumping exceeds the requirements of paragraph 501-5.2e(5). Final finishing shall be accomplished while the concrete is still in the plastic state.

In the event that slumping or sloughing occurs behind the paver or if there are any other structural or surface defects which, in the opinion of the Engineer, cannot be corrected within permissible tolerances, paving operations shall be immediately stopped until proper adjustment of the equipment or procedures have been made. In the event that satisfactory procedures and pavement are not achieved after not more than 2,000 linear feet of single lane paving, the Contractor shall complete the balance of the work with the use of standard metal forms and the formed method of placing and curing. Any concrete not corrected to permissible tolerances shall be removed and replaced at the Contractor's expense.

501-4.9 STRIKE-OFF OF CONCRETE AND PLACEMENT OF REINFORCEMENT. Following the placing of the concrete, it shall be struck off to conform to the cross section shown on the Plans and to an elevation such that when the concrete is properly consolidated and finished, the surface of the pavement shall be at the elevation shown on the Plans. When reinforced concrete pavement is placed in two layers, the bottom layer shall be struck off to such length and depth that the sheet of reinforcing steel fabric or bar mat may be laid full length on the concrete in its final position without further manipulation. The reinforcement shall then be placed directly upon the concrete, after which the top layer of the concrete shall be placed, struck off, and screeded. If any portion of the bottom layer of concrete has been placed more than 30 minutes without being covered with the top layer or if initial set has taken place, it shall be removed and replaced with freshly mixed concrete at the Contractor's expense. When reinforced concrete is placed in one layer, the reinforcement may be positioned in advance of concrete placement or it may be placed in plastic concrete by mechanical or vibratory means after spreading.

Reinforcing steel, at the time concrete is placed, shall be free of mud, oil, or other organic matter that may adversely affect or reduce bond. Reinforcing steel with rust, mill scale or a combination of both will be considered satisfactory, provided the minimum dimensions, weight, and tensile properties of a hand wire-brushed test specimen are not less than the applicable ASTM specification requirements.

501-4.10 JOINTS. Joints shall be constructed as shown on the Plans and in accordance with these requirements. All joints shall be constructed with their faces perpendicular to the surface of the pavement and finished or edged as shown on the Plans. Joints shall not vary more than 1/2 inch from their designated position and shall be true to line with not more than 1/4 inch variation in 10 feet. The surface across the joints shall be tested with a Contractor furnished 10-foot straightedge as the joints are finished and any irregularities in excess of 1/4 inch shall be corrected before the concrete has hardened. All joints shall be so prepared, finished, or cut to provide a groove of uniform width and depth as shown on the Plans.

- Construction. Longitudinal construction joints shall be slip-formed or formed against side forms with or without keyways, as shown in the Plans.

Transverse construction joints shall be installed at the end of each day's placing operations and at any other points within a paving lane when concrete placement is interrupted for more than 30 minutes or it appears that the concrete will obtain its initial set before fresh concrete arrives. The installation of the joint shall be located at a planned contraction or expansion joint. If placing of the concrete is stopped, the Contractor shall remove the excess concrete back to the previous planned joint.

- Contraction. Contraction joints shall be installed at the locations and spacing as shown on the Plans. Contraction joints shall be installed to the dimensions required by forming a groove or cleft in the top of the slab while the concrete is still plastic or by sawing a groove into the concrete surface after the concrete has hardened. When the groove is formed in plastic concrete the sides of the grooves shall be finished even and smooth with an edging tool. If an insert material is used, the installation and edge finish shall be according to the manufacturer's instructions. The groove shall be finished or cut clean so that spalling will be avoided at intersections with other joints. Grooving or sawing shall produce a slot at least 1/8 inch wide and to the depth shown on the Plans.

- Expansion. Expansion joints shall be installed as shown on the Plans. The premolded filler of the thickness as shown on the Plans, shall extend for the full depth and width of the slab at the joint, except for space for sealant at the top of the slab. The filler shall be securely staked or fastened into position perpendicular to the proposed finished surface. A cap shall be provided to protect the top edge of the filler and to permit the concrete to be placed and finished. After the concrete has been placed and struck off, the cap shall be carefully withdrawn leaving the space over the premolded filler. The edges of the joint shall be finished and tooled while the concrete is still plastic. Any concrete bridging the joint space shall be removed for the full width and depth of the joint.

- Keyways. Keyways shall be formed in the plastic concrete by means of side forms or the use of keyway liners which are inserted during the slip-form operations. The keyway shall be formed to a tolerance of 1/4 inch in any dimension and shall be of sufficient stiffness to support the upper keyway flange without distortion or slumping of the top of the flange. The dimensions of the keyway forms shall not vary more than plus or minus 1/4 inch from the mid-depth of the pavement. Liners that remain in place permanently and become part of the keyed joint shall be made of galvanized, copper clad, or of similar rust-resistant material compatible with plastic and hardened concrete and shall not interfere with joint reservoir sawing and sealing.

- Tie Bars. Tie bars shall consist of deformed bars installed in joints as shown on the Plans. Tie bars shall be placed at right angles to the centerline of the concrete slab and shall be spaced at intervals shown on the Plans. They shall be held in position parallel to the pavement surface and in the middle of the slab depth. When tie bars extend into an unpaved lane, they may be bent against the form at longitudinal construction joints, unless threaded bolt or other assembled tie bars are specified. These bars shall not be painted, greased, or enclosed in sleeves. When slip-form operations call for tie bars, two-piece hook bolts can be installed in the female side of the keyed joint provided the installation is made without distorting the keyed dimensions or causing edge slump. If a bent tie bar installation is used, the tie bars shall be inserted through the keyway liner only on the female side of the joint. In no case shall a bent tie bar installation for male keyways be permitted.

- Dowel Bars. Dowel bars or other load-transfer units of an approved type shall be placed across joints in the manner as shown on the Plans. They shall be of the dimensions and spacings as shown and held rigidly in the middle of the slab depth in the proper horizontal and vertical alignment by an approved assembly device to be left permanently in place. The dowel or load-transfer and joint devices shall be rigid enough to permit complete assembly as a unit ready to be lifted and placed into position. A metal, or other type, dowel expansion cap or sleeve shall be furnished for each dowel bar used with expansion joints. These caps shall be substantial enough to prevent collapse and shall be placed on the ends of the dowels as shown on the Plans. The caps or sleeves shall fit the dowel bar tightly and the closed end shall be watertight. The portion of each dowel painted with rust preventative paint, as required under paragraph 501-2.7 and shown on the Plans to receive a debonding lubricant, shall be thoroughly coated with asphalt MC-70, or an approved lubricant, to prevent the concrete from bonding to that portion of the dowel. If free-sliding plastic-coated or epoxy-coated steel dowels are used, a lubrication bond breaker shall be used except when approved pullout tests indicate it is not necessary. Where butt-type joints with dowels are designated, the exposed end of the dowel shall be oiled.

Dowel bars at contraction joints may be placed in the full thickness of pavement by a mechanical device approved by the Engineer. The device shall be capable of installing dowel bars within the maximum permissible alignment tolerances. Dowels bars at longitudinal construction joints shall be bonded in drilled holes.

- Installation of Joint Devices. All joint devices shall be approved by the Engineer.

The top of an assembled joint device shall be set at the proper distance below the pavement surface and the elevation shall be checked. Such devices shall be set to the required position and line and shall be securely held in place by stakes or other means to the maximum permissible tolerances during the placing and finishing of the concrete. Where premolded joint material is used, it shall be placed and held in a vertical position; if constructed in sections, there shall be no offsets between adjacent units.

Dowel bars and assemblies shall be checked for position and alignment. The maximum permissible tolerances on dowel bar alignment shall be in accordance with paragraph 501-5.2e(6). During the concrete placement operation, it is advisable to place plastic concrete directly on dowel assemblies immediately prior to passage of the paver to help maintain dowel position and alignment within maximum permissible tolerances.

When concrete is placed using slip-form pavers, dowels and tie bars shall be placed in longitudinal construction joints by bonding the dowels or tie bars into holes drilled into the hardened concrete. Holes approximately 1/8 to 1/4 inch greater in diameter than the dowel or tie bar shall be drilled with rotary-type core drills that must be held securely in place to drill perpendicularly into the vertical face of the pavement slab. Rotary-type percussion drills may be used provided that spalling of concrete does not occur. Any damage of the concrete shall be repaired by the Contractor in a method approved by the Engineer. Dowels or tie bars shall be bonded in the drilled holes using an epoxy resin material. Installation procedures shall be adequate to insure that the area around dowels is completely filled with epoxy grout. Epoxy shall be injected into the back of the hole and displaced by the insertion of the dowel bar. Bars shall be completely inserted into the hole and shall not be withdrawn and reinserted creating air pockets in the epoxy around the bar. The Contractor shall furnish a template for checking the position and alignment of the dowels. Dowel bars shall not be less than 10 inches from a transverse joint and shall not interfere with dowels in the transverse direction.

- Sawing of Joints. Joints shall be cut as shown on the Plans. Equipment shall be as described in paragraph 501-4.1. The circular cutter shall be capable of cutting a groove in a straight line and shall produce a slot at least 1/8 inch wide and to the depth shown on the Plans. The top portion of the slot shall be widened by sawing to provide adequate space for joint sealers as shown on the Plans. Sawing shall commence as soon as the concrete has hardened sufficiently to permit cutting without chipping, spalling, or tearing and before uncontrolled shrinkage cracking of the pavement occurs. Sawing shall be carried on both during the day and night as required. The joints shall be sawed at the required spacing, consecutively in sequence of the concrete placement.

501-4.11 FINAL STRIKE-OFF, CONSOLIDATION, AND FINISHING.

- Sequence. The sequence of operations shall be the strike-off, floating and removal of laitance, straightedging, and final surface finish. The addition of superficial water to the surface of the concrete to assist in finishing operations will not be permitted.

- Finishing at Joints. The concrete adjacent to joints shall be compacted or firmly placed without voids or segregation against the joint material; it shall be firmly placed without voids or segregation under and around all load-transfer devices, joint assembly units, and other features designed to extend into the pavement. Concrete adjacent to joints shall be mechanically vibrated as required in paragraph 501-4.8a. After the concrete has been placed and vibrated adjacent to the joints, the finishing machine shall be operated in a manner to avoid damage or misalignment of joints. If uninterrupted operations of the finishing machine, to, over, and beyond the joints, cause segregation of concrete, damage to, or misalignment of the joints, the finishing machine shall be stopped when the screed is approximately 8 inches from the joint. Segregated concrete shall be removed from the front of and off the joint; and the forward motion of the finishing machine shall be resumed. Thereafter, the finishing machine may be run over the joint without lifting the screed, provided there is no segregated concrete immediately between the joint and the screed or on top of the joint.

- Machine Finishing. The concrete shall be spread as soon as it is placed, and it shall be struck off and screeded by a finishing machine. The machine shall go over each area as many times and at such intervals as necessary to give to proper consolidation and to leave a surface of uniform texture. Excessive operation over a given area shall be avoided. When side forms are used, the tops of the forms shall be kept clean by an effective device attached to the machine, and the travel of the machine on the forms shall be maintained true without lift, wobbling, or other variation tending to affect the precision finish. During the first pass of the finishing machine, a uniform ridge of concrete shall be maintained ahead of the front screed for its entire length. When in operation, the screed shall be moved forward with a combined longitudinal and transverse shearing motion, always moving in the direction in which the work is progressing, and so manipulated that neither end is raised from the side forms during the striking-off process. If necessary, this shall be repeated until the surface is of uniform texture, true to grade and cross section, and free from porous areas.

- Hand Finishing. Hand finishing methods will not be permitted, except under the following conditions: in the event of breakdown of the mechanical equipment, hand methods may be used to finish the concrete already deposited on the grade; in areas of narrow widths or of irregular dimensions where operation of the mechanical equipment is impractical. Concrete, as soon as placed, shall be struck off and screeded. An approved portable screed shall be used. A second screed shall be provided for striking off the bottom layer of concrete when reinforcement is used.

The screed for the surface shall be a least 24 inches longer than the maximum width of the slab to be struck off. It shall be of approved design, sufficiently rigid to retain its shape, and shall be constructed either of metal or of other suitable material covered with metal. Consolidation shall be attained by the use of suitable vibrators.

- Floating. After the concrete has been struck off and consolidated, it shall be further smoothed and trued by means of a longitudinal float using one of the following methods:

- Hand Method. Long-handled floats shall not be less than 12 feet in length and 6 inches in width, stiffened to prevent flexibility and warping. The float shall be operated from foot bridges spanning but not touching the concrete or from the edge of the pavement. Floating shall pass gradually from one side of the pavement to the other. Forward movement along the centerline of the pavement shall be in successive advances of not more than one-half the length of the float. Any excess water or laitance in excess of 1/8 inch thick shall be removed and wasted.

- Mechanical Method. The Contractor may use a machine composed of a cutting and smoothing float(s), suspended from and guided by a rigid frame and constantly in contact with, the side forms or underlying surface. If necessary, long-handled floats having blades not less than 5 feet in length and 6 inches in width may be used to smooth and fill in open-textured areas in the pavement. When the crown of the pavement will not permit the use of the mechanical float, the surface shall be floated transversely by means of a long-handled float. Care shall be taken not to work the crown out of the pavement during the operation. After floating, any excess water and laitance in excess of 1/8 inch thick shall be removed and wasted. Successive drags shall be lapped one-half the length of the blade.

- Straight-edge Testing and Surface Correction. After the pavement has been struck off and while the concrete is still plastic, it shall be tested for trueness with a Contractor furnished 16-foot straightedge swung from handles 3 feet longer than one-half the width of the slab. The straightedge shall be held in contact with the surface in successive positions parallel to the centerline and the whole area gone over from one side of the slab to the other, as necessary. Advancing shall be in successive stages of not more than one-half the length of the straightedge. Any excess water and laitance in excess of 1/8 inch thick shall be removed from the surface of the pavement and wasted. Any depressions shall be immediately filled with freshly mixed concrete, struck off, consolidated, and refinished. High areas shall be cut down and refinished. Special attention shall be given to assure that the surface across joints meets the smoothness requirements of paragraph 501-5.2e(3). Straightedge testing and surface corrections shall continue until the entire surface is found to be free from observable departures from the straightedge and until the slab conforms to the required grade and cross section. The use of long-handled wood floats shall be confined to a minimum; they may be used only in emergencies and in areas not accessible to finishing equipment.

501-4.12 SURFACE TEXTURE. The surface of the pavement shall be finished with either a broom, burlap drag, or artificial turf finish for all newly constructed concrete pavements. It is important that the texturing equipment not tear or unduly roughen the pavement surface during the operation. Any imperfections resulting from the texturing operation shall be corrected. The corrugations shall be uniform in appearance and approximately 1/16 inch in depth.

- Brush or Broom Finish. If the pavement surface texture is to be a type of brush or broom finish, it shall be applied when the water sheen has practically disappeared. The equipment shall operate transversely across the pavement surface.

- Burlap Drag Finish. If a burlap drag is used to texture the pavement surface, it shall be at least 15 oz/yd2. To obtain a textured surface, the transverse threads of the burlap shall be removed approximately 1 foot from the trailing edge. A heavy buildup of grout on the burlap threads produces the desired wide sweeping longitudinal striations on the pavement surface.

- Artificial Turf Finish. If artificial turf is used to texture the surface, it shall be applied by dragging the surface of the pavement in the direction of concrete placement with an approved full-width drag made with artificial turf. The leading transverse edge of the artificial turf drag will be securely fastened to a lightweight pole on a traveling bridge. At least 24 inches of the artificial turf shall be in contact with the concrete surface during dragging operations. A variety of different types of artificial turf are available and approval of any one type will be done only after it has been demonstrated by the Contractor to provide a satisfactory texture. One type that has provided satisfactory texture consists of 7,200 approximately 0.85-inches-long polyethylene turf blades per square foot.

501-4.13 CURING. Immediately after finishing operations are completed and marring of the concrete will not occur, the entire surface of the newly placed concrete shall be cured for a 7-day cure period in accordance with one of the methods below. Failure to provide sufficient cover material of whatever kind the Contractor may elect to use, or lack of water to adequately take care of both curing and other requirements, shall be cause for immediate suspension of concreting operations. The concrete shall not be left exposed for more than 1/2 hour during the curing period. The concrete shall be maintained at a temperature of at least 50 ºF for a period of 72 hours after placing and at a temperature above freezing for the remainder of the curing time. The Contractor shall be responsible for the quality and strength of the concrete placed during cold weather, and any concrete injured by frost action shall be removed and replaced at the Contractor's expense.

- Impervious Membrane Method. The entire surface of the pavement shall be sprayed uniformly with white pigmented curing compound immediately after the finishing of the surface and before the set of the concrete has taken place. The curing compound shall not be applied during rainfall. Curing compound shall be applied by mechanical sprayers under pressure at the rate of 1 gallon to not more than 150 square feet. The spraying equipment shall be of the fully atomizing type equipped with a tank agitator. At the time of use, the compound shall be in a thoroughly mixed condition with the pigment uniformly dispersed throughout the vehicle. During application the compound shall be stirred continuously by mechanical means. Hand spraying of odd widths or shapes and concrete surfaces exposed by the removal of forms will be permitted. The curing compound shall be of such character that the film will harden within 30 minutes after application. Should the film become damaged from any cause, including sawing operations, within the required curing period, the damaged portions shall be repaired immediately with additional compound or other approved means. Upon removal of side forms, the sides of the exposed slabs shall be protected immediately to provide a curing treatment equal to that provided for the surface.

- Polyethylene Films. The top surface and sides of the pavement shall be entirely covered with polyethylene sheeting. The units shall be lapped at least 18 inches. The sheeting shall be placed and weighted to cause it to remain in contact with the surface and sides. The sheeting shall have dimensions that will extend at least twice the thickness of the pavement beyond the edges of the pavement. Unless otherwise specified, the sheeting shall be maintained in place for 7 days after the concrete has been placed.

- Waterproof Paper. The top surface and sides of the pavement shall be entirely covered with waterproofed paper. The units shall be lapped at least 18 inches. The paper shall be placed and weighted to cause it to remain in contact with the surface covered. The paper shall have dimensions that will extend at least twice the thickness of the pavement beyond the edges of the slab. The surface of the pavement shall be thoroughly saturated prior to placing of the paper. Unless otherwise specified, the paper shall be maintained in place for 7 days after the concrete has been placed.

- White Burlap-Polyethylene Sheets. The surface of the pavement shall be entirely covered with the sheeting. The sheeting used shall be such length (or width) that it will extend at least twice the thickness of the pavement beyond the edges of the slab. The sheeting shall be placed so that the entire surface and both edges of the slab are completely covered. The sheeting shall be placed and weighted to remain in contact with the surface covered, and the covering shall be maintained fully saturated and in position for 7 days after the concrete has been placed.

501-4.14 REMOVING FORMS. Unless otherwise specified, forms shall not be removed from freshly placed concrete until it has hardened sufficiently to permit removal without chipping, spalling, or tearing but in no case, less than 24 hours. After the forms have been removed, the sides of the slab shall be cured as outlined in one of the methods indicated in paragraph 501-4.14. Major honeycombed areas shall be considered as defective work and shall be removed and replaced in accordance with paragraph 501-5.2(f).

501-4.15 SEALING JOINTS. The joints in the pavement shall be sealed in accordance with Item P-605.

501-4.16 PROTECTION OF PAVEMENT. The Contractor shall protect the pavement and its appurtenances against both public traffic and traffic caused by the Contractor's employees and agents. This shall include workers to direct traffic and the erection and maintenance of warning signs, lights, pavement bridges, crossovers, and protection of unsealed joints from intrusion of foreign material, etc. Any damage to the pavement occurring prior to final acceptance shall be repaired or the pavement replaced at the Contractor's expense. The Contractor shall have available at all times, materials for the protection of the edges and surface of the unhardened concrete. Such protective materials shall consist of rolled polyethylene sheeting at least 4 mils thick of sufficient length and width to cover the plastic concrete slab and any edges. The sheeting may be mounted on either the paver or a separate movable bridge from which it can be unrolled without dragging over the plastic concrete surface. When rain appears imminent, all paving operations shall stop and all available personnel shall begin covering the surface of the unhardened concrete with the protective covering.

501-4.17 OPENING TO TRAFFIC. The pavement shall not be opened to traffic until test specimens molded and cured in accordance with ASTM C 31 have attained a flexural strength of 550 psi when tested in accordance with ASTM C 78. If such tests are not conducted, the pavement shall not be opened to traffic until 14 days after the concrete was placed. Prior to opening to traffic, the pavement shall be cleaned.

MATERIAL ACCEPTANCE

501-5.1 ACCEPTANCE SAMPLING AND TESTING. All acceptance sampling and testing, with the exception of coring for thickness determination, necessary to determine conformance with the requirements specified in this section will be performed by the Engineer. Concrete shall be accepted for strength and thickness on a lot basis. After initial curing, the Contractor shall deliver the beams and cores to the State Materials Laboratory (5750 Tudor Road, Anchorage, Alaska) or the Northern Region Materials Laboratory (2301 Peger Road, Fairbanks, Alaska), as directed by the Engineer, for final curing and/or acceptance testing.

A lot shall consist of 1000 cubic yards.

- Flexural Strength.

- Sampling. Each lot shall be divided into five equal sublots. One sample shall be taken for each sublot from the plastic concrete delivered to the job site. Sampling locations shall be determined by the Engineer in accordance with random sampling procedures contained in ASTM D 3665. The concrete shall be sampled in accordance with ASTM C 172. The Contractor shall make the number of flexural beam specimens specified. Each beam shall be between 20 and 30 inches in length.

- Testing. Two specimens shall be made from each sample. Specimens shall be made in accordance with ASTM C 31 and the flexural strength of each specimen shall be determined in accordance with ASTM C 78 at a loading rate that constantly increases the extreme fiber stress at the mid-point of the allowable range. The flexural strength for each sublot shall be computed by averaging the results of the two test specimens representing that sublot.

- Curing. The Contractor shall provide adequate facilities for the initial curing of beams. During the 24 hours after molding, the temperature immediately adjacent to the specimens must be maintained in the range of 60 to 80 ºF, and loss of moisture from the specimens must be prevented. The specimens may be stored in tightly constructed wooden boxes, damp sand pits, temporary buildings at construction sites, under wet burlap in favorable weather, or in heavyweight closed plastic bags, or using other suitable methods, provided the temperature and moisture loss requirements are met.

- Acceptance. Acceptance of pavement for flexural strength will be determined by the Engineer in accordance with paragraph 501-5.2b.

- Pavement Thickness. Sampling and testing for pavement placed with slipform paving methods shall be as follows. Pavement placed using fixed forms shall not be cored. Sampling and testing shall be accomplished by inspection and measurement of the forms prior to and after placing of concrete.

- Sampling. Each lot shall be divided into four equal sublots and one core shall be taken by the Contractor for each sublot. Sampling locations shall be determined by the Engineer in accordance with random sampling procedures contained in ASTM D 3665. Areas, such as thickened edges, with planned variable thickness, shall be excluded from sample locations.

Cores shall be neatly cut with a core drill. The Contractor shall furnish all tools, labor, and materials for cutting samples and filling the cored hole. Core holes shall be filled by the Contractor with a non-shrink grout approved by the Engineer within one day after sampling.

- Testing. The thickness of the cores shall be determined by the Engineer by the average caliper measurement in accordance with ASTM C 174.

- Acceptance. Acceptance of pavement for thickness shall be determined by the Engineer in accordance with paragraph 501-5.2c.

- Partial Lots. If 200 cubic yards or less remain to complete the project quantity, it will be considered as part of the previous lot. If more than 200 cubic yards remain, it will be considered as a complete lot and sampled and tested as such.

Where three sublots have been produced, they shall constitute a lot. Where one or two sublots have been produced, they shall be incorporated into the next lot or the previous lot and the total number of sublots shall be used in the acceptance criteria calculation, i.e., n=5 or n=6.

- Outliers. All individual flexural strength tests within a lot shall be checked for an outlier (test criterion) in accordance with ATM, SP-7. Outliers shall be discarded, and the PWL shall be determined using the remaining test values.

- Yield, Cement Content, and Air Content. Acceptance of pavement for yield, cement content, and air content will be determined by the Engineer in accordance with paragraph 501-5.2e.(7) at the testing rate of 1 test per 200 cubic yards.

501-5.2 ACCEPTANCE CRITERIA.

- General. Acceptance will be based on the following characteristics of the completed pavement:

- Flexural strength

- Thickness

- Smoothness

- Grade

- Edge slump

- Dowel bar alignment

- Yield, cement content, and air content

Flexural strength and thickness shall be evaluated for acceptance on a lot basis using the method of estimating percentage of material within specification limits (PWL). Acceptance using PWL considers the variability (standard deviation) of the material and the testing procedures, as well as the average (mean) value of the test results to calculate the percentage of material that is above the lower specification tolerance limit (L).

Acceptance for flexural strength will be based on the criteria contained in accordance with paragraph 501-5.2e(1). Acceptance for thickness will be based on the criteria contained in paragraph 501-5.2e(2). Acceptance for smoothness will be based on the criteria contained in paragraph 501-5.2e(3). Acceptance for grade will be based on the criteria contained in paragraph 501-5.2e(4).

The Engineer may at any time, not withstanding previous plant acceptance, reject and require the Contractor to dispose of any batch of concrete mixture which is rendered unfit for use due to contamination, segregation, or improper slump. Such rejection may be based on only visual inspection. In the event of such rejection, the Contractor may take a representative sample of the rejected material in the presence of the Engineer, and if it can be demonstrated in the laboratory, in the presence of the Engineer, that such material was erroneously rejected, payment will be made for the material at the contract unit price.

- Flexural Strength. Acceptance of each lot of in-place pavement for flexural strength shall be based on PWL. The Contractor shall target production quality to achieve 90 PWL or higher.

- Pavement Thickness. Acceptance of each lot of in-place pavement shall be based on PWL. The Contractor shall target production quality to achieve 90 PWL or higher.

- Percentage of Material Within Limits (PWL). The PWL shall be determined in accordance with procedures specified in Section 110 of the General Provisions.

The lower specification tolerance limit (L) for flexural strength and thickness shall be:

| Lower Specification Tolerance Limit (L) |
| --- |
| Flexural Strength | 0.93 x strength specified in paragraph 501-3.1 |
| Thickness | Plan Thickness - 0.5 inch |

- Acceptance Criteria.

- Flexural Strength. If the PWL of the lot equals or exceeds 90%, the lot shall be acceptable. Acceptance and payment for the lot shall be determined in accordance with paragraph 501-8.1.

- Thickness. If the PWL of the lot equals or exceeds 90%, the lot shall be acceptable. Acceptance and payment for the lot shall be determined in accordance with paragraph 501-8.1.

- Smoothness. As soon as the concrete has hardened sufficiently, the pavement surface shall be tested with a 16-foot straightedge or other specified device. Surface smoothness deviations shall not exceed 1/4 inch from the straightedge placed in any direction, including placement along and spanning any pavement joint edge.

Areas in a slab showing high spots of more than 1/4 inch but not exceeding 1/2 inch in 16 feet shall be marked and immediately ground down with an approved grinding machine to an elevation that will fall within the tolerance of 1/4 inch or less. Where the departure from correct cross section exceeds 1/2 inch, the pavement shall be removed and replaced at the expense of the Contractor when so directed by the Engineer.

- Grade. An evaluation of the surface grade shall be made by the Engineer for compliance to the tolerances contained below.

Lateral Deviation. Lateral deviation from established alignment of the pavement edge shall not exceed plus or minus 0.10 foot in any lane.

Vertical Deviation. Vertical deviation from established grade shall not exceed plus or minus 0.05 foot at any point.

- Edge Slump. When slip-form paving is used, not more than 15% of the total free edge of each 500-foot segment of pavement, or fraction thereof, shall have an edge slump exceeding 1/4 inch, and none of the free edge of the pavement shall have an edge slump exceeding 3/8 inch. (The total free edge of 500 feet of pavement will be considered the cumulative total linear measurement of pavement edge originally constructed as nonadjacent to any existing pavement; i.e., 500 feet of paving lane originally constructed as a separate lane will have 1,000 feet of free edge, 500 feet of fill-in lane will have no free edge, etc.). The area affected by the downward movement of the concrete along the pavement edge shall be limited to not more than 18 inches from the edge. When excessive edge slump cannot be corrected before the concrete has hardened, the area with excessive edge slump shall be removed and replaced at the expense of the Contractor when so directed by the Engineer.

- Dowel Bar Alignment. Dowel bars and assemblies shall be checked for position and alignment. The maximum permissible tolerance on dowel bar alignment in each plane, horizontal and vertical, shall not exceed 2% (or 1/4 inch per foot) of a dowel bar.

- Yield, Cement Content, and Air Content. Yield, cement content, and air content shall be determined in accordance with ASTM C 138.

- Removal and Replacement of Concrete. Any area or section of concrete that is removed and replaced shall be removed and replaced back to planned joints. The Contractor shall replace damaged dowels and the requirements for doweled longitudinal construction joints in paragraph 501-4.10 shall apply to all contraction joints exposed by concrete removal.

CONTRACTOR QUALITY CONTROL

501-6.1 QUALITY CONTROL PROGRAM. The Contractor shall develop a Quality Control Program in accordance with Section 100 of the General Provisions. The program shall address all elements which effect the quality of the pavement including but not limited to:

| a. Mix Design | e. Proportioning | i. Dowel Placement and Alignment |
| --- | --- | --- |
| b. Aggregate Gradation | f. Mixing and Transportation | j. Flexural Strength |
| c. Quality of Materials | g. Placing and Consolidation | k. Finishing and Curing |
| d. Stockpile Management | h. Joints | l. Surface Smoothness |

501-6.2 QUALITY CONTROL TESTING. The Contractor shall perform all quality control tests necessary to control the production and construction processes applicable to this specification and as set forth in the Quality Control Program. The testing program shall include, but not necessarily be limited to, tests for aggregate gradation, aggregate moisture content, slump, and air content.

A Quality Control Testing Plan shall be developed as part of the Quality Control Program.

- Fine Aggregate.

- Gradation. A sieve analysis shall be made at a minimum of every 100 cubic yards in accordance with ASTM C 136 from randomly sampled material taken from the discharge gate of storage bins or from the conveyor belt.

- Moisture Content. If an electric moisture meter is used, at least two direct measurements of moisture content shall be made per week to check the calibration. If direct measurements are made in lieu of using an electric meter, two tests shall be made per day. Tests shall be made in accordance with ASTM C 70 or ASTM C 566.

- Coarse Aggregate.

- Gradation. A sieve analysis shall be made at a minimum of every 100 cubic yards for each size of aggregate. Tests shall be made in accordance with ASTM C 136 from randomly sampled material taken from the discharge gate of storage bins or from the conveyor belt.

- Moisture Content. If an electric moisture meter is used, at least two direct measurements of moisture content shall be made per week to check the calibration. If direct measurements are made in lieu of using an electric meter, two tests shall be made per day. Tests shall be made in accordance with ASTM C 566.

- Slump. Slump tests shall be performed for every 100 cubic yards of material produced. Slump tests shall be performed in accordance with ASTM C 143 from material randomly sampled from material discharged from trucks at the paving site. Material samples shall be taken in accordance with ASTM C 172.

- Air Content. Air content tests, shall be performed for every 100 cubic yards of material produced. Air content tests shall be performed in accordance with ASTM C 231 for gravel and stone coarse aggregate and ASTM C 173 for porous coarse aggregate, from material randomly sampled from trucks at the plant site. Material samples shall be taken in accordance with ASTM C 172.

501-6.3 CONTROL CHARTS. The Contractor shall maintain linear control charts for fine and course aggregate, gradation, slump, and air content.

Control charts shall be posted in a location satisfactory to the Engineer and shall be kept up to date at all times. As a minimum, the control charts shall identify the project number, the contract item number, the test number, each test parameter, the Action and Suspension Limits, or Specification limits, applicable to each test parameter, and the Contractor's test results. The Contractor shall use the control charts as part of a process control system for identifying potential problems and assignable causes before they occur. If the Contractor's projected data during production indicates a potential problem and the Contractor is not taking satisfactory corrective action, the Engineer may halt production or acceptance of the material.

- Fine and Coarse Aggregate Gradation. The Contractor shall record the running average of the last five gradation tests for each control sieve on linear control charts. Specification limits contained in Tables 1 and 2 shall be superimposed on the Control Chart for job control.

- Slump and Air Content. The Contractor shall maintain linear control charts both for individual measurements and range (i.e., difference between highest and lowest measurements) for slump and air content in accordance with the following Action and Suspension Limits.

CONTROL CHART LIMITS

Based on Sample Size n=4

| Control Parameter | Individual Measurements | Range Suspension Limit |
| --- | --- | --- |
|  | Action Limit | Suspension Limit |  |
| Slump | +/- 1 in. | +/- 1.5 inch | +/- 2.4 inch |
| Air Content | +/- 1.2% | +/- 1.8% | +/- 2.8% |

The individual measurement control charts shall use the mix design Target Values as indicators of central tendency.

501-6.4 CORRECTIVE ACTION. The Quality Control Plan shall indicate that appropriate action shall be taken when the process is believed to be out of control. The Quality Control Plan shall detail what action will be taken to bring the process into control and shall contain sets of rules to gauge when a process is out of control. As a minimum, a process shall be deemed out of control and corrective action taken if any one of the following conditions exists.

- Fine and Coarse Aggregate Gradation. When two consecutive averages of five tests are outside of the Tables 1 or 2 specification limits, immediate steps, including a halt to production, shall be taken to correct the grading.

- Fine and Coarse Aggregate Moisture Content. Whenever the moisture content of the fine or coarse aggregate changes by more than 0.5%, the scale settings for the aggregate batcher(s) and water batcher shall be adjusted.

- Slump. The Contractor shall halt production and make appropriate adjustments whenever:

- one point falls outside the Suspension Limit line for individual measurements or range; or

- two points in a row fall outside the Action Limit line for individual measurements.

- Air Content. The Contractor shall halt production and adjust the amount of air-entraining admixture whenever:

- one point falls outside the Suspension Limit line for individual measurements or range; or

- two points in a row fall outside the Action Limit line for individual measurements.

Whenever a point falls outside the Action Limits line, the air-entraining admixture dispenser shall be calibrated to ensure that it is operating correctly and with good reproducibility.

METHOD OF MEASUREMENT

501-7.1 Portland cement concrete pavement will be measured by the number of cubic yards of pavement as specified in place, completed and accepted.

BASIS OF PAYMENT

501-8.1 PAYMENT. Payment for accepted concrete pavement will be made at the contract unit price per cubic yard, adjusted in accordance with paragraph 501-8.1a.

Payment shall be full compensation for all labor, materials, tools, equipment, and incidentals required to complete the work as specified herein and on the drawings.

- Basis of Adjusted Payment. The pay factor for each individual lot will be calculated in accordance with Table 2. A pay factor will be calculated for both flexural strength and thickness. The lot pay factor will be the lower of the two pay factors.

TABLE 2.    PRICE ADJUSTMENT SCHEDULE

| Percentage of Material Within Specification Limits (PWL) | Pay Factor |
| --- | --- |
| 96 - 100 | 1.05 |
| 90 - 95 | 0.01 PWL + 0.10 |
| 75 - 89 | 0.005 PWL + 0.55 |
| 55 - 74 | 0.14 PWL – 0.12 |
| Below 55 | 0* |

*If the PWL falls below 55, the lot shall be removed and replaced. However, the Engineer may decide to allow the rejected lot to remain. In that case, if the Engineer and Contractor agree in writing that the lot shall not be removed, the pay factor for the lot shall be 0.50.

For each lot accepted, the adjusted contract unit price shall be the product of the lot pay factor for the lot and the contract unit price.

- Payment. Payment will be made under:

Item P-501a	Portland Cement Concrete Pavement - per cubic yard

TESTING REQUIREMENTS

AASHTO T 26	Quality of Water to be Used in Concrete

ASTM C 31	Making and Curing Concrete Test Specimens in the Field

ASTM C 70	Surface Moisture in Fine Aggregate

ASTM C 78	Flexural Strength of Concrete (Using Simple Beam with Third-Point Loading)

ASTM C 131	Resistance to Abrasion of Small Size Coarse Aggregate by Use of the Los Angeles Machine

ASTM C 136	Sieve Analysis of Fine and Coarse Aggregates

ASTM C 138	Unit Weight, Yield, and Air Content (Gravimetric) of Concrete

ASTM C 143	Slump of Portland Cement Concrete

ASTM C 172	Sampling Freshly Mixed Concrete

ASTM C 173	Air Content of Freshly Mixed Concrete by the Volumetric Method

ASTM C 174	Measuring Length of Drilled Concrete Cores

ASTM C 231	Air Content of Freshly Mixed Concrete by the Pressure Method

ASTM C 311	Sampling and Testing Fly Ash for Use as an Admixture in Portland Cement Concrete

ASTM C 535	Resistance to Abrasion of Large Size Coarse Aggregate by Use of the Los Angeles Machine

ASTM C 566	Total Moisture Content of Aggregates by Drying

ASTM C 1077	Standard Practice for Laboratories Testing Concrete and Concrete Aggregates for Use in Construction and Criteria for Laboratory Evaluation

ASTM D 3665	Random Sampling of Construction Materials

ASTM D 4791	Flat or Elongated Particles in Coarse Aggregate

ATM SP-7	Standard Practice for Determination of Outlier Test Results

MATERIAL REQUIREMENTS

AASHTO M 254	Coated Dowel Bars

ACI 306R	Cold Weather Concreting

ASTM A 185	Welded Steel Wire Fabric for Concrete Reinforcement

ASTM A 615	Deformed and Plain Billet-Steel Bars for Concrete Reinforcement

ASTM A 616	Rail-Steel Deformed and Plain Bars for Concrete Reinforcement

ASTM A 617	Axle-Steel Deformed and Plain Bars for Concrete Reinforcement

ASTM A 704	Welded Steel Plain Bar or Rod Mats for Concrete Reinforcement

ASTM A 714	High-Strength Low-Alloy Welded and Seamless Steel Pipe

ASTM C 33	Concrete Aggregates

ASTM C 94	Ready-Mixed Concrete

ASTM C 150	Portland Cement

ASTM C 171	Sheet Materials for Curing Concrete

ASTM C 260	Air-Entraining Admixtures for Concrete

ASTM C 309	Liquid Membrane-Forming Compounds

ASTM C 494	Chemical Admixtures for Concrete

ASTM C 595	Blended Hydraulic Cements

ASTM C 618	Fly Ash and Raw or Calcined Natural Pozzolan for Use as a Mineral Admixture in Portland Cement Concrete

ASTM C 881	Epoxy-Resin-Base Bonding System for Concrete

ASTM D 1751	Preformed Expansion Joint Fillers for Concrete Paving and Structural Construction (Nonextruding and Resilient Bituminous Types)

PART VII – MISCELLANEOUS

## ITEM P-602	BITUMINOUS PRIME COAT

DESCRIPTION

602-1.1 This item shall consist of an application of bituminous material on the prepared base course in accordance with these Specifications and in reasonably close conformity to the lines shown on the Plans.

MATERIALS

602-2.1 BITUMINOUS MATERIAL. The types, grades, controlling specifications, and application temperatures for the bituminous materials are given in Table 1. The Engineer shall designate the specific material to be used.

TABLE 1.    BITUMINOUS MATERIAL

| Type and Grade | Specification | Application Temperatures \1\ °F | Application Rate gal/yd2 |
| --- | --- | --- | --- |
| Emulsified Asphalt |  |  |  |
| SS-1, SS-1h | ASTM D 977 | 70-160 | 0.27 to 0.53 |
| MS-2, HFMS-1 | ASTM D 977 | 70-160 | 0.27 to 0.53 |
| CSS-1, CSS-1h | ASTM D 2397 | 70-160 | 0.27 to 0.53 |
| CMS-2 | ASTM D 2397 | 70-160 | 0.27 to 0.53 |
| CMS-2s | \2\ | 70-160 | 0.22 to 0.44 |
| Cutback Asphalt |  |  |  |
| RC-30 | ASTM D 2028 | 80+ | 0.27 to 0.53 |
| RC-70 | ASTM D 2028 | 120+ | 0.27 to 0.53 |
| RC-250 | ASTM D 2028 | 165+ | 0.27 to 0.53 |
| MC-30 | ASTM D 2027 | 80+ | 0.11 to 0.33 |

\1\ The maximum temperature for cutback asphalt shall be that at which fogging occurs.

\2\ CMS-2s shall meet the following specifications: Viscosity, Sabolt Furol, of 50 to 450 at 120 °F when tested under ASTM D 244. Particle charge test of Positive when tested under ASTM D 244. Sieve test maximum of 0.10% when tested under ASTM D 244. Oil distillate, by volume of emulsion, of 20% maximum when tested under ASTM D 244. Residue of 65% minimum when tested under ASTM D 244. Penetration of 100 to 250 at 77 °F, 100 g, 5 s when tested under ASTM D 5. Ductility of 40 cm minimum at 77 °F when tested under ASTM D 113. Solubility in trichloroethylene of 97.5% minimum.

CONSTRUCTION METHODS

602-3.1 WEATHER LIMITATIONS. The prime coat shall be applied only when the existing surface is dry or contains sufficient moisture to get uniform distribution of the bituminous material, when the surface temperature is above 45 °F, and when the weather is not foggy or rainy. The temperature requirements may be waived, but only when so directed by the Engineer.

602-3.2 EQUIPMENT. The equipment used by the Contractor shall include a self-powered pressure bituminous material distributor and equipment for heating bituminous material.

The distributor shall be designed, equipped, maintained, and operated so that bituminous material at even heat may be applied uniformly on variable widths of surface at the specified rate. The allowable variation from the specified rate shall not exceed 10%. Distributor equipment shall include a tachometer, pressure gages, volume-measuring devices or a calibrated tank, and a thermometer for measuring temperatures of tank contents. The distributor shall be self-powered and shall be equipped with a power unit for the pump and full circulation spray bars adjustable laterally and vertically.

A power broom and/or blower shall be provided for any required cleaning of the surface to be treated.

602-3.3 APPLICATION OF BITUMINOUS MATERIAL. Immediately before applying the prime coat, the full width of the surface to be primed shall be swept with a power broom to remove all loose dirt and other objectionable material.

The bituminous material including solvent shall be uniformly applied with a bituminous distributor at the rate specified in Table 1, depending on the base course surface texture. The type of bituminous material and application rate shall be approved by the Engineer prior to application.

Following the application, the primed surface shall be allowed to dry not less than 48 hours without being disturbed or for such additional time as may be necessary to permit the drying out of the prime until it will not be picked up by traffic or equipment. This period shall be determined by the Engineer. The surface shall then be maintained by the Contractor until the surfacing has been placed. Suitable precautions shall be taken by the Contractor to protect the primed surface against damage during this interval, including supplying and spreading any sand necessary to blot up excess bituminous material.

602-3.4 BITUMINOUS MATERIAL CONTRACTOR'S RESPONSIBILITY. Samples of the bituminous materials that the Contractor proposes to use, together with a statement as to their source and character, must be submitted and approved before use of such material begins. The Contractor shall require the manufacturer or producer of the bituminous materials to furnish material subject to this and all other pertinent requirements of the contract. Only satisfactory materials, so demonstrated by service tests, shall be acceptable.

The Contractor shall furnish vendor's certified test reports for each carload, or equivalent, of bituminous material shipped to the project. The report shall be delivered to the Engineer before permission is granted for use of the material. The furnishing of the vendor's certified test report for the bituminous material shall not be interpreted as basis for final acceptance. All such test reports shall be subject to verification by testing samples of materials received for use on the project.

602-3.5 FREIGHT AND WEIGH BILLS. Before the final estimate is allowed, the Contractor shall file with the Engineer receipted bills when railroad shipments are made, and certified weigh bills when materials are received in any other manner, of the bituminous materials actually used in the construction covered by the contract. The Contractor shall not remove bituminous material from the tank car or storage tank until the initial outage and temperature measurements have been taken by the Engineer, nor shall the car or tank be released until the final outage has been taken by the Engineer.

Copies of freight bills and weigh bills shall be furnished to the Engineer during the progress of the work.

METHOD OF MEASUREMENT

602-4.1 The bituminous material for prime coat will be measured by the ton.

BASIS OF PAYMENT

602-5.1 Payment will be made at the contract unit price per ton for bituminous prime coat.

Payment will be made under:

Item P-602a	Bituminous Prime Coat - per ton

MATERIAL REQUIREMENTS

ASTM D 977	Emulsified Asphalt

ASTM D 2027	Standard Specification for Cutback Asphalt (Medium-Curing Type)

ASTM D 2028	Asphalt, Cutback (Rapid Curing Grade)

ASTM D 2397	Cationic Emulsified Asphalt

TESTING REQUIREMENTS

ASTM D 5	Penetration of Bituminous Materials

ASTM D 113	Ductility of Bituminous Materials

ASTM D 244	Emulsified Asphalts

ITEM P-603	BITUMINOUS TACK COAT

DESCRIPTION

603-1.1 This item shall consist of preparing and treating a bituminous or concrete surface with bituminous material in accordance with these Specifications and in reasonably close conformity to the lines shown on the Plans.

MATERIALS

603-2.1 BITUMINOUS MATERIALS. The bituminous material shall be either cutback asphalt, emulsified asphalt, or tar and shall conform to the requirements of Table 1. The type, grade, controlling specification, and application temperature of bituminous material to be used shall be specified by the Engineer.

TABLE 1.    BITUMINOUS MATERIAL

| Type and Grade | Specification | Application Temperature °F | Application Rate gal/yd2 |
| --- | --- | --- | --- |
| Emulsified Asphalt |  |  |  |
| SS-1, SS-1h | ASTM D 977 | 75-130 | 0.05 to 0.16 |
| CSS-1, CSS-1h | ASTM D 2397 | 75-130 | 0.05 to 0.16 |
| STE-1 | \1\ | 68-140 | 0.04 to 0.10 |
| Cutback Asphalt |  |  |  |
| RC-70 | ASTM D 2028 | 120-160 | 0.05 to 0.16 |
| Tar |  |  |  |
| RTCB 5, RTCB 6 | AASHTO M 52 | 60-120 | 0.05 to 0.16 |

\1\ STE-1 shall meet the following specifications: Viscosity, Sabolt Furol at 77 °F of 30 max., when tested under ASTM D 244. Particle charge test of Positive when tested under ASTM D 244 (If particle charge test is inconclusive, material having a max. pH value of 6.7 will be acceptable). Storage Stability, 1 day 1% max when tested under ASTM D 244. Demulsibility, 35 mil 0.8% Dioctyl Sodium Sulfosuccinate Solution 25 minimum when tested under ASTM D 244. Sieve test maximum of 0.10% when tested under ASTM D 244. Oil distillate, by volume of emulsion, of 5% maximum when tested under ASTM D 244. Residue of 45% minimum when tested under ASTM D 244. Penetration at 77 °F, 100 gm, 5 sec. of 100 minimum, 200 maximum when tested under ASTM D 5. Ductility at 77 °F of 40 cm minimum when tested under ASTM D 113. Solubility in trichloroethylene of 97.5% minimum

CONSTRUCTION METHODS

603-3.1 WEATHER LIMITATIONS. The tack coat shall be applied only when the existing surface is dry and the surface temperature is above 40 °F. The temperature requirements may be waived, but only when so directed by the Engineer.

603-3.2 EQUIPMENT. The Contractor shall provide equipment for heating and applying the bituminous material.

The distributor shall be designed, equipped, maintained, and operated so that bituminous material at even heat may be applied uniformly on variable widths of surface at the specified rate. The allowable variation from the specified rate shall not exceed 10%. Distributor equipment shall include a tachometer, pressure gages, volume-measuring devices or a calibrated tank, and a thermometer for measuring temperatures of tank contents. The distributor shall be self-powered and shall be equipped with a power unit for the pump and full circulation spray bars adjustable laterally and vertically.

A power broom and/or blower shall be provided for any required cleaning of the surface to be treated.

603-3.3 APPLICATION OF BITUMINOUS MATERIAL. Immediately before applying the tack coat, the full width of surface to be treated shall be swept with a power broom and/or airblast to remove all loose dirt and other objectionable material.

Emulsified asphalt shall be applied a sufficient time in advance of the paver to ensure that all water has evaporated before any of the overlying mixture is placed on the tacked surface.

The bituminous material including vehicle or solvent shall be uniformly applied with a bituminous distributor at the rate specified in Table 1, depending on the condition of the existing surface. The type of bituminous material and application rate shall be approved by the Engineer prior to application.

Following the application, the surface shall be allowed to cure without being disturbed for such period of time as may be necessary to permit drying out and setting of the tack coat. This period shall be determined by the Engineer. The surface shall then be maintained by the Contractor until the next course has been placed. Suitable precautions shall be taken by the Contractor to protect the surface against damage during this interval.

603-3.4 BITUMINOUS MATERIAL-CONTRACTOR'S RESPONSIBILITY. Samples of the bituminous material that the Contractor proposes to use, together with a statement as to its source and character, must be submitted and approved before use of such material begins. The Contractor shall require the manufacturer or producer of the bituminous material to furnish material subject to this and all other pertinent requirements of the contract. Only satisfactory materials so demonstrated by service tests, shall be acceptable.

The Contractor shall furnish the vendor's certified test reports for each carload, or equivalent, of bituminous material shipped to the project. The report shall be delivered to the Engineer before permission is granted for use of the material. The furnishing of the vendor's certified test report for the bituminous material shall not be interpreted as a basis for final acceptance. All such test reports shall be subject to verification by testing samples of material received for use on the project.

603-3.5 FREIGHT AND WEIGH BILLS. Before the final estimate is allowed, the Contractor shall file with the Engineer receipted bills when railroad shipments are made, and certified weigh bills when materials are received in any other manner, of the bituminous materials actually used in the construction covered by the contract. The Contractor shall not remove bituminous material from the tank car or storage tank until the initial outage and temperature measurements have been taken by the Engineer, nor shall the car or tank be released until the final outage has been taken by the Engineer. Copies of freight bills and weigh bills shall be furnished to the Engineer during the progress of the work.

METHOD OF MEASUREMENT

603-4.1 Bituminous tack coat will be measured by the ton in accordance with Subsection 90-02.

BASIS OF PAYMENT

603.5-1 Payment will be made at the contract unit price per ton of bituminous material.

Payment will be made under:

Item P-603a	Bituminous Tack Coat - per ton

MATERIAL REQUIREMENTS

AASHTO M 52	Tar for Use in Road Construction

ASTM D 633	Volume Correction Table for Road Tar

ASTM D 977	Emulsified Asphalt

ASTM D 2028	Liquid Asphalt (Rapid-Curing Type)

ASTM D 2397	Cationic Emulsified Asphalt

TESTING REQUIREMENTS

ASTM D 5	Penetration of Bituminous Materials

ASTM D 113	Ductility of Bituminous Materials

ASTM D 244	Emulsified Asphalts

ITEM P-605	JOINT SEALING FILLER

DESCRIPTION

605-5.1 This item shall consist of providing and installing a resilient and adhesive joint sealing filler capable of effectively sealing joints and cracks in pavements.

MATERIALS

605-2.1 JOINT SEALERS. Joint sealing material shall meet the requirements of ASTM D 3581.

Each lot or batch of sealing compound shall be delivered to the jobsite in the manufacturer's original sealed container. Each container shall be marked with the manufacturer's name, batch or lot number, and the safe heating temperature and shall be accompanied by the manufacturer's certification stating that the compound meets the requirements of this specification.

CONSTRUCTION METHODS

605-3.1 TIME OF APPLICATION. Joints shall be sealed as soon after completion of the curing period as feasible and before the pavement is opened to traffic, including construction equipment. The pavement temperature shall be above 50 °F at the time of installation of the poured joint sealing material.

605-3.2 PREPARATION OF JOINTS. Immediately before sealing, the joints shall be thoroughly cleaned of all laitance, curing compound, and other foreign material. Cleaning shall be accomplished by wire brushing. Upon completion of cleaning, the joints shall be blown out with compressed air. The joint faces shall be surface dry when the seal is applied.

Prior to resealing joints, the existing joint material shall be removed to the depth as shown on the Plans. If joint sealer other than that originally used is specified, all existing joint sealer shall be removed.

605-3.3 INSTALLATION OF SEALANT. Joints shall be inspected for proper width, depth, alignment, and preparation, and shall be approved by the Engineer before sealing is allowed.

The joint sealant shall be applied uniformly solid from bottom to top and shall be filled without formation of entrapped air or voids. A backing material shall be placed as shown on the Plans and shall be nonadhesive to the concrete or the sealant material. The heating kettle shall be an indirect heating type, constructed as a double boiler. A positive temperature control and mechanical agitation shall be provided. The sealant shall not be heated to within 20 degrees (F) below the safe heating temperature. The safe heating temperature can be obtained from the manufacturer's shipping container. A direct connecting pressure type extruding device with nozzles shaped for insertion into the joint shall be provided. Any sealant spilled on the surface of the pavement shall be removed immediately.

METHOD OF MEASUREMENT

605-4.1 Joint sealing material will be measured by the linear foot of sealant in place, complete, and accepted.

BASIS OF PAYMENT

605-5.1 Payment for joint sealing material will be made at the contract unit price per linear foot.

Payment will be made under:

Item P-605a	Joint Sealing Filler - per linear foot

TESTING REQUIREMENTS

ASTM D 412	Rubber Properties in Tension

ASTM D 1644	Nonvolatile Content of Varnishes

MATERIAL REQUIREMENTS

ASTM D 3581	Joint Sealant, Hot-Poured, Jet-Fuel-Resistant Type, for Portland Cement Concrete and Tar-Concrete Pavements

ITEM P-606	ADHESIVE COMPOUND

DESCRIPTION

606-1.1 This specification covers two types of material; a liquid suitable for sealing electrical wire in saw cuts in pavement and sealing light fixtures or bases in pavement, and a paste suitable for embedding light fixtures in the pavement. Both types of material are two-component filled formulas with the characteristics specified in paragraph 606-2.4. Materials supplied for use with bituminous concrete pavements must be formulated so they are compatible with the bituminous concrete.

EQUIPMENT AND MATERIALS

606-2.1 CURING. When prewarmed to 77 °F, mixed, and placed in accordance with manufacturer's directions, the materials shall cure at temperatures of 45 °F or above without the application of external heat.

606-2.2 STORAGE. The adhesive components shall not be stored at temperatures over 86 °F.

606-2.3 CAUTION. Installation and use shall be in accordance with the manufacturer's recommended procedures. Avoid prolonged or repeated contact with skin. In case of contact, wash with soap and flush with water. If taken internally, call doctor. Keep away from heat or flame. Avoid vapor. Use in well-ventilated areas. Keep in cool place. Keep away from children.

606-2.4 CHARACTERISTICS. When mixed and cured in accordance with the manufacturer's directions, the materials shall have the following properties shown in Table 1.

SAMPLING, INSPECTION, AND TEST PROCEDURES

606-3.1 TENSILE PROPERTIES. Tests for tensile strength and elongation shall be conducted in accordance with ASTM D 638.

606-3.2 EXPANSION. Tests for coefficients of linear and cubical expansion shall be conducted in accordance with ASTM D 1168, Method B, except that mercury shall be used instead of glycerin. The test specimen(s) shall be mixed in the proportions specified by the manufacturer, and cured in a glass tub approximately 2 inches long by 3/8 inch in diameter. The interior of the tube shall be precoated with a silicone mold release agent. The hardened sample shall be removed from the tube and aged at room temperature for 1 week before conducting the test. The test temperature range shall be from 35 to 140 °F.

606-3.3 TEST FOR DIELECTRIC STRENGTH. Test for dielectric strength shall be conducted in accordance with ASTM D 149 for sealing compounds to be furnished for sealing electrical wires in pavement.

606-3.4 TEST FOR ARC RESISTANCE. Test for arc resistance shall be conducted in accordance with ASTM D 495 for sealing compounds to be furnished for sealing electrical wires in pavement.

606-3.5 TEST FOR ADHESION TO STEEL. The ends of two smooth, clean, steel specimens (approximately 1 inch X 1 inch X 6 inches) are bonded together with adhesive mixture and allowed to cure at room temperature for a period of time to meet formulation requirements and then tested to failure on a Riehle (or similar) tensile tester. The thickness of adhesive to be tested shall be 1/4 inch.

TABLE 1.    PROPERTY REQUIREMENTS

| Physical or Electrical Property | Minimum | Maximum | ASTM Method |
| --- | --- | --- | --- |
| Tensile |
| Portland Cement Concrete | 1,000 psi |  | D 638 |
| Bituminous Concrete | 500 psi |  |  |
| Elongation |
| Portland Cement Concrete | 8% \1\ |  | D 638 |
| Bituminous Concrete | 50% |  | D 638 |
| Coef. of cub. exp., cm3/cm3/°C | 0.00090 | 0.00120 | D 1168 |
| Coef. of lin. exp., cm/cm/°C | 0.00030 | 0.00040 | D 1168 |
| Dielectric strength, short time test | 350 volts/mil. |  | D 149 |
| Arc resistance | 125 secs. |  | D 495 |
| Adhesion to steel | 1,000 psi |  |  |
| Adhesion to portland cement concrete | 200 psi |  |  |
| Adhesion to asphalt concrete | (no test available) |  |  |

\1\ 20% or more (without filler) for formulations to be supplied for areas subject to freezing.

606-3.6 ADHESION TO PORTLAND CEMENT CONCRETE.

- Concrete Test Block Preparation. The aggregate grading shall be as shown in Table 2.

The coarse aggregate shall consist of crushed rock having a minimum of 75% of the particles with at least one fractured face and having a water absorption of not more than 1.5%. The fine aggregate shall consist of crushed sand manufactured from the same parent rock as the coarse aggregate. The concrete shall have a water-cement ratio of 5.5 gallons of water per bag of cement, a cement factor of 6, plus or minus 0.5, bags of cement per cubic yard of concrete, and a slump of 2-1/2 inches plus or minus 1/2 inch. The ratio of fine aggregate to total aggregate shall be approximately 40% by solid volume. The air content shall be 5.0%, plus or minus 0.5%, and it shall be obtained by the addition to the batch of an air-entraining admixture such as vinsol resin. The mold shall be metal with a metal base plate. Means shall be provided for securing the base plate to the mold. The assembled mold and base plate shall be watertight and shall be oiled with mineral oil before use. The inside measurement of the mold shall be such that several 1-inch by 2-inch by 3-inch test blocks can be cut from the specimen with a concrete saw having a diamond blade. The concrete shall be prepared and cured in accordance with ASTM C 192.

TABLE 2.    AGGREGATE FOR BOND TEST BLOCKS

| Type | Sieve Size | Percent Passing |
| --- | --- | --- |
| Coarse Aggregate | 3/4 in. | 97 to 100 |
|  | 1/2 in. | 63 to 69 |
|  | 3/8 in. | 30 to 36 |
|  | No. 4 | 0 to 3 |
| Fine Aggregate | No. 4 | 100 |
|  | No. 8 | 82 to 88 |
|  | No. 16 | 60 to 70 |
|  | No. 30 | 40 to 50 |
|  | No. 50 | 16 to 26 |
|  | No. 100 | 5 to 9 |

- Bond Test. Prior to use, oven-dry the test blocks to constant weight at a temperature of 220 to 230 °F, cool to room temperature, 73.4 ±3 °F, in a desiccator, and clean the surface of the blocks of film or powder by vigorous brushing with a stiff-bristled fiber brush. Two test blocks shall be bonded together on the 1-inch X 3-inch sawed face with the adhesive mixture and allowed to cure at room temperature for a period of time to meet formulation requirements and then tested to failure in a Riehle (or similar) tensile tester. The thickness of the adhesive to be tested shall be 1/4 inch.

606-3.7 COMPATIBILITY WITH ASPHALT CONCRETE. Test for compatibility with asphalt in accordance with ASTM D 3407.

606-3.8 CERTIFICATION. The Contractor shall furnish the vendor's certified test reports for each batch of material delivered to the project. The report shall certify that the material meets specification requirements and is suitable for use with portland cement concrete or bituminous concrete pavements. The report shall be delivered to the Engineer before permission is granted for use of the material. In addition the Contractor shall obtain a statement from the supplier or manufacturer which guarantees the material for one year. The supplier or manufacturer shall furnish evidence that the material has performed satisfactorily on other projects.

606-3.9 APPLICATION. Adhesive shall be applied on a dry, clean surface, free of grease, dust, and other loose particles. The method of mixing and application shall be in strict accordance with the manufacturer's recommendations.

METHOD OF MEASUREMENT

606-4.1 The adhesive compound will be measured by the pound of adhesive as specified, in place, complete and accepted. When required in the installation of an in-runway lighting system or portion thereof, no measurement will be made for direct payment of adhesive, as the cost of furnishing and installing will be considered as a subsidiary obligation in the completion of the installation.

BASIS OF PAYMENT

606-5.1 Payment will be made, where applicable, at the contract unit price per pound for the adhesive.

Payment will be made under:

Item P-606a	Adhesive Compound - per pound

TESTING REQUIREMENTS

ASTM C 192	Making and Curing Concrete Compression and Flexure Test Specimens in the Laboratory

ASTM D 149	Dielectric Breakdown Voltage and Dielectric Strength of Electrical Insulating Materials at Commercial Power Frequencies

ASTM D 495	High-Voltage, Low-Current, Arc Resistance of Solid Electrical Insulating Materials

ASTM D 638	Tensile Properties of Plastics

ASTM D 1168	Hydrocarbon Waxes Used for Electrical Insulation

ASTM D 3407	Joint Sealants, Hot-Poured, For Concrete and Asphalt Pavements

ITEM P-609	SEAL COATS AND BITUMINOUS SURFACE TREATMENT

DESCRIPTION

609-1.1 This item shall consist of a bituminous surface treatment as a wearing course composed of a single or multiple application of bituminous material and aggregate cover placed on the prepared primed base or properly cured wearing surface, in accordance with these Specifications, and shall conform to the dimensions and typical cross section shown on the Plans.

609-1.2 QUANTITIES OF MATERIALS. The approximate amounts of materials per square yard for the bituminous surface treatment shall be as provided in Table 1 for the treatment specified on the Plans or in the Special Provisions. The exact amounts to be used shall be determined by the Engineer.

TABLE 1.    QUANTITIES OF MATERIALS

| Application No | Aggregate lb/yd2 | Asphalt gal/yd2 | Type of Asphalt \1\ |
| --- | --- | --- | --- |
| 1 | 40-50 | 0.35-0.45 | Asphalt Cement |
|  |  | 0.40-0.50 | Emulsified Asphalt |
| 2 | 20-25 | 0.15-0.25 | Asphalt Cement |
|  |  | 0.20-0.35 | Emulsified Asphalt |
| 3 | 15-20 | 0.15-0.20 | Emulsified Asphalt |

\1\ See Table 3 for grades of asphalt and spraying temperatures.

MATERIALS

609-2.1 AGGREGATE MATERIALS. The aggregate material shall be either crushed stone or crushed gravel. The cover material shall be screenings; sand may be used when specified.

If the material is to be crushed stone, it shall be manufactured from sound, hard, durable rock of accepted quality and crushed to specification size. All strata, streaks, and pockets of clay, dirt, sandstone, soft rock, or other unsuitable material accompanying the sound rock shall be discarded and not allowed to enter the crusher.

If the material is to be crushed gravel, it shall consist of hard, durable, fragments of stone or gravel of accepted quality and crushed to specification size. All strata, streaks, and pockets of sand, excessively fine gravel, clay, or other unsuitable material including all stones, rocks, and boulders of inferior quality shall be discarded and not allowed to enter the crusher. The crushing of the gravel shall result in a product in which the material retained on the separate No. 4, 3/8-inch, and 1/2-inch sieves shall have at least 75% of particles with at least one fractured face as determined by WAQTC TM 1.

The crushed aggregate shall not contain more than 8%, by weight, of elongated or flat pieces per ASTM D 4791 and shall be free from wood, roots, vegetable, organic, or other extraneous matter. The crushed coarse aggregate shall have a percentage of wear not more than 40 at 500 revolutions, per ASTM C 131.

The aggregate shall show no evidence of disintegration nor show a total loss greater than 12% when subjected to five cycles of the sodium sulfate accelerated soundness test specified in ASTM C 88.

Aggregates shall have a minimum degradation value of 50 when tested in accordance with ATM 313.

The crushed aggregate for the applications shall meet the requirements for gradation given in Table 2 when tested in accordance with ASTM C 136 and with WAQTC Field Operating Procedure (FOP) for AASHTO T 27 and T 11.

TABLE 2.    REQUIREMENTS FOR GRADATION OF AGGREGATE

| Sieve Designation (square openings) | Percentage by Weight Passing Sieves |
| --- | --- |
| Aggregate for first application |
| 1 in. | 100 |
| 3/4 in. | 90-100 |
| 1/2 in. | 20-55 |
| 3/8 in. | 0-15 |
| No. 4 | 0-5 |
| No. 200 | 0-1 |
| Aggregate for second application |
| 1/2 in. | 100 |
| 3/8 in. | 85-100 |
| No. 4 | 10-30 |
| No. 8 | 0-10 |
| No. 16 | 0-5 |
| No. 200 | 0-1 |
| Aggregate for third application |
| 3/8 in. | 100 |
| 1/4 in. | 90-100 |
| No. 4 | 60-85 |
| No. 8 | 0-25 |
| No. 16 | 0-5 |
| No. 200 | 0-2 |

The gradations in the table represent the limits which shall determine suitability of aggregate for use for the specified applications from the sources of supply. The final gradations decided on, within the limits designated in the table, shall be uniformly graded from coarse to fine.

The cover aggregate used in the third application shall be a light-colored material whose color and reflectivity shall be approved by the Engineer.

The aggregate to be used shall show no evidence of stripping or swell when tested in accordance with AASHTO T 182 and T 101. The use of antistrip agents for the control of stripping shall be used if necessary.

609-2.2 BITUMINOUS MATERIAL. The types, grades, controlling specifications, and application temperatures for the bituminous materials are shown in Table 3. The Engineer shall designate the specific material to be used.

TABLE 3.    BITUMINOUS MATERIALS

| Type and Grade | Specification | Spraying Temperature \1\ Deg. F |
| --- | --- | --- |
| Asphalt Cement |
| AC 2.5, AC-5 | ASTM D 3381 | 275+ |
| AR-1000, 2000 | ASTM D 3381 | 280+ |
| 120-150, 200-300 | ASTM D 946 | 270+ |
| Emulsified Asphalt |
| RS-1 | ASTM D 977 | 70-140 |
| RS-2 | ASTM D 977 | 125-175 |
| MS-1, HFMS-1 | ASTM D 977 | 70-160 |
| CRS-1 | ASTM D 2397 | 125-175 |
| CRS-2 | ASTM D 2397 | 125-175 |

\1\ The maximum temperature for asphalt cements shall be below that at which fogging occurs.

CONSTRUCTION METHODS

609-3.1 WEATHER LIMITATIONS. Bituminous material shall be applied only when the existing surface is dry and the atmospheric temperature is above 60 °F. No material shall be applied when rain is imminent or when dust or sand is blowing.

609-3.2 EQUIPMENT AND TOOLS. The Contractor shall furnish all equipment, tools, and machines necessary for the performance of the work.

- Pressure Distributor. The distributor shall be designed, equipped, maintained, and operated so that bituminous material at even heat may be applied uniformly on variable widths of surface at the specified rate. The allowable variation from the specified rate shall not exceed 10%. Distributor equipment shall include a tachometer, pressure gages, volume-measuring devices or a calibrated tank, and a thermometer for measuring temperatures of tank contents. The distributor shall be self-powered and shall be equipped with a power unit for the pump and full circulation spray bars adjustable laterally and vertically.

- Aggregate Spreader. The aggregate spreader shall be a self-propelled mechanical spreader or truck-attached mechanical spreader capable of uniformly distributing aggregate at the specified rates.

- Roller. The roller shall be a pneumatic-tired roller with an effective rolling width of at least 60 inches and capable of exerting a minimum contact pressure of 40 psi.

- Power Broom. A power broom and/or blower shall be provided for removing loose material from the surface to be treated.

609-3.3 PREPARING UNDERLYING COURSE. The surface of the underlying course shall be prepared, shaped, and conditioned to a uniform grade and section, as shown on the Plans and as specified. Loose dirt and other objectionable material shall be removed from the surface.

On those type of bases where a prime coat is required and specified, the prime shall be applied and satisfactorily cured before starting the bituminous surface treatment.

When specified, the Contractor shall be required to patch, with premixed material, any holes or other malformations deviating from the true cross section and grade. The premixed material shall be made of the bituminous material specified and prepared by the method directed by the Engineer. All small patches shall be thoroughly hand tamped while the large patches shall be rolled with a power or pneumatic roller.

609-3.4 APPLICATION OF BITUMINOUS MATERIAL. Bituminous material shall be applied upon the properly prepared surface at the rate and temperature specified using a pressure distributor to obtain uniform distribution at all points. To insure proper drainage, the strips shall begin along the centerline of the pavement on a crowned section or on the high side of the pavement with a one-way slope. During all applications, the surfaces of adjacent structures shall be protected in such manner as to prevent their being spattered or marred. Bituminous materials shall not be discharged into borrow pits or gutters or upon the airport area.

609-3.5 APPLICATION OF AGGREGATE MATERIAL. Immediately after the application of the bituminous material or when directed, the aggregates at the rate specified for each designated application shall be spread uniformly over the bituminous material. Trucks spreading aggregate shall be operated backward so that the bituminous material will be covered before the truck wheels pass over it. The aggregate shall be spread in the same width of application as the bituminous material and shall not be applied in such thickness as to cause blanketing. Back-spotting or sprinkling of additional aggregate material, and pouring additional bituminous material over areas that show up having insufficient cover or bitumen, shall be done by hand whenever necessary. Additional spreading of aggregate material shall be done with a motor-patrol grader equipped with broom moldboard, a broom drag, or a power broom, as directed by the Engineer.

Immediately after spreading each application, the aggregate shall be rolled. The rolling shall be continued until no more aggregate can be worked into the surface. In the construction of the second and third application, blading with the wire-broom moldboard attachment or broom dragging shall begin as soon as possible after the rolling has started and after the surface has set sufficiently to prevent excessive marking. Further blading and rolling on the strip being placed and on adjacent strips previously placed, shall be done as often as necessary to keep the aggregate material uniformly distributed. These operations shall be continued until the surface is evenly covered and cured to the satisfaction of the Engineer.

Succeeding applications shall not be applied until the preceding application has set and in no case until at least 24 hours have elapsed. If dust, dirt, or other foreign matter accumulates on the surface between the applications, the Contractor shall be required to sweep and clean the surface as specified herein. The bituminous material and the aggregate shall be spread upon the clean and properly cured surface and handled as required. Extreme care shall be taken in all applications to avoid brooming or tracking dirt or any foreign matter on any portion of the pavement surface under construction.

All surplus aggregate from the final application shall be swept off the surface and removed prior to final acceptance of the work.

609-3.6 CORRECTION OF DEFECTS. Any defects, such as raveling, low centers, lack of uniformity, or other imperfections caused by faulty workmanship, shall be corrected to the satisfaction of the Engineer.

609-3.7 CERTIFICATION. Samples of the bituminous materials that the Contractor proposes to use, together with a statement as to their source and character, shall be submitted and approval obtained before use of such materials begins.

The Contractor shall furnish vendor's certified test reports for each carload, or equivalent, of bitumen shipped to the project. The report shall be delivered to the Engineer before permission is granted for use of the material. The furnishing of the vendor's certified test report for the bituminous material shall not be interpreted as a basis for final acceptance. All such test reports shall be subject to verification by testing sample materials as received for use on the project.

609-3.8 FREIGHT AND WEIGH BILLS. Before the final estimate is allowed the Contractor shall file with the Engineer receipted bills where railroad shipments are made, and certified weight bills when materials are received in any other manner, of the bituminous and covering materials actually used in the construction covered by the contract. The Contractor shall not remove bituminous material from the tank car or storage tank until the initial outage and temperature measurements have been taken by the Engineer, nor shall the car or tank be released until the final outage has been taken by the Engineer. Copies of all freight bills and weigh bills shall be furnished to the Engineer during the progress of the work.

METHOD OF MEASUREMENT

609-4.1 The bituminous material will be measured by the ton. Water added to emulsified asphalt will not be measured for payment.

609-4.2 The quantity of aggregate materials for the first application to be paid for will be the number of tons of aggregate used for the accepted work.

609-4.3 The quantity of aggregate material for the second application to be paid for will be the number of tons of aggregate used for the accepted work.

609-4.4 The weight of aggregate for the third application to be paid for will be the number of tons of aggregate used for the accepted work.

BASIS OF PAYMENT

609-5.1 Payment will be made at the contract unit price per ton for bituminous material for surface treatment and per ton for the first, second and third aggregate application.

Payment will be made under:

Item P-609a 	Bituminous Material - per ton

Item P-609b 	First Application Aggregate - per ton

Item P-609c 	Second Application Aggregate - per ton

Item P-609d 	Third Application Aggregate - per ton

TESTING REQUIREMENTS

ASTM C 29 	Unit Weight of Aggregate

ASTM C 88 	Soundness of Aggregates by Use of Sodium Sulfate or Magnesium Sulfate

ASTM C 131	Resistance to Abrasion of Small Size Coarse Aggregate by Use of the Los Angeles Machine

ASTM C 136	Sieve or Screen Analysis of Fine and Coarse Aggregate

ASTM D 4791	Flat or Elongated Particles in Coarse Aggregate

ATM 313	Aggregate Degradation

WAQTC TM 1	Determining the Percentage of Fracture in Coarse Aggregate

WAQTC FOP for AASHTO T 27 and T 11	Coarse and Fine Aggregate Gradation

MATERIAL REQUIREMENTS

ASTM D 946	Penetration-Graded Asphalt-Cement for Use in Pavement Construction

ASTM D 977	Emulsified Asphalt

ASTM D 1250	Petroleum Measurement Tables

ASTM D 2397	Cationic Emulsified Asphalt

ASTM D 3381	Viscosity-Graded Asphalt-Cement for Use in Pavement Construction

ITEM P-610	STRUCTURAL PORTLAND CEMENT CONCRETE

DESCRIPTION

610-1.1 This item shall consist of plain or reinforced structural portland cement concrete, prepared and constructed in accordance with these Specifications, at the locations and of the form and dimensions shown on the Plans.

MATERIALS

610-2.1 GENERAL. Only approved materials, conforming to the requirements of these Specifications, shall be used in the work. They may be subjected to inspection and tests at any time during the progress of their preparation or use. The source of supply of each of the materials shall be approved by the Engineer before delivery or use is started. Representative preliminary samples of the materials shall be submitted by the Contractor, when required, for examination and test. Materials shall be scored and handled to insure the preservation of their quality and fitness for use and shall be located to facilitate prompt inspection. All equipment for handling and transporting materials and concrete must be clean before any material or concrete is placed therein.

In no case shall the use of pit-run or naturally mixed aggregates be permitted. Naturally mixed aggregate shall be screened and washed, and all fine and coarse aggregates shall be stored separately and kept clean. The mixing of different kinds of aggregates from different sources in one storage pile or alternating batches of different aggregates will not be permitted.

610-2.2 COARSE AGGREGATE. The coarse aggregate shall meet the requirements of ASTM C 33.

Coarse aggregate shall be well graded from coarse to fine and shall meet one of the gradations shown in Table 1, using ASTM C 136 and with WAQTC FOP for AASHTO T 27 and T 11.

TABLE 1.    GRADATION FOR COARSE AGGREGATE

| Sieve Designation (square openings) | Percentage by Weight Passing Sieves |
| --- | --- |
|  | 2 in. | 1-1/2 in. | 1 in. | 3/4 in. | 1/2 in. | 3/8 in. | No. 4 |
| No. 4 to 3/4 in. |  |  | 100 | 90-100 |  | 20-55 | 0-10 |
| No. 4 to 1 in. |  | 100 | 90-100 |  | 25-60 |  | 0-10 |
| No. 4 to 1-1/2 in. | 100 | 95-100 |  | 35-70 |  | 10-30 | 0-5 |

610-2.3 FINE AGGREGATE. The fine aggregate shall meet the requirements of ASTM C 33.

The fine aggregate shall be well graded from fine to coarse and shall meet the requirements of Table 2, when tested in accordance with ASTM C 136 and with WAQTC FOP for AASHTO T 27 and T 11:

TABLE 2.    GRADATION FOR FINE AGGREGATE

| Sieve Designation (square openings) | Percentage by Weight Passing Sieves |
| --- | --- |
| 3/8 in. | 100 |
| No. 4 | 95-100 |
| No. 16 | 45-80 |
| No. 30 | 25-55 |
| No. 50 | 10-30 |
| No. 100 | 2-10 |

Blending will be permitted, if necessary, in order to meet the gradation requirements for fine aggregate. Fine aggregate deficient in the percentage of material passing the No. 50 sieve may be accepted, provided that such deficiency does not exceed 5% and is remedied by the addition of pozzolanic or cementitious materials other than portland cement, as specified in 610-2.6 on admixtures, in sufficient quantity to produce the required workability as approved by the Engineer.

610-2.4 CEMENT. Cement shall conform to the requirements of ASTM C 150 Type I, II, or III.

The Contractor shall furnish vendors' certified test reports for each carload, or equivalent, of cement shipped to the project. The report shall be delivered to the Engineer before permission to use the cement is granted. All such test reports shall be subject to verification by testing sample materials received for use on the project.

610-2.5 WATER. The water used in concrete shall be free from sewage, oil, acid, strong alkalies, vegetable matter, and clay and loam. If the water is of questionable quality, it shall be tested in accordance with AASHTO T 26.

610-2.6 ADMIXTURES. The use of any material added to the concrete mix shall be approved by the Engineer. Before approval of any material, the Contractor shall be required to submit the results of complete physical and chemical analyses made by an acceptable testing laboratory. Subsequent tests shall be made of samples taken by the Engineer from the supply of the material being furnished or proposed for use on the work to determine whether the admixture is uniform in quality with that approved.

Pozzolanic admixtures shall be fly ash or raw or calcined natural pozzolans meeting the requirements of ASTM C 618.

Air-entraining admixtures shall meet the requirements of ASTM C 260. Air-entraining admixtures shall be added at the mixer in the amount necessary to produce the specified air content.

Water-reducing, set-controlling admixtures shall meet the requirements of ASTM C 494, Type A, water-reducing or Type D, water-reducing and retarding. Water-reducing admixtures shall be added at the mixer separately from air-entraining admixtures in accordance with the manufacturer's printed instructions.

610-2.7 PREMOLDED JOINT MATERIAL. Premolded joint material for expansion joints shall meet the requirements of ASTM D 1751.

610-2.8 JOINT FILLER. The filler for joints shall meet the requirements of Item P-605.

610-2.9 STEEL REINFORCEMENT. Reinforcing shall consist of Deformed and Plain Billet-Steel Bars conforming to the requirements of ASTM A 615, Welded Steel Wire Fabric conforming to the requirements of ASTM A 185, Welded Deformed Steel Fabric conforming to the requirements of ASTM A 497, or Bar Mats conforming to the requirements of ASTM A 184, as shown on the Plans.

610-2.10 COVER MATERIALS FOR CURING. Curing materials shall conform to one of the following specifications:

ASTM C 171	Waterproof Paper for Curing concrete

ASTM C 171	Polyethylene Sheeting for Curing Concrete

ASTM C 309, Type 1 or 2	Liquid Membrane-Forming Compounds for Curing Concrete

CONSTRUCTION METHODS

610-3.1 GENERAL. The Contractor shall furnish all labor, materials, and services necessary for, and incidental to, the completion of all work as shown on the drawings and specified herein. All machinery and equipment owned or controlled by the Contractor, which he proposes to use on the work, shall be of sufficient size to meet the requirements of the work, and shall be such as to produce satisfactory work; all work shall be subject to the inspection and approval of the Engineer.

610-3.2 CONCRETE COMPOSITION. The concrete shall develop a minimum compressive strength of 3,600 psi in 28 days as determined by test cylinders made in accordance with ASTM C 31 and tested in accordance with ASTM C 39. The concrete shall contain not less than 470 pounds of cement per cubic yard. The concrete shall contain 5% of entrained air, plus or minus 1%, as determined by ASTM C 231 and shall have a slump of not more than 4 inches as determined by ASTM C 143.

610-3.3 ACCEPTANCE SAMPLING AND TESTING. Concrete for each structure will be accepted on the basis of the compressive strength specified in paragraph 3.2. The concrete shall be sampled in accordance with ASTM C 172. Compressive strength specimens shall be made in accordance with ASTM C 31 and tested in accordance with ASTM C 39.

Concrete cylindrical test specimens shall be made in accordance with ASTM C 31 and tested in accordance with ASTM C 39. The Contractor shall cure and store the test specimens under such conditions as directed. The Engineer will make the actual tests on the specimens at no expense to the Contractor.

610-3.4 PROPORTIONING AND MEASURING DEVICES. When package cement is used, the quantity for each batch shall be equal to one or more whole sacks of cement. The aggregates shall be measured separately by weight. If aggregates are delivered to the mixer in batch trucks, the exact amount for each mixer charge shall be contained in each batch compartment. Weighing boxes or hoppers shall be approved by the Engineer and shall provide means of regulating the flow of aggregates into the batch box so that the required and exact weight of aggregates can be readily obtained.

610-3.5 CONSISTENCY. The consistency of the concrete shall be checked by the slump test specified in ASTM C 143.

610-3.6 MIXING. Concrete may be mixed at the construction site, at a central point, or in truck mixers. The concrete shall be mixed and delivered in accordance with the requirements of ASTM C 94.

610-3.7 MIXING CONDITIONS. The concrete shall be mixed only in quantities required for immediate use. Concrete shall not be mixed while the air temperature is below 40 °F without permission of the Engineer. If permission is granted for mixing under such conditions, aggregates or water, or both, shall be heated and the concrete shall be placed at a temperature not less than 50 °F nor more than 100 °F. The Contractor shall be held responsible for any defective work, resulting from freezing or injury in any manner during placing and curing, and shall replace such work at his/her expense.

Retempering of concrete by adding water or any other material shall not be permitted.

The delivery of concrete to the job shall be in such a manner that batches of concrete will be deposited at uninterrupted intervals.

610-3.8 FORMS. Concrete shall not be placed until all the forms and reinforcements have been inspected and approved by the Engineer. Forms shall be of suitable material and shall be of the type, size, shape, quality, and strength to build the structure as designed on the Plans. The forms shall be true to line and grade and shall be mortar-tight and sufficiently rigid to prevent displacement and sagging between supports. The Contractor shall bear responsibility for their adequacy. The surfaces of forms shall be smooth and free from irregularities, dents, sags, and holes.

The internal ties shall be arranged so that, when the forms are removed, no metal will show in the concrete surface or discolor the surface when exposed to weathering. All forms shall be wetted with water or with a nonstaining mineral oil which shall be applied shortly before the concrete is placed. Forms shall be constructed so that they can be removed without injuring the concrete or concrete surface. The forms shall not be removed before the expiration of at least 30 hours from vertical faces, walls, slender columns, and similar structures; forms supported by falsework under slabs, beams, girders, arches, and similar construction shall not be removed until tests indicate that at least 60% of the design strength of the concrete has developed.

610-3.9 PLACING REINFORCEMENT. All reinforcement shall be accurately placed, as shown on the Plans, and shall be firmly held in position during concreting. Bars shall be fastened together at intersections. The reinforcement shall be supported by approved metal chairs. Shop drawings, lists, and bending details shall be supplied by the Contractor when required.

Reinforcing bars shall be bent cold and shall conform accurately to the shape and dimensions shown on the diagram. In no case shall the radius of any bend be less than 4 times the diameter of the bar.

Place reinforcement as indicated on the Plans or as hereinafter specified. Rigidly block and wire in place, using metal or plastic supports or concrete blocks and securely tie at each intersection with annealed iron wire of at least 1/8 inch.

Do not splice bars at points not indicated on the Plans except with the consent of the Engineer. Such splices shall be at the points of minimum tensile stress and the lap shall be not less than 36 bar diameters.

Verify the quantity, size, and shape of the reinforcement against the structure drawings and make necessary corrections to the bar lists and bending schedules before ordering. Errors in the bar lists and/or bending schedules shall not be cause for adjustment of the contract prices.

If reinforcing bars are to be welded, follow AWS D12.1.

610-3.10 EMBEDDED ITEMS. Before placing concrete, any items that are to be embedded shall be firmly and securely fastened in place as indicated. All such items shall be clean and free from coating, rust, scale, oil, or any foreign matter. The embedding of wood shall be avoided. The concrete shall be spaded and consolidated around and against embedded items.

610-3.11 PLACING CONCRETE. All concrete shall be placed during daylight, unless otherwise approved. The concrete shall not be placed until the depth and character of foundation, the adequacy of forms and falsework, and the placing of the steel reinforcing have been approved. Concrete shall be placed as soon as practical after mixing and in no case later than 1 hour after water has been added to the mix. The method and manner of placing shall be such to avoid segregation and displacement of the reinforcement. Troughs, pipes, and chutes shall be used as an aid in placing concrete when necessary. Dropping the concrete a distance of more than 5 feet, or depositing a large quantity at one point, will not be permitted. Concrete shall be placed upon clean, damp surfaces, free from running water, or upon properly consolidated soil.

The concrete shall be compacted with suitable mechanical vibrators operating within the concrete. When necessary, vibrating shall be supplemented by hand spading with suitable tools to assure proper and adequate compaction. Vibrators shall be manipulated so as to work the concrete thoroughly around the reinforcement and embedded fixtures and into corners and angles of the forms. The vibration at any joint shall be of sufficient duration to accomplish compaction but shall not be prolonged to the point where segregation occurs. Concrete deposited under water shall be carefully placed in a compact mass in its final position by means of a tremie, a closed bottom dump bucket, or other approved method and shall not be disturbed after being deposited.

610-3.12 CONSTRUCTION JOINTS. When the placing of concrete is suspended, necessary provisions shall be made for joining future work before the placed concrete takes its initial set. For the proper bonding of old and new concrete, such provisions shall be made for grooves, steps, keys, dovetails, reinforcing bars or other devices as may be prescribed. The work shall be arranged so that a section begun on any day shall be finished during daylight of the same day. Before depositing new concrete on or against concrete which has hardened, the surface of the hardened concrete shall be cleaned by a heavy steel broom, roughened slightly, wetted, and covered with a neat coating of cement paste or grout.

610-3.13 EXPANSION JOINTS. Expansion joints shall be constructed at such points and of such dimensions as may be indicated on the drawings. The premolded filler shall be cut to the same shape as that of the surfaces being joined. The filler shall be fixed firmly against the surface of the concrete already in place in such manner that it will not be displaced when concrete is deposited against it.

610-3.14 DEFECTIVE WORK. Any defective work disclosed after the forms have been removed shall be immediately removed and replaced. If any dimensions are deficient, or if the surface of the concrete is bulged, uneven, or shows honeycomb, which in the opinion of the Engineer cannot be repaired satisfactorily, the entire section shall be removed and replaced at the expense of the Contractor.

610-3.15 SURFACE FINISH. All exposed concrete surfaces shall be true, smooth, free from open or rough spaces, depressions, or projections. The concrete in horizontal plane surfaces shall be brought flush with the finished top surface at the proper elevation and shall be struck-off with a straightedge and floated. Mortar finishing shall not be permitted, nor shall dry cement or sand-cement mortar be spread over the concrete during the finishing of horizontal plane surfaces.

When directed, the surface finish of exposed concrete shall be a rubbed finish. If forms can be removed while the concrete is still green, the surface shall be pointed and wetted and then rubbed with a wooden float until all irregularities are removed. If the concrete has hardened before being rubbed, a carborundum stone shall be used to finish the surface. When approved, the finishing can be done with a rubbing machine.

610-3.16 CURING AND PROTECTION. All concrete shall be properly cured and protected by the Contractor. The work shall be protected from the elements, flowing water, and from defacement of any nature during the building operations. The concrete shall be cured as soon as it has sufficiently hardened by covering with an approved material. Water-absorptive coverings shall be thoroughly saturated when placed and kept saturated for a period of at least 3 days for Type III Portland Cement and at least 7 days for Type I or Type II Portland Cement Concrete. All curing mats or blankets shall be sufficiently weighted or tied down to keep the concrete surface covered and to prevent the surface from being exposed to currents of air. Where wooden forms are used, they shall be kept wet at all times until removed to prevent the opening of joints and drying out of the concrete. Traffic shall not be allowed on concrete surfaces for 7 days after the concrete has been placed.

610-3.17 DRAINS OR DUCTS. Drainage pipes, conduits, and ducts that are to be encased in concrete shall be installed by the Contractor before the concrete is placed. The pipe shall be held rigidly so that it will not be displaced or moved during the placing of the concrete.

610-3.18 COLD WEATHER PROTECTION. When concrete is placed at temperatures below 40 °F, the Contractor shall provide satisfactory methods and means to protect the mix from injury by freezing. The aggregates, or water, or both, shall be heated in order to place the concrete at temperatures between 50 and 100 °F.

Calcium chloride may be incorporated in the mixing water when directed by the Engineer. Not more than 2 pounds of Type 1 nor more than 1.6 pounds of Type 2 shall be added per bag of cement. After the concrete has been placed, the Contractor shall provide sufficient protection such as cover, canvas, framework, heating apparatus, etc., to enclose and protect the structure and maintain the temperature of the mix at not less than 50 °F until at least 60% of the designed strength has been attained.

610-3.19 FILLING JOINTS. All joints which require filling shall be thoroughly cleaned, and any excess mortar or concrete shall be cut out with proper tools. Joint filling shall not be started until after final curing and shall be done only when the concrete is completely dry. The cleaning and filling shall be carefully done with proper equipment and in a manner to obtain a neat looking joint free from excess filler.

METHOD OF MEASUREMENT

610-4.1 Portland cement concrete will be measured by the number of cubic yards of concrete complete in place and accepted. In computing the volume of concrete for payment, the dimensions used will be those shown on the Plans or ordered by the Engineer. No measurements or other allowances will be made for forms, falsework, cofferdams, pumping, bracing, expansion joints, or finishing of the concrete. No deductions will be made for the volumes of reinforcing steel or embedded items.

610-4.2 Reinforcing steel will be measured by the calculated theoretical number of pounds placed, as shown on the Plans, complete in place and accepted. The unit weight used for deformed bars will be the weight of plain square or round bars of equal nominal size. If so indicated on the Plans, the weight to be paid for will include the weight of metal pipes and drains, metal conduits and ducts, or similar materials indicated and included.

BASIS OF PAYMENT

610-5.1 Payment will be made at the contract unit price per cubic yard for structural portland cement concrete and per pound for reinforcing steel.

Payment will be made under:

Item P-610a	Structural Portland Cement Concrete - per cubic yard

Item P-610b	Steel Reinforcement - per pound

TESTING REQUIREMENTS

ASTM C 31	Making and Curing Test Specimens in the Field

ASTM C 39	Compressive Strength of Cylindrical Concrete Specimens

ASTM C 136	Sieve or Screen Analysis of Fine and Coarse Aggregate

ASTM C 138	Unit Weight, Yield, and Air Content of Concrete

ASTM C 143	Slump of Portland Cement Concrete

ASTM C 231	Air Content of Freshly Mixed Concrete by the Pressure Method

WAQTC FOP for AASHTO T 27 and T 11	Coarse and Fine Aggregate Gradation

MATERIAL REQUIREMENTS

ASTM A 184	Fabricated Deformed Steel Bar Mats for Concrete Reinforcement

ASTM A 185	Welded Steel Wire Fabric for Concrete Reinforcement

ASTM A 497	Welded Deformed Steel Wire Fabric for Concrete Pavement

ASTM A 615	Deformed and Plain Billet-Steel Bars for Concrete Reinforcement

ASTM C 33	Concrete Aggregates

ASTM C 94	Ready-Mixed Concrete

ASTM C 150	Portland Cement

ASTM C 171	Sheet Materials for Curing Concrete

ASTM C 260	Air-Entraining Admixtures for Concrete

ASTM C 309	Liquid Membrane-Forming Compounds for Curing Concrete

ASTM C 618	Fly Ash and Raw or Calcined Natural Pozzolan for Use as a Mineral Admixture in Portland Cement Concrete

ASTM D 1751	Preformed Expansion Joint Fillers for Concrete Paving and Structural Construction

ASTM D 1752	Preformed Sponge Rubber and Cork Expansion Joint Fillers for Concrete Paving and Structural Construction

AWS D12.1	Recommended Practices for Welding Reinforcing Steel, Metal Inserts and Connections in Reinforced Concrete Construction

## ITEM P-620	RUNWAY AND TAXIWAY PAINTING

DESCRIPTION

620-1.1 This item shall consist of the painting of numbers, markings, and stripes on the surface of runways, taxiways, and aprons, in accordance with these Specifications and at the locations shown on the Plans, or as directed by the Engineer.

MATERIALS

620-2.1 MATERIALS ACCEPTANCE. The Contractor shall furnish manufacturer's certified test reports for materials shipped to the project. The certified test reports shall include a statement that the materials meet the specification requirements. The reports can be used for material acceptance or the Engineer may perform verification testing. The reports shall not be interpreted as a basis for payment. The Contractor shall notify the Engineer upon arrival of a shipment of materials to the site.

620-2.2 PAINT. Paint shall be waterborne or solvent base in accordance with the requirements of paragraph 620-2.2, a. or b. Paint shall be furnished in white (37925) and yellow (33538 or 33655) in accordance with Federal Standard No 595. Paint shall be furnished in Type II (fast drying time for no-pick-up) when tested in accordance with ASTM D 711.

- Waterborne. Paint shall meet the requirements of Federal Specification TT-P-1952D, Type II.

- Solvent Base. Paint shall meet the requirements of Federal Specification A-A-2886A, Type II, or the State of Alaska DOT&PF maintenance specification for "Traffic Paint - No-Heat Instant Dry Pavement Marking Material”.

620-2.3 REFLECTIVE MEDIA. Glass beads shall meet the requirements of Fed. Spec. TT-B-1325, Type I, gradation A. Glass beads shall be treated with adhesion promoting and/or flotation coatings as specified by the manufacturer of the paint.

CONSTRUCTION METHODS

620-3.1 WEATHER LIMITATIONS. The painting shall be performed only when the surface is dry and when the surface temperature is at least 40 °F and rising and the pavement surface temperature is at least 5 °F above the dew point.

620-3.2 EQUIPMENT. Equipment shall include the apparatus necessary to properly clean the existing surface, a mechanical marking machine, a bead dispensing machine, and such auxiliary hand-painting equipment as may be necessary to satisfactorily complete the job.

The mechanical marker shall be an atomizing spray-type marking machine suitable for application of traffic paint. It shall produce an even and uniform film thickness at the required coverage and shall apply markings of uniform cross sections and clear-cut edges without running or spattering and without over spray.

620-3.3 PREPARATION OF SURFACE. Immediately before application of the paint, the surface shall be dry and free from dirt, grease, oil, laitance, or other foreign material which would reduce the bond between the paint and the pavement. The area to be painted shall be cleaned by sweeping and blowing or by other methods as required to remove all dirt, laitance, and loose materials. Areas which cannot be satisfactorily cleaned by brooming and blowing shall be scrubbed as directed with a 10% solution of tri-sodium phosphate or an equally suitable solution. After scrubbing, the solution shall be rinsed off and the surface dried prior to painting.

620-3.4 LAYOUT OF MARKINGS. The proposed markings shall be laid out in advance of the paint application. The locations of markings to receive glass beads shall be shown on the Plans. Space control points at such intervals to ensure accurate location of all markings. Provide an experienced technician to supervise the location, alignment, layout dimensions, and application of the paint.

620-3.5 APPLICATION. Paint shall be applied at the locations and to the dimensions and spacing shown on the Plans. Paint shall not be applied until the layout and condition of the surface have been approved by the Engineer.

The edges of the markings shall not vary from a straight line more than 1/2 inch in 50 feet, and the marking dimensions and spacings shall be within the following tolerances:

Dimension and Spacing	Tolerance

| Less than 36 inches | 1/2 inch |
| --- | --- |
| 36 inches to 6 feet | 1 inch |
| 6 feet to 60 feet | 2 inches |
| Over 60 feet | 3 inches |

The paint shall be mixed and applied in accordance with the manufacturer's instructions. The addition of thinner will not be permitted. The paint shall be applied to the pavement with a marking machine at the rate shown in Table 1

TABLE 1.    APPLICATION RATES FOR PAINT AND GLASS BEADS

| Paint Type | Paint, ft2/gal maximum | Glass Beads lb/gal of paint (±2 oz.) |
| --- | --- | --- |
| Waterborne | 115 | 7 |
| Solvent Base | 40 | 6 |

Pressure apply the glass beads on the marked areas at the locations shown on the Plans using a mechanical dispenser mounted not more than 12 inches behind the paint dispenser. Beads shall be applied at the rate shown in Table 1 and shall adhere to the cured paint or all marking operations shall cease until corrections are made.

All emptied containers shall be returned to the paint storage area for checking by the Engineer. The containers shall not be removed from the airport or destroyed until authorized by the Engineer.

620-3.6 PROTECTION. After application of the paint, all markings shall be protected from damage until the paint is dry. All surfaces shall be protected from excess moisture and/or rain and from disfiguration by spatter, splashes, spillage, or drippings of paint.

METHOD OF MEASUREMENT

620-4.1 The quantity of runway and taxiway markings to be paid for will be the number of square feet of painting and the number of pounds of reflective media, performed in accordance with the Specifications and accepted by the Engineer.

BASIS OF PAYMENT

620-5.1 Payment will be made at the respective contract price per square foot for runway and taxiway painting and per pound for reflective media.

Payment will be made under:

Item P-620a	Runway and Taxiway Painting - per square foot

Item P-620b	Reflective Media - per pound

TESTING REQUIREMENTS

ASTM C 371	Wire-Cloth Sieve Analysis of Nonplastic Ceramic Powders

ASTM D 92	Flash and Fire Points by Cleveland Open Cup

ASTM D 711	No-Pick-Up Time of Traffic Paint

ASTM D 968	Abrasion Resistance of Organic Coatings by Falling Abrasive

ASTM D 1652	Epoxy Content of Epoxy Resins

ASTM D 2074	Total Primary, Secondary, and Tertiary Amine Values of Fatty Amines by Alternative Indicator Method

ASTM D 2240	Rubber Products-Durometer Hardness

ASTM G 53	Operating Light and Water-Exposure Apparatus (Florescent UV-Condensation Type) for Exposure of Nonmetallic Materials.

Federal Test Method	Paint, Varnish, Lacquer and Related Materials; Methods of Inspection,

Standard No. 141	Sampling and Testing

## MATERIAL REQUIREMENTS

Alaska DOT/PF	Traffic Paint - No-Heat Instant Dry Pavement Marking Material; White and Yellow

ASTM D 476	Titanium Dioxide Pigments

Code of Federal Regulations	40 CFR Part 60, Appendix A, 29 CFR Part 1910.1200

Commercial Item Description 	Paint, Traffic, Solvent Based

(CID) A-A 2886A

Fed. Spec. TT-B-1325	Beads (Glass Spheres) Retroreflective

Fed. Spec. TT-P-1952D	Paint, traffic and Airfield Marking, Waterborne

Federal Standard 595	Colors used in Government Procurement

ITEM P-625	COAL-TAR PITCH EMULSION SEAL COAT

DESCRIPTION

625-1.1 This item shall consist of an application of a coal-tar emulsion seal coat, with or without mineral aggregate, applied on an existing, previously prepared bituminous surface, in accordance with these Specifications for the area shown on the Plans or as designated by the Engineer. The material is intended for use as a fuel-resistant sealer.

MATERIALS

625-2.1 AGGREGATE. The aggregate shall either be a natural or manufactured angular aggregate and shall be composed of clean, hard, durable, uncoated particles, free from lumps of clay and all organic matter. The aggregate shall meet the gradation in Table 1, when tested in accordance with WAQTC FOP for AASHTO T 27 and T 11.

TABLE 1.    GRADATION OF AGGREGATES

| Sieve size | Percent Passing, By Weight |
| --- | --- |
| No. 8 | 100 |
| No. 16 | 97-100 |
| No. 20 | 85-100 |
| No. 30 | 15-85 |
| No. 50 | 2-10 |
| No. 100 | 0-2 |

625-2.2 BITUMINOUS MATERIALS. The bituminous material shall be a coal-tar pitch emulsion prepared from a high temperature, coal-tar pitch conforming to the requirements of ASTM D 490, grade 11/12. Oil and water gas tar shall not be used even though they comply with ASTM D 490. The coal-tar pitch emulsion shall conform to all requirements of ASTM D 5727, except that the water content shall not exceed 50%.

625-2.3 WATER. The water used in mixing shall be potable and free from harmful soluble salts. The temperature of the water added during mixing shall be at least 50 °F. The pH of the water, added during mixing, shall conform to the requirements of the coal-tar emulsion manufacturer.

COMPOSITION AND APPLICATION

625-3.1 COMPOSITION. The coal-tar pitch emulsion seal coat shall consist of a mixture of coal-tar pitch emulsion, water, and aggregate in proportions that fall within the ranges shown in Table 2.

625-3.2 JOB MIX FORMULA. The Contractor shall submit the recommended formulation of water, emulsion, and aggregate and application rate proposed for use to the Engineer at least 15 calendar days prior to the start of operations. The mix design shall be within the range shown in Table 2. No seal coat shall be produced for payment until a job mix formula has been approved by the Engineer. The job mix formula for each mixture shall be in effect until modified in writing by the Engineer.

TABLE 2.    COMPOSITION OF MIXTURE

| Type of Seal Coat | Water gal/gal of emul. | Aggregate lb/gal of emul. | Application Rate gal/yd2 (per application) |
| --- | --- | --- | --- |
| Sand Slurry | 0.15 (max) | 2-5 | 0.15-0.20 |
| Plain Emulsion | 0.10 (max) | -- | 0.08-0.10 |

625-3.3 APPLICATION RATE. The sand slurry coal-tar emulsion seal coat shall be applied in 2 coats. The application rate submitted with the job mix formula shall be verified during placement of the test section and shall fall within the limits shown in Table 2.

625-3.4 TEST SECTION. Prior to full production, the Contractor shall prepare a quantity of mixture in the proportions shown in the approved mix design. The amount of mixture shall be sufficient to place a test section a minimum of 250 yd2 at the rate specified in the job mix formula. The area to be tested will be designated by the Engineer and will be located on a representative section of the pavement to be seal coated. The actual application rate will be determined by the Engineer during placement of the test section and will depend on the condition of the pavement surface.

The test section shall be used to verify the adequacy of the mix design and to determine the application rate. The same equipment and method of operations shall be used on the test section as will be used on the remainder of the work.

If the test section should prove to be unsatisfactory, the necessary adjustments to the mix composition, application rate, placement operations, and equipment shall be made. Additional test sections shall be placed and evaluated, if required. Full production shall not begin without the Engineer's approval.

CONSTRUCTION METHODS

625-4.1 WEATHER LIMITATIONS. The seal coat shall not be applied when the surface is wet or when the humidity or impending weather conditions will not allow proper curing. The seal coat shall be applied only when the pavement surface temperature is 60 °F or higher.

625-4.2 EQUIPMENT AND TOOLS. The Contractor shall furnish all equipment, tools, and machinery necessary for the performance of the work.

- Distributors. Distributors or spray units used for the spray application of the seal coat shall be self-propelled and capable of uniformly applying 0.15 to 0.55 gal/yd2 of material over the required width of application. Distributors shall be equipped with removable manhole covers, tachometers, pressure gauges, and volume-measuring devices.

The mix tank shall have a mechanically powered, full-sweep mixer with sufficient power to move and homogeneously mix the entire contents of the tank.

The distributor shall be equipped with a positive placement pump so that a constant pressure can be maintained on the mixture to the spray nozzles.

- Mixing Equipment. The mixing machine shall have a continuous flow mixing unit capable of accurately delivering a predetermined proportion of aggregate, water, and emulsion, and of discharging the thoroughly mixed product on a continuous basis. The mixing unit shall be capable of thoroughly blending all ingredients together and discharging the material to the spreader box without segregation.

- Spreading Equipment. Attach to the mixing machine a mechanical-type squeegee distributor, equipped with flexible material in contact with the surface to prevent loss of slurry from the spreader box. It shall be maintained to prevent loss of slurry on varying grades and adjusted to assure uniform spread. There shall be a lateral control device and a flexible strike-off capable of being adjusted to lay the slurry at the specified rate of application. The spreader box shall have an adjustable width. The box shall be kept clean; coal-tar emulsion and aggregate build-up on the box shall not be permitted.

- Calibration. The Contractor shall furnish all equipment and materials and labor necessary to calibrate the equipment. It shall be calibrated to assure that it will produce and apply a mix that conforms to the job mix design. Commercial equipment should be provided with a method of calibration by the manufacturer. All calibrations shall be made with the approved job materials prior to applying the seal coat to the pavement. A copy of the calibration test results shall be furnished to the Engineer.

625-4.3 PREPARATION OF PAVEMENT SURFACE. Bituminous pavement surfaces which have been softened by petroleum derivatives or have failed due to any other cause shall be removed to the full depth of the damage and replaced with new bituminous concrete similar to that of the existing pavement. Areas of the pavement surface to be treated shall be in a firm consolidated condition. They shall be sufficiently cured so that there is no concentration of oils on the surface. This can usually be determined by pouring water on the surface to be treated. If the water, after standing for a short period, picks up a film of oil, the surface is not sufficiently cured for the application of emulsion.

A minimum of 15 days shall elapse between the placement of a bituminous surface course and the application of the seal coat.

625-4.4 CLEANING EXISTING SURFACE. Prior to placing the seal coat, the surface of the pavement shall be clean and free from dust, dirt, or other loose foreign matter, grease, oil, or any type of objectionable surface film. When directed by the Engineer, the existing surface shall be cleaned with wire brushes and a power blower.

Where vegetation exists in cracks, the vegetation shall be removed and the cracks cleaned to a depth of 2 inches, where practicable. These cracks shall be treated with a concentrated solution of an herbicide approved by the Engineer.

Route out cracks less than 1/2 inch wide and seal them. Fill existing cracks greater than 1/2 inch wide with sealer and aggregate meeting Subsection 625-2.1. Crack sealer shall meet the requirements of ASTM D 3405 remaining flexible to -40 °F. Areas that have been subjected to fuel or oil spillage shall be wire brushed to remove any dirt accumulations. The area shall then be primed with shellac or a synthetic resin to prevent the seal coat from debonding.

625-4.5 TACK COAT. A tack coat shall be applied only if recommended by the emulsion supplier. After the surface has been prepared, a tack coat of 3 parts water to 1 part emulsified binder, as specified in Subsection 625-2.2, shall be applied at the rate of 0.05 to 0.10 gal/yd2 of surface.

When a tack coat is not specified, the pavement shall be dampened with a fog spray of water if recommended by the supplier. No standing water shall remain on the surface.

Following the application, the surface shall be allowed to cure without being disturbed for such period of time as may be necessary to permit adhesion of the seal coat. This period shall be determined by the Engineer. Suitable precautions shall be taken by the Contractor to protect the surface against damage during this interval.

625-4.6 APPLICATION OF PLAIN EMULSION. Plain emulsion shall be applied at a uniform rate with a distributor at the rate as determined in Subsection 625-3.4. When it is necessary to dilute the emulsion in older to aid application, the emulsion may be diluted with clean water but not by more than 10%.

625-4.7 APPLICATION OF SAND SLURRY. The sand slurry shall be applied at a uniform rate with a distributor or squeegee at the rate determined in Subsection 625-3.4. When the emulsion, water, and aggregate are blended, the material shall be premixed to produce a homogeneous mixture of uniform consistency. The quantities of materials to be combined in each batch shall be in accordance with the approved mix design.

The mixing sequence of the various components shall be the same as indicated in the job mix formula. After all constituents are in the mixer, the mixing shall continue for approximately 5 minutes or longer, if necessary. The mixing shall produce a smooth, free flowing homogeneous mixture of uniform consistency. Slow mixing shall be continuous from the time the emulsion is placed into the mixer until the slurry is applied by distributor truck or poured into the spreading equipment. During the entire mixing process, no breaking, segregating, or hardening of the emulsion nor balling, lumping, or swelling of the aggregate shall be permitted. The slurry shall be applied at a uniform rate to provide the quantity determined during placement of the test strip.

When a spreader box is used, a sufficient amount of slurry shall be fed in the spreader box to keep a full supply against the full width of the squeegee, so that complete coverage of all surface voids and cracks is obtained.

Manufacturer's recommendations regarding application by spraying or squeegeeing should be followed. In areas inaccessible to equipment, the slurry may be applied by means of a hand squeegee.

Upon completion of the work, the seal coat shall have no pinholes, bare spots, or cracks through which liquids or foreign matter could penetrate to the underlying pavement. The finished surface shall present a uniform texture.

Each application shall be allowed to dry thoroughly before the next coat is applied. Suitable precautions shall be taken by the Contractor to protect the surface against damage during this interval.

625-4.8 CURING. The mixture shall be permitted to dry for a minimum of 24 hours after the final application before opening to traffic and shall be sufficiently cured to drive over without damage to the seal coat. Any damage to the uncured mixture will be the responsibility of the Contractor to repair.

625-4.9 HANDLING. The mixture shall be continuously agitated from the initial mixing until its application on the pavement surface. The distributor or applicator, pumps, and all tools shall be maintained in a satisfactory working condition.

QUALITY CONTROL

625-5.1 CONTRACTOR'S CERTIFICATION. The Contractor shall furnish the manufacturer's certification that each consignment of emulsion shipped to the project meets the requirements of ASTM D 5727, except that the water content shall not exceed 50%. The certification shall also indicate the solids and ash content of the emulsion and the date the tests were conducted. The certification shall be delivered to the Engineer prior to the beginning of work.

625-5.2 INSPECTION. The Contractor shall have an independent technical consultant on the job site during the seal coat operations. The consultant shall have knowledge of the materials, procedures, and equipment described in this specification and shall assist the Contractor regarding proper mixing of the component materials and application of the seal coat. The consultant shall have a minimum of 3 years experience in the use of coal-tar seal coats. Documentation of this experience shall be furnished to the Engineer prior to the start of operations.

METHOD OF MEASUREMENT

625-6.1 The coal-tar pitch emulsion will be measured by the ton of undiluted coal-tar emulsion.

625-6.2 The mineral aggregate will be measured by the ton.

BASIS OF PAYMENT

625-7.1 Payment will be made at the contract unit prices for materials complete in place, including acceptable test sections.

The cost of the technical consultant is subsidiary.

Payment will be made under:

Item P-625a	Coal-Tar Pitch Emulsion - per ton

Item P-625b	Aggregate - per ton

TESTING REQUIREMENTS

WAQTC FOP for AASHTO T 27 and T 11	Coarse and Fine Aggregate Gradation

MATERIAL REQUIREMENTS

ASTM D 490	Tars, (For Use in Road Construction)

ASTM D 3450	Joint Sealants, Hot Poured, for Concrete and Asphalt Pavements

ASTM D 5727	Emulsified Refined Coal Tar (Mineral Colloid Type)

### ITEM P-626	EMULSIFIED ASPHALT SLURRY SEAL SURFACE TREATMENT

DESCRIPTION

626-1.1 This item shall consist of a mixture of emulsified asphalt, mineral aggregate, and water properly proportioned, mixed, and spread on an asphalt prepared underlying course or existing wearing course in accordance with these Specifications and shall conform to the dimensions shown on the Plans or as directed by the Engineer.

MATERIALS

626-2.1 AGGREGATE. The aggregate shall consist of sound and durable manufactured sand, slag, crusher fines, crushed stone, or a combination thereof. The aggregate shall be clean and free from vegetable matter, dirt, and other deleterious substances. The aggregate shall have a sand equivalent of not less than 45% when tested in accordance with ASTM D 2419. The aggregate shall show a loss of not more than 35% when tested in accordance with ASTM C 131. The sodium sulfate soundness loss shall not exceed 12%, or the magnesium soundness loss shall not exceed 20% after 5 cycles when tested in accordance with ASTM C 88. Aggregate shall be 100% crushed. Aggregates shall have a minimum degradation value of 50 when tested in accordance with ATM 313.

The combined aggregate shall conform to the gradation shown in Table 1 when tested in accordance with ASTM C 136 and ASTM C 117.

TABLE 1.    GRADATION OF AGGREGATES

| Sieve Size | Percent by Weight Passing Sieve |
| --- | --- |
|  | Type I | Type II | Type III |
| 3/8 in. | 100 | 100 | 100 |
| No. 4 | 100 | 90 - 100 | 70 - 90 |
| No. 8 | 90 - 100 | 65 - 90 | 45 - 70 |
| No. 16 | 65 - 90 | 45 - 70 | 28 - 50 |
| No. 30 | 40 - 65 | 30 - 50 | 19 - 34 |
| No. 50 | 25 - 42 | 18 - 30 | 12 - 25 |
| No. 100 | 15 - 30 | 10 - 21 | 7 - 18 |
| No. 200 | 10 - 20 | 5 - 15 | 5 - 15 |
| Residual asphalt content, percent dry weight of aggregate | 10% - 16% | 7.5% - 13.5% | 6.5% - 12% |

The job mix formula (mix design) shall be run using aggregate within the gradation band for the desired type shown in Table 1. Once the mix design has been submitted and approved, the aggregate used on the project shall not vary by more than the tolerances shown in Table 2. At no time shall the aggregate used go out of the gradation bands in Table 1.

The aggregate will be accepted at the job location or stockpile. The stockpile will be accepted based on 5 gradation tests samples in accordance with ASTM D 75. If the average of the 5 tests is within the gradation tolerances, the materials will be accepted. If the tests show the material to be out of tolerance, the Contractor has the choice either to remove the material or blend other aggregates with the stockpile material to bring it into specification. Materials used in blending shall meet the quality tests before blending and shall be blended in a manner to produce a consistent gradation. This blending may require a new mix design.

Screening shall be required at the project stockpile site if there are any problems created by having oversize materials in the mix.

Precautions shall be taken to prevent segregation of the aggregate in storing and handling. The stockpile shall be kept in areas that drain readily.

- Aggregate Tolerance. Once the mix design has been accepted, the aggregate gradation used on the project may vary from the aggregate gradation used in the mix design on each sieve by the percentages shown in Table 2. If the project aggregate fails to remain within this tolerance, a new mix design will be required by the Engineer at the expense of the Contractor.

TABLE 2.    TOLERANCES

| Sieve Size | Tolerance, percent passing by weight |
| --- | --- |
| 3/8 in. | ± 5 |
| No. 4 | ± 5 |
| No. 8 | ± 5 |
| No. 16 | ± 5 |
| No. 30 | ± 5 |
| No. 50 | ± 4 |
| No. 100 | ± 3 |
| No. 200 | ± 2 |
| Residual Asphalt, percent dry weight of aggregate | ± 1 |

626-2.2 MINERAL FILLER. If mineral filler, in addition to that naturally present in the aggregate, is necessary, it shall meet the requirements of ASTM D 242 and shall be used in the amounts required by the mix design. The mineral filler shall be considered as part of the aggregate.

626-2.3 EMULSIFIED ASPHALT. The emulsified asphalt shall conform to the requirements of ASTM D 977 and/or 2397 and shall be SS, CSS, CQS, or QS type emulsions.

626-2.4 WATER. All water used in making the slurry shall be potable and free from harmful soluble salts and chemicals.

COMPOSITION AND APPLICATION

626-3.1 COMPOSITION. The slurry seal shall consist of a mixture of emulsified asphalt, mineral aggregate, and water.

626-3.2 JOB MIX FORMULA. No slurry seal for payment shall be placed until a mix design has been approved by the Engineer. The mix design shall be developed by a laboratory with experience in designing slurry seal mixes and a signed copy shall be submitted in writing by the Contractor to the Engineer at least 10 days prior to the start of operations.

The laboratory report (mix design) shall indicate the proportions of aggregates, mineral filler (min. and max.), water (min. and max.) and asphalt emulsion based on the dry aggregate weight. It shall also report the quantitative effects of moisture content on the unit weight of the aggregate (bulking effects). The mix design shall be in effect until modified in writing by the Engineer. Should a change in sources of materials be made, a new mix design shall be established before the new material is used.

The Contractor shall submit to the Engineer for approval a complete mix design on the materials proposed for use, prepared and certified by an approved laboratory. Compatibility of the aggregate, emulsion, mineral filler, and other additives shall be verified by the mix design. The mix design shall be made with the same aggregate and grade of emulsified asphalt that the Contractor will provide on the project. At a minimum the required tests and values needed are as follows:

| TEST | DESCRIPTION | SPECIFICATION |
| --- | --- | --- |
| ISSA TB-100 | Wet Track Abrasion Loss, One Hour Soak | 50 g/ft² Max |
| ISSA TB-115 | Determination of Slurry Seal Compatibility | Pass |

626-3.3 APPLICATION RATE. Unless otherwise specified, the slurry seal shall be applied to at the application rates shown in Table 3 for that gradation of material used. The rate of application shall not vary more than ± 2 lb/yd².

TABLE 3.    APPLICATION RATES

Pounds of mixture per square yard

| Type I | Type II | Type III |
| --- | --- | --- |
| 8 - 12 | 12 - 20 | 18 - 30 |

626-3.4 TEST SECTIONS. Test sections, of 60 yd2 each, shall be placed prior to the start of the slurry seal work in the presence of the Engineer. The test area will be designated by the Engineer and will be located on the existing pavement. Test strips shall be made by each machine after calibration. Samples of the slurry seal may be taken and the mix consistency verified by using ISSA TB-106 Slurry Seal Consistency test. In addition, the proportions of the individual materials may be verified by the Engineer by using the calibration information provided after machine calibration. If any test does not meet specification requirements, additional tests shall be made at the expense of the Contractor, until an acceptable test strip is placed.

CONSTRUCTION METHODS

626-4.1 WEATHER LIMITATIONS. The slurry seal shall not be applied if the pavement temperature is below 60 °F. No slurry seal shall be applied when there is danger that the finished product will freeze before 24 hours. The mixture shall not be applied when weather conditions prolong opening to traffic beyond a reasonable time.

626-4.2 EQUIPMENT AND TOOLS. The Contractor shall furnish all equipment, tools, and machinery necessary for the performance of this work.

- Slurry Mixing Equipment. The machine shall be specifically designed and manufactured to lay slurry seal. The material shall be mixed by a self-propelled slurry seal mixing machine of either truck mounted or continuous run design. Either type machine shall be able to accurately deliver and proportion the aggregate, emulsified asphalt, mineral filler, and water to a revolving mixer and discharge the mixed product on a continuous flow basis. The machine shall have sufficient storage capacity for materials to maintain an adequate supply to the proportioning controls.

If continuous run equipment is used, the machine shall be equipped to allow the operator to have full control of the forward and reverse speed of the machine during application of the slurry seal, with a self-loading device, with opposite side driver stations, all part of original equipment manufacturer design.

The aggregate shall be prewetted immediately prior to mixing with the emulsion. The mixing unit of the mixing chamber shall be capable of thoroughly blending all ingredients. No excessive mixing shall be permitted. The mixing machine shall be equipped with a fines feeder that provides an accurate metering device or method to introduce a predetermined proportion of mineral filler into the mixer at the same time and location that the aggregate is fed into the mixer.

The mixing machine shall be equipped with a water pressure system and fog-type spray bar adequate for complete fogging of the surface with an application of 0.05 to 0.10 gal/yd² preceding the spreading equipment.

Sufficient machine storage capacity to mix properly and apply a minimum of 5 tons of the slurry shall be provided. Proportioning devices shall be calibrated prior to placing the slurry seal.

- Slurry Spreading Equipment. The mixture shall be spread uniformly by means of a conventional surfacing spreader box attached to the mixer and equipped to agitate and spread the material evenly throughout the box. A front seal shall be provided to insure no loss of the mixture at the surface contact point. The rear seal shall act as the final strike-off and shall be adjustable. The spreader box and rear strike-off shall be so designed and operated that a uniform consistency is achieved to produce a free flow of material to the rear strike-off. The spreader box shall have suitable means provided to side shift the box to compensate for variations in the pavement geometry. A burlap drag or other approved screed may be attached to the rear of the spreader box to provide a uniform mat.

A continuous spreading operation shall be maintained by means of a continuous charging operation so that a minimum of construction joints occur. Continuous operating is defined as one in which the spreading operation progresses prior to initial setting or breaking of the slurry mix, which starts within approximately 15 minutes.

Provide suitable storage facilities for the asphalt emulsion, using containers equipped to prevent water from entering the emulsion. If necessary, suitable heat shall be provided to prevent freezing.

- Auxiliary Equipment. Other tools or equipment such as brushes, hand squeegees, hose equipment, tank trucks, water distributors and flushers, power blowers, barricades, etc., shall be provided as required.

- Roller. The roller, if required, shall be a self-propelled pneumatic-tired roller capable of exerting a contact pressure during rolling of 50 psi. It shall be equipped with a water spray system, to be used if the slurry is picking up on the tires during rolling.

- Tack Coat and Distributor. Normally a tack coat is not required unless the surface to be covered is extremely dry and raveled or is concrete or brick. If required, the tack coat should consist of one part emulsified asphalt and three parts water. The emulsified asphalt may be the same as that used in the mix. Pressure distributors used for application of the diluted asphalt emulsion tack coat shall be self-propelled, equipped with pneumatic tires, and capable of uniformly applying 0.05 to 0.15 gal/yd² of the diluted emulsion over the required width of application. Distributors shall be equipped with tachometers, pressure gages, and volume-measuring devices. The tack coat shall be applied at least 2 hours before the slurry seal but within the same day.

626-4.3 EQUIPMENT CALIBRATION. Each slurry mixing unit to be used on the project shall be calibrated in the presence of the Engineer prior to construction. Previous calibration documentation covering the exact materials to be used may be accepted by the Engineer provided they were made during the calendar year. The documentation shall include an individual calibration of each material at various settings, which can be related to the machine's metering devices. No machine will be allowed to work on the project until the calibration has been completed and/or accepted.

626-4.4 PREPARATION OF EXISTING SURFACE. Prior to placing the tack coat and slurry seal coat, unsatisfactory areas shall be repaired and the surface shall be cleaned of dust, dirt, or other loose foreign matter, grease, oil, excessive rubber accumulation, or any type of objectionable surface film. Any standard cleaning method will be acceptable except that water flushing will not be permitted in areas where considerable cracks are present in the pavement surface.

Any painted stripes or markings on the surface of the runways or taxiways to be treated, shall be removed.

Cracks wider than 1/4 inch shall be cleaned with compressed air, and sealed with a compatible crack sealer prior to applying the slurry seal. Cracks wider than 3/4 inch should be pre-filled and sealed with the slurry mixture prior to surfacing. Cracks that show evidence of vegetation shall be cleaned and treated with an approved herbicide.

626-4.5 APPLICATION OF SLURRY SEAL COAT. Charge the mixture in the following order:

- Water

- Aggregate

- Asphalt Emulsion

No violent mixing will be permitted. Maintain temperature range at the mixer between 90 and 120 °F. Mix until a uniform coating of the aggregate is obtained. Continue mixing until the mixture is discharged into the spreader box. Discard the entire batch if there is evidence that the emulsion has broken.

The surface shall be prewet by fogging ahead of the slurry spreader box. Water used in prewetting the surface shall be applied at such a rate that the entire surface is damp with no apparent flowing water in front of the slurry spreader box. The slurry mixture shall be of the desired consistency when deposited on the surface, and no additional elements shall be added. Total time of mixing shall not exceed 2 minutes. A sufficient amount of slurry shall be carried in all parts of the spreader box at all times so that complete coverage of all surface voids and cracks is obtained. Care shall be taken not to overload the spreader box which shall be towed at a slow and uniform rate not to exceed 5 mph. No lumping, balling, or unmixed aggregate shall be permitted. No segregation of the emulsion and fines from the coarse aggregate will be permitted. If the coarse aggregate settles to the bottom of the mix, the slurry shall be removed from the pavement surface. A sufficient amount of slurry shall be fed into the box to keep a full supply against the full width of the spreader box. The mixture shall not be permitted to overflow the sides of the spreader box. No breaking of the emulsion will be allowed in the spreader box.

Apply the slurry seal to form a film with a maximum thickness of 3/8 inch. Isolated depressions and cracks may have a thickness greater than 3/8 inch in order to obtain a smooth surface.

The finished surface shall have no more than 4 tear or drag marks greater than 1/2 inch wide and 4 inches long in any 12 foot by 22 foot section. It shall have no tear or drag marks greater than 1 inch wide and 3 inches long.

The finished surface shall have no transverse ripples of 1/4 inch or more in depth, as measured with a 10-foot straight edge laid upon the surface.

Adjacent lanes shall be lapped at the edges a minimum of 2 inches with a maximum of 4 inches to provide complete sealing at the overlap. Construction longitudinal and transverse joints shall be neat and uniform without buildup, uncovered areas, or unsightly appearance. All joints shall have no more than 1/4 inch difference in elevation when measured across with a 10-foot straight edge.

After application of the slurry seal, the surface shall be rolled with a pneumatic-tired roller a minimum of 2 complete passes. The roller shall be operated at a tire pressure of approximately 50 psi.

The fresh slurry seal application shall be protected by barricades and markers and permitted to dry for 4 to 24 hours, depending on weather conditions. Any damage to uncured slurry shall be repaired at the expense of the Contractor.

In areas where the spreader box cannot be used, the slurry shall be applied by means of a hand squeegee. Upon completion of the work, the seal coat shall have no holes, bare spots, or cracks through which liquids or foreign matter could penetrate to the underlying pavement. The finished surface shall present a uniform and skid resistant texture satisfactory to the Engineer. All wasted and unused material and all debris shall be removed from the site prior to final acceptance.

Upon completion of the project, the Contractor shall sweep the finished surface with a conventional power rotary broom, to remove any potential loose material from the surface. The material removed by sweeping shall be disposed of in a manner satisfactory to the Engineer.

626-4.6 CERTIFICATION. Samples of the emulsion that the Contractor proposes to use, together with a statement as to its source, shall be submitted, and approval shall be obtained before using such material. The Contractor shall submit to the Engineer a manufacturer's certified report for each consignment of the emulsion. The manufacturer's certified report shall not be interpreted as a basis for final acceptance. All such reports shall be subject to verification by testing samples of the emulsion as received for use on the project.

METHOD OF MEASUREMENT

626-5.1 The emulsified asphalt for slurry coat will be measured by the square yard.

626-5.2 Aggregate will be measured by the ton of dry aggregate.

626-5.3 Tack coat will be measured by the ton.

BASIS OF PAYMENT

626-6.1 Payment will be made at the contract unit price per square yard for the slurry coat and at the contract price per ton for aggregate and tack coat.

Payment will be made under:

Item P-626a	Emulsified Asphalt for Slurry Coat - per square yard

Item P-626b	Aggregate - per ton

Item P-626c	Emulsified Asphalt for Tack Coat - per ton

TESTING REQUIREMENTS

ASTM C 88	Soundness of Aggregates by Use of Sodium Sulfate or Magnesium Sulfate

ASTM C 117	Materials Finer than No. 200 Sieve in Mineral Aggregate by Washing

ASTM C 128	Specific Gravity and Absorption of Fine Aggregate

ASTM C 131	Resistance to Abrasion of Small Size Course Aggregate by Use of the Los Angeles Machine

ASTM C 136	Sieve or Screen Analysis of Fine and Coarse Aggregates

ASTM D 75	Sampling Aggregates

ASTM D 2419	Sand Equivalent Value of Soils and Fine Aggregate

ATM 313	Aggregate Degradation

ISSA	International Slurry Surfacing Association, Washington, DC

ISSA A 105	Recommended Performance Guidelines

ISSA TB-100	Wet Track Abrasion Loss

ISSA TB-106	Slurry Seal Consistency

ISSA TB 111	Outline Guide Design Procedure for Slurry Seal

ISSA TB-115	Determination of Slurry Seal Compatibility

MATERIAL REQUIREMENTS

ASTM D 242	Mineral Filler for Bituminous Paving Mixtures

ASTM D 977	Emulsified Asphalt

ASTM D 2397	Cationic Emulsified Asphalt

ITEM P-630	PAVEMENT GROOVING

# DESCRIPTION

630 1.1 This item shall consist of saw cutting of grooves on runways, taxiways, or other paved surfaces to the dimensions shown on the Plans or as directed by the Engineer.

EQUIPMENT AND MATERIALS

630-2.1 Pavement Grooving Machine. The pavement grooving machine shall be a single self-propelled unit with multiple cutting blades mounted on a single shaft. The machine shall have a minimum cutting width of 36 inches and shall have diamond cutting blades. The unit shall have sufficient control to cut grooves to the tolerance specified below.

630-2.2 Water. The grooving machine shall be furnished with a continuous source of water for cutting and clean-up. The Contractor shall be responsible for locating a water source capable of providing the quality and quantity of water necessary to ensure a continuous grooving operation.

CONSTRUCTION METHODS

630-3.1 Layout. The area to be grooved shall be laid out in the field by the Contractor. The Contractor shall use string or chalk line or other method approved by the Engineer.

630-3.2 Sawing Grooves. Grooves shall be cut at right angles to the centerline for grooving or runways or taxiways or in the direction specified for other surfaces. Grooves shall be cut continuously from beginning of the cut to the end without stopping. The alignment of groves with respect to centerline shall be monitored continuously and corrected at the end of each shift or a maximum of 300 feet.

Grooves shall extend a minimum of 6 feet beyond the edge of structural pavement (side stripe) on surfaces with paved shoulders. On pavements without paved shoulders, grooves shall be cut as close as practicable to the edge of the pavement.

Should one cutting blade break during operations, work may continue until the end of that shift at which time the blade must be replaced. Should more than one blade break, work shall be suspended until all defective blades are replaced.

630-3.3 Pavement Curing. No grooving will be allowed on a newly placed paved surface until sufficient time has elapsed to allow the pavement to cure. For Hot Mixed Asphalt (HMA) pavement, a minimum of 14 calendar days shall have elapsed before grooving. For Portland Cement Concrete (PCC) pavement, a minimum of 7 days shall have elapsed.

630-3.4 In-Pavement Fixtures. Grooves shall be sawed no less than 6 inches and no more than 18 inches from in-pavement fixtures such as light fixtures or surface sensors.

No grooving shall occur through longitudinal or diagonal saw kerfs where lighting or surface sensor cables are installed. Grooves may be continued through longitudinal construction joints in PCC pavement.

630-3.5 Clean-up. Clean-up shall be continuous throughout the grooving operation. Waste material collected during the grooving operation shall be disposed of by flushing with water, sweeping or by vacuuming. If waste material is flushed from the surface, the material shall not be allowed to enter any airport storm drain or sanitary sewer system.

630-3.6 TOLERANCES. Grooves shall be 1/4 inch deep and 1/4 inch wide with a tolerance of ±1/16 inch. Not more than 60% of the grooves shall be less than 1/4 inch. Grooves shall be spaced at 1-1/2 inches center to center with a tolerance of +0 inch and -1/8 inch.

Grooves shall be perpendicular to the established centerline ± 1 degree. The grooves shall not vary more than 3 inches in alignment for a 75-foot groove length.

METHOD OF MEASUREMENT

630-5.1 Pavement grooving will be measured either by neat line dimensions as shown in the Plans or as a single item of work. No deductions will be made for areas skipped to avoid joints or in-pavement fixtures.

BASIS OF PAYMENT

630-6.1 Payment will be made at the contract unit price or the lump sum price for pavement grooved and accepted by the Engineer.

Payment will be made under:

Item P-630a	Pavement Grooving - per square yard

Item P-630b	Pavement Grooving - per lump sum

ITEM P-640	SEGMENTED CIRCLE

DESCRIPTION

640-1.1 This item consists of furnishing and installing an airport segmented circle, in accordance with the dimensions, design, details, and location shown on the Plans. Construct barrel-type or panel-type, as shown in the bid schedule.

If shown on the Plans, the segmented circle includes landing direction indicator, landing strip indicators, or traffic pattern indicators.

# MATERIALS

640-2.1 Barrel-Type.

- Barrels. Cylindrical, steel, 55-gallon, undamaged, contaminant-free, and rust-free.

- Primer Paint. Rustoleum 960, or approved equal.

- Finish Paint. Aviation Gloss Orange, No. 12197, meeting Federal Standard 595.

640-2.2 Panel-Type.

- Panels. Sheet aluminum with a reflective covering and meeting the following requirements:

- Use alloy 6061-T6, 5052-H36, 5052-H38, or recycled aluminum meeting alloy 3105, as specified in ASTM B 209. The sheets shall be 14 gage.

- Make each panel a continuous sheet for the length and width shown on the Plans. Furnish panels that are cut to size and shape and free of buckles, warp, dents, cockles, burrs and any other defects resulting from fabrication. Complete all possible fabrication including shearing, cutting and punching of holes prior to the base metal preparation.

- Treat the aluminum base metal sheets with chromate conversion coating for aluminum conforming to the requirements of ASTM B 449, Class 2. After cleaning and coating operations, protect the panels at all times from contact or exposure to greases, oils, dust or other contaminants.

- Cover one side of each panel with orange reflective sheeting, meeting the requirements of AASHTO M 268, Type II or Type III.

- Stanchions. Perforated, galvanized, square steel tubing with the dimensions shown on the Plans and meeting the following requirements:

- Fabricate tube with cold-rolled carbon steel sheets, 12 gage, commercial quality, meeting ASTM A 653, coating designation G 90. Form tubes, roll to size, and weld in the corner.

- Perforate all members for their entire length with 7/16 inch diameter holes on 1 inch centers.

- Furnish members that are straight and with a smooth, uniform finish with no splices.

- Ensure that all perforations and cut off ends are free from burrs.

- Hardware and Fasteners. Hardware and fasteners shall meet the following requirements:

- Gusset and splice plates shall be 1/4 inch thick steel , ASTM A 36, galvanized.

- Fasteners shall be galvanized, Grade 2, bolts with washers of the sizes shown on the Plans.

# CONSTRUCTION METHODS

# 640-3.1 General. The site may be either on a prepared pad constructed for that purpose under separate item or on natural ground, whichever is shown on the Plans.

If the segmented circle is to be placed on original ground, clear the site of all brush and vegetation to the limits shown on the Plans and level the site.

Use material excavated for installation of barrels or stanchions as backfill. Spread excess material evenly over ground adjacent to the barrels, stanchions, or pad so as to leave the site in a neat condition.

640-3.2 Barrel-Type. Clean the outside of each barrel with an approved solvent and paint with 1 coat of primer paint and 2 coats of finish paint.

Cut hole maximum of 6 inches in bottom of barrel. Fill barrel one third with clean sand or gravel. Bury the bottom one third of barrel at the location and in the configuration shown on the Plans.

640-3.3 Panel-Type. Prepare and assemble panels, perforated steel tubes, and hardware as shown in the Plans. Bury stanchions to the depth, at the location, and in the configuration shown on the Plans.

640-4.1 METHOD OF MEASUREMENT. Segmented circle will not be measured for payment.

640-5.1 BASIS OF PAYMENT. Payment will be made at the contract lump sum price shown on the bid schedule.

Clearing of the site is paid for under Item P-151. If Item P-151 is not included in the bid schedule, clearing is subsidiary.

Payment will be made under:

Item P-640a	Segmented Circle (Barrel-Type) - per lump sum

Item P-640b	Segmented Circle (Panel-Type) - per lump sum

MATERIAL REQUIREMENTS

AASHTO M 268	Standard Specification for Retroreflective Sheeting

ASTM A 36	Structural Steel

ASTM A 653	Standard Specification for Steel Sheet, Zinc-Coated (Galvanized) or Zinc-Iron Alloy-Coated (Galvannealed) by the Hot-Dip Process

ASTM A 924	Standard Specification for General Requirements for Steel Sheet, Metallic-Coated by the Hot-Dip Process

ASTM B 209	Standard Specification for Aluminum and Aluminum-Alloy Sheet and Plate

ASTM B 449	Standard Specification for Chromates on Aluminum

Federal Standard 595	Colors Used in Government Procurement

### ITEM P-650	AIRCRAFT TIE-DOWN

#### DESCRIPTION

650-1.1 This item consists of furnishing and installing aircraft tie-down anchors in accordance with these specifications and the details on the Plans.

## MATERIALS

650-2.1 General. Anchor assemblies shall have a minimum tensile breaking strength of 6,000 pounds and minimum field pull-out capacity of 3,000 pounds. Provide manufacturer’s certification of minimum breaking strength. The Contractor shall field-test the installed anchors to the minimum pull-out force and certify that this requirement has been met for each anchor.

Each anchor assembly shall include a 1-1/2 inch inside diameter by 3/8 inch stainless steel tether ring.

650-2.2 Soil Anchor Tie-downs. Soil anchors shall be Duckbill model 88-DB1, Manta Ray model MR-88, or an approved equal. Known suppliers include Foresight Products, Commerce City, CO; Williams Form Engineering, Grand Rapids, MI; and Earth Anchor Installation & Sales, Santa Rosa, CA.

650-2.3 Rock Anchor Tie-downs. Rock anchors shall be 1/2 inch diameter Williams Solid Bar “Spin Lock” Rock Bolts, Williams Titan Injection Anchor 30/16, or an approved equal.

## CONSTRUCTION METHODS

650-3.1 General. Tie-down anchors shall be installed in shallow 8-inch diameter depressions such that tops of tether rings will be 3/8 inch below finish grade when service loaded. If the anchor is set in pavement, the depression shall be sealed with like paving material.

650-3.2 Soil Anchor Tie-downs. Soil anchors shall be driven to sufficient depth to develop the minimum pull-out strength in accordance with the manufacturer’s installation instructions. Predrilling may be required depending on soil class. Anchor placement shall be achieved by methods recommended in the manufacturer’s installation instructions. Backfill material, if required, shall be compactable aggregate.

The galvanized cable shall be swaged and no intermediate splicing shall be allowed. Field cutting of the cables, which results in damage to the galvanizing, shall not be permitted.

650-3.3 Rock Anchor Tie-downs. Rock anchors shall be anchored in sound bedrock at sufficient penetration to develop the minimum pull-out strength in accordance with the manufacturer’s instructions.

## METHOD OF MEASUREMENT

650-4.1 By each set, consisting of 3 anchors, completed and accepted in final position.

## BASIS OF PAYMENT

650-5.1 At the contract price, per set, for each of the pay items shown in the bid schedule.

Payment will be made under:

Item P-650a	Soil Anchor Tie-down - per set

Item P-650b	Rock Anchor Tie-down - per set

PART VIII - FENCING

ITEM F-160	WIRE FENCE WITH WOOD POSTS

(Classes A and B Fences)

DESCRIPTION

160-1.1 This item covers the requirements for furnishing materials and constructing wire fences and gates with wood posts in accordance with the details included herein and as shown on the Plans. The class of fence to be erected shall be either Class A, woven wire fencing surmounted by 2 strands of barbed wire, or Class B, 4 strands of barbed wire, as specified.

MATERIALS

160-2 WIRE.

- Woven Wire (Zinc-coated). The woven wire fabric shall meet ASTM A 116, Design Number 726-6-12 ½, Grade 60, Class 3 coating.

- Barbed Wire (Zinc-coated). Barbed wire shall meet ASTM A 121, 12 ½-gage, 4 points, 5-inch spacing, 14-gage round barbs, Class 3 coating. Chain Link Fence Grade.

- Barbed Wire (Aluminum-coated). Barbed wire shall meet ASTM A 585, Type I (Standard).

- Bracing Wire (Zinc-coated). Wire used for cable for bracing shall be No. 9 smooth galvanized soft wire.

160-2.2 GATES AND HARDWARE. Gate frames shall be constructed of hot-dip galvanized steel tubing conforming to AASHTO M 181 and shall be the size shown on the Plans. Heavily galvanized hinges and latches for wood posts shall be furnished with each gate. Either a bolt or lag screw hinge shall be used, and either a wing or butterfly latch shall be furnished.

160-2.3 POSTS.

- Species. All posts shall be one of the following species of wood, unless otherwise specified.

Group I	Group II

Cedar	Douglas-Fir

Chestnut	Gum, Red

Cypress, Southern	Larch, Western

Locust, Black	Pine, Southern Yellow

Osage-orange	Pine, Lodgepole

Redwood	Tamarack

Yew, Pacific	Ash

Honey locust	Maple, Sugar

Oak, White	Oak, Red

Mulberry	Spruce

Live Oak

Posts of Group I may be used untreated, provided at least 75% of the wood is heartwood. Posts of less than 75% heartwood of Group I shall be given a preservative treatment for the part of the post that will have contact with the ground line in accordance with the method specified under subparagraph e(1) below. Posts of Group II shall be given a preservative treatment in accordance with the method specified under subparagraph e(2) below.

- Quality. Posts shall be peeled, sound, straight-grained, free from decay, cracks, and splits; shakes shall not be in excess of 1/4 inch wide and 3 feet long. Checks (lengthwise separations of the wood in a generally radial direction) are permitted, provided they are not injurious.

- Dimensions. All posts shall be of the length shown on the Plans. Posts shall have the minimum top diameters shown on the Plans or as specified. Sawed and split posts are acceptable in lieu of round posts provided their dimensions are such that round posts of required diameter could be turned therefrom.

- Manufacture. Outer bark shall be completely removed from all posts including depressions. Inner bark shall be removed from all post surfaces to be treated, except inner bark may remain in depressions. The amount of wood shaved off in the removal of inner bark shall be held to a minimum.

- Treatment.

- Butt treatment. All timber shall be thoroughly seasoned and dry (22% maximum moisture content) before applying preservative treatment. The treatment shall be by a process at least equal to a hot and cold bath process. The hot bath temperature shall be from 200 to 230 °F for a duration of 45 minutes, and the cold bath temperature not over 120 °F for a duration of 45 minutes. The preservative shall be either coal-gas tar or coke-oven tar creosote conforming to American Wood Preservers Association (AWPA) Specification No. 4 for Grade 1 creosote; or a 5% minimum, by weight, pentachlorophenol petroleum solution made by either mixing a liquid concentrate of pentachlorophenol in fuel oil or kerosene, or by dissolving pentachlorophenol crystals of technical purity in suitable fuel oil solvents, as specified by AWPA.

- Full length treatment. Posts shall be conditioned by air seasoning, steaming, or heating in oil in a manner that prevents injurious checking, splitting, or warping before treating. The treatment, care, and preservative shall be in accordance with Fed. Spec. TT-W-571.

160-2.4 BRACES. Cleats, gate stops, and braces shall be of the size shown on the Plans. They shall be of the same species and quality specified for the posts or approved by the Engineer, and they shall be free from knots larger than one-third the width of the piece. Gate stops shall be made of posts of suitable length. Braces may be made of posts of suitable length or of sawed lumber. All cleats, gate stops, and any braces in contact with the ground and for a distance of at least 6 inches above the ground shall be treated by the hot and cold bath process, specified herein for posts. The wire used in cable for bracing shall conform to 160-2.1e.

160-2.5 STAPLES. The staples shall be No. 9 galvanized steel wire, 1 inch long for hardwood posts and 1-1/2 inches long for use in softwood posts.

160-2.6 GATE LOCKS. Gate locks shall be provided for each gate and shall be brass, restricted keyway padlocks with a shackle that is 3/8 inch in diameter having a closed clearance of 2-1/4 inches. The locks shall have control key removable cores and each lock shall have a separate replacement core. All cores shall be keyed differently. The Contractor shall provide keys per lock and 2 core removal keys.

CONSTRUCTION METHODS

160-3.1 GENERAL. The fence shall be constructed in accordance with the details on the Plans and as specified herein. The Contractor shall be responsible for establishing the fence alignment as shown on the Plans. After the fence line has been staked and prior to fence installation, the Contractor shall review the alignment with the Engineer and make required adjustments to avoid conflicts.

When directed, the Contractor shall span the opening below the fence with barbed wire fastened to posts of extra length at locations of small natural or drainage ditches where it is not practical to conform the fence to the general contour of the ground surface. The new fence shall be permanently tied to the terminals of existing fences whenever required by the Engineer. The finished fence shall be plumb, taut, true to line and ground contour, and complete in every detail. When directed, the Contractor shall stake down the woven wire fence at several points between posts.

When directed, in order to keep stock on adjoining property enclosed at all times, the Contractor shall arrange the work so that construction of the new fence will immediately follow the removal of existing fences. The length of unfenced section at any time shall not exceed 300 feet or such length that the stock can be kept in the proper field. The work shall progress in this manner, and at the close of the working day, the newly constructed fence shall be tied to the unremoved existing fence. Any openings in the fence shall be guarded when stock is using the adjoining property.

160-3.2 CLEARING FENCE LINE. The site of the fence shall be sufficiently clear of obstructions, and surface irregularities shall be graded so that the fence will conform to the general contour of the ground. The fence line shall be cleared to a minimum width of 10 feet on each side of the centerline of the fence. This clearing shall consist of the removal of all stumps, brush, rocks, trees, or other obstructions that will interfere with proper construction of the fence. Stumps within the cleared area of the fence line shall be grubbed or excavated. The bottom of the fence shall be placed a uniform distance above ground as specified in the Plans. When shown on the Plans, existing fences which coincide with, or are in a position to interfere with, the new fence location shall be removed by the Contractor as part of the construction work, unless such removal is listed as a separate item in the bid schedule. All holes remaining after post and stump removal shall be refilled with suitable soil, gravel, or other material acceptable to the Engineer and shall be compacted properly with tampers.

160-3.3 SETTING POSTS. Posts shall be set with large ends down, plumb, and in good line on the side on which the wire is to be fastened. Posts shall be set full depth and shall not be cut off to eliminate rock or other excavation. Where rock is encountered, it shall be removed, even if blasting is necessary, to provide full-depth and full-size holes. The bottoms of all posts shall be cut off square. The diameter of the holes shall be at least 6 inches larger than the diameter of the posts. When cleats are used on posts, the holes shall be dug large enough to accommodate them. After posts are placed and lined, the holes shall be backfilled with suitable material that shall be properly compacted by the use of tampers. The posts adjacent to end, corner, anchor, and gate posts shall be set and braced with braces and wire, as shown on the Plans.

160-3.4 ANCHORING. Corner, end, gate, and adjacent intermediate posts shall be anchored, by gaining and spiking cleats to the sides of the posts, as indicated on the Plans. No cleats will be required on other intermediate posts or on anchor posts.

160-3.5 BRACING. End, corner, anchor, and gate posts shall be braced by using a post of sufficient length or a piece of sawed lumber of the proper size, together with a wire cable. The wooden brace shall be gained and securely spiked into the end, corner, anchor, or gate posts and into the next intermediate posts about 6 inches from the top of the respective posts. A cable made of a double strand of galvanized soft wire shall be looped around the end, corner, anchor, or gate post near the ground and around the next intermediate post about 12 inches from the top. After the cable has been stapled in this position, it shall be twisted until tight. The staples used to hold the cable shall be not less than 1-1/2 inches long. The tool used for twisting the cable shall be left in placed to permit later adjustment of bracing if found necessary. Anchor posts shall be set at approximately 500-foot intervals and braced to the adjacent posts. Posts shall be braced before the wire fencing is placed.

160-3.6 INSTALLING WIRE. The wires shall be placed on the side of the posts away from the airport or as directed. The wire fence shall be placed on the posts at the height indicated on the Plans. Longitudinal wires shall be installed parallel and drawn uniformly taut. The vertical stay wires of the woven wire fencing shall be straight and vertical. At end and gate posts the woven wire and barbed wire shall be wrapped once around the post; each longitudinal wire shall be stapled at least three times and the ends of these wires shall be tied with a snug, tight twist. Each longitudinal wire shall be stapled to each intermediate post with one steel wire staple; at the corner and anchor posts, two or more stapled shall be used. The top strand of barbed wire of all fences shall be stapled with two staples in each post. All staples shall be set diagonally with the grain of the wood and driven up tight. After the fence has been erected, the tops of the wood posts shall be sawed off with a 1-to-3 pitch. The bottom wire of the wire fencing shall clear the ground by not more than 4 inches or less than 1 inch at any place.

160-3.7 SPLICING WIRE. Wire splices in longitudinal wires will be permitted if made with an approved galvanized bolt-clamp splice or a wire splice made as follows: The end of the wires shall be carried 3 inches past the splice tool and wrapped around the other wire away from the tool for at least 6 turns in opposite directions. After the tool is removed, the space occupied by it shall be closed by pulling the ends together. The unused ends of the wires shall be cut off neatly. Woven wire shall be spliced only at posts.

160-3.8 INSTALLING GATES. The gates shall be hung on gate fittings, as shown on the Plans. Fittings on the gate posts shall be clamped, screwed, or bolted to prevent slipping. Gates shall be so erected as to swing in the direction indicated and shall be provided with gate stops, as specified or as shown on the Plans. Gates shall be erected locations shown on the Plans.

160-3.9 EXISTING FENCE CONNECTIONS. Wherever the new fence joins an existing fence, either at a corner or at the intersection of straight fence lines, a corner or anchor post shall be set at the junction and braced and anchored the same as herein described for corner posts.

If the connection is made at other than the corner of the new fence, the last span of the old fence shall contain a brace span.

METHOD OF MEASUREMENT

160-4.1. Fences will be measured in place from outside to outside of end posts or corner posts and will be the length of fence actually constructed, except for the space occupied by the gates.

160-4.2. Gates will be measured in units for each gate installed and accepted.

BASIS OF PAYMENT

160-5.1 Payment will be made at the contract unit price per linear foot for fence and per each for gates.

Work involved in clearing and disposal of material along the fence line and any required rock excavation are subsidiary.

Payment will be made under:

Item F-160a	Fence, Class A - per linear foot

Item F-160b	Fence, Class B - per linear foot

Item F-160c	Gates (Width) - per each

Item F-160d	Walkway Gates (Width) - per each

MATERIAL REQUIREMENTS

AASHTO M 181	Chain Link Fence

ASTM A 116	Zinc-Coated (Galvanized) Steel Woven Wire Fence Fabric

ASTM A 121	Zinc-Coated (Galvanized) Steel Barbed Wire

ASTM A 585	Aluminum-Coated Steel Barbed Wire

Fed. Spec. TT-W-571	Wood Preservation: Testing Practices

ITEM F-161	WIRE FENCE WITH STEEL POSTS

(Classes C and D Fences)

DESCRIPTION

161-1.1 This item covers the requirements for furnishing materials and constructing wire fences and gates with steel posts in accordance with the details included herein and as shown on the Plans. The class of fence to be erected shall be either Class C, woven wire fencing surmounted by 2 strands of barbed wire, or Class D, 4 strands of barbed wire, as specified.

MATERIALS

161-2.1 WIRE.

- Woven Wire (Zinc-coated). The woven wire fabric shall meet ASTM A 116, Design Number 726-6-12 ½, Grade 60, Class 3 coating.

- Barbed Wire (Zinc-coated). Barbed wire shall meet ASTM A 121, 12 ½-gage, 4 points, 5-inch spacing, 14-gage round barbs, Class 3 coating, Chain Link Fence Grade.

- .Barbed Wire (Aluminum-coated). Barbed wire shall meet ASTM A 585, Type I (Standard).

- Bracing Wire (Zinc-coated). Wire used for cable for bracing shall be No. 9 smooth galvanized soft wire.

161-2.2 FENCE POSTS, GATES, RAILS, BRACES, AND ACCESSORIES. These items shall be hot-dip galvanized steel, conforming to AASHTO M 181.

161-2.3 CONCRETE. Concrete shall be of a commercial grade with a minimum 28-day compressive strength of 2,500 psi or an approved, pre-mixed, sacked concrete.

161-2.4 GATE LOCKS. Gate locks shall be provided for each gate and shall be brass, restricted-keyway padlocks with a shackle that is 3/8 inch in diameter having a closed clearance of 2-1/4 inches. The locks shall have control key removable cores and each lock shall have a separate replacement core. All cores shall be keyed differently. The Contractor shall provide 4 keys per lock and 2 core removal keys.

CONSTRUCTION METHODS

161-3.1 GENERAL. The fence shall be constructed in accordance with the details on the Plans and as specified herein. The Contractor shall be responsible for establishing the fence alignment as shown on the Plans. After the fence line has been staked, and prior to fence installation, the Contractor shall review the alignment with the Engineer and make required adjustments to avoid conflicts.

When directed, the Contractor shall span the opening below the fence with barbed wire fastened to stakes of the required length at locations of small natural or drainage ditches where it is not practical to conform the fence to the general contour of the ground surface. The new fence shall be permanently tied to the terminals of existing fences whenever required by the Engineer. The finished fence shall be plumb, taut, true to line and ground contour, and complete in every detail. When directed, the Contractor shall stake down the woven wire fence at several points between posts.

When directed, in order to keep stock on adjoining property enclosed at all times, the Contractor shall arrange the work so that construction of the new fence will immediately follow the removal of existing fences. The length of unfenced section at any time shall not exceed 300 feet or such length that the stock can be kept in the proper field. The work shall progress in this manner and at the close of the working day the newly constructed fence shall be tied to the existing fence. Any openings in the fence shall be guarded when stock is using the adjoining property.

161-3.2 CLEARING FENCE LINE. The site of the fence shall be sufficiently cleared of obstructions, and surface irregularities shall be graded so that the fence will conform to the general contour of the ground. The fence line shall be cleared to a minimum width of 10 feet on each side of the centerline of the fence. This clearing shall consist of the removal of all stumps, brush, rocks, trees, or other obstructions which will interfere with proper construction of the fence. Stumps within the cleared area of the fence shall be placed a uniform distance above ground, as specified in the Plans. When shown on the Plans or as directed by the Engineer, the existing fences which coincide with, or are in a position to interfere with, the new fence location shall be removed by the Contractor as a part of the construction work unless such removal is listed as a separate item in the bid schedule. All holes remaining after post and stump removal shall be refilled with suitable soil, gravel, or other material acceptable to the Engineer and shall be compacted properly with tampers.

161-3.3 INSTALLING POSTS. All posts shall be spaced as shown on the Plans. Corner, brace, anchor, end, and gate posts shall be set in concrete bases as shown on the Plans. The top of the base shall be slightly above the ground surface, trowel finished, and sloped to drain. Holes of full depth and size for the concrete bases for posts shall be provided even if blasting of rock or other obstructions is necessary. All line posts may be either driven or set in dug holes to a penetration of 3 feet. All post setting shall be done carefully and to true alignment. Dirt removed for placing posts, anchor bars, flanges, etc., shall be replaced, tamped, and leveled. When posts are driven, care shall be exercised to prevent marring or buckling of the posts. Damaged posts shall be replaced at the Contractor’s expense.

161-3.4 BRACING. All corner, anchor, end, and gate posts shall be braced as shown on the Plans. Anchor posts shall be set at approximately 500-foot intervals and braced to the adjacent posts.

161-3.5 INSTALLING WIRE. All barbed wire and woven wire shall be placed on the side of the post away from the airport, or as directed, at the height indicated on the Plans. The woven wire shall be carefully stretched and hung without sag and with true alignment. Care shall be taken not to stretch the wire so tightly that it will break in cold weather or pull up corner and brace posts. All horizontal wires shall be fastened securely to each post by fasteners or clips designed for use with the posts furnished. The woven wire shall be wrapped around end, corner, and gate posts, and the ends of all horizontal wires shall be tied with snug, tight twists. The wire shall be secured to prevent slipping up and down the post. Barbed wire strands shall be stretched and each strand secured to each post to prevent slipping out of line or becoming loose. At end, corner, and gate posts the barbed wire shall be securely wrapped and anchored once abut the post from outside and secured against slipping by tying the ends with snug, tight twists. However, on spans of less than 100 feet, both ends of the span need not be wrapped around the posts. The bottom wire of the woven wire fencing shall clear the ground by not more than 4 inches or less than 1 inch at any place.

161-3.6 SLPICING WIRE. Splices in barbed and woven wire will be permitted if made with an approved galvanized bolt-clamp splice or a wire splice made as follows: The ends of each wire shall be carried 3 inches past the splice tool and wrapped around the other wire for at least 6 turns in opposite directions. After the tool is removed, the space occupied by it shall be closed by pulling the ends together. The unused ends of the wire shall be cut off neatly.

161-3.7 INSTALLING GATES. The gates shall be hung on gate fittings as shown on the Plans. They shall be attached in such a manner that the gate cannot be lifted off the hinges. Gates shall be erected to swing in the direction indicated and shall be provided with gate stops, as specified or as shown on the Plans. Gates shall be erected at locations shown on the Plans.

161-3.8 EXISTING FENCE CONNECTIONS. Wherever the new fence joins an existing fence, either at a corner or at the intersection of straight fence lines, a corner or anchor post shall be set at the junction and braced and anchored the same as herein described for corner posts.

If the connection is made at other than the corner of the new fence, the last span of the old fence shall contain a brace span.

METHOD OF MEASUREMENT

161-4.1. Fences will be measured in place from outside to outside of end posts or corner posts and will be the length of fence actually constructed, except for the space occupied by the gates.

161-4.2. Gates will be measured in units for each gate installed and accepted.

BASIS OF PAYMENT

161-5.1. Payment will be made at the contract unit price per linear foot for fence and per each for gates.

Work involved in clearing and disposal of material along the fence line and any required rock excavation are subsidiary.

Payment will be made under:

Item F-161a	Fence, Class C - per linear foot

Item F-161b	Fence, Class D - per linear foot

Item F-161c	Gates (Width) - per each

Item F-161d	Walkway Gates - per each

MATERIAL REQUIREMENTS

AASHTO M 181	Chain Link Fence

ASTM A 116	Zinc-Coated (Galvanized) Steel Woven Wire Fence Fabric

ASTM A 121	Zinc-Coated (Galvanized) Steel Barbed Wire

ASTM A 585	Aluminum-Coated Steel Barbed Wire

ITEM F-162	CHAIN-LINK FENCE

DESCRIPTION

162-1.1 This item shall consist of furnishing and erecting a chain-link fence in accordance with these specifications and the details shown on the Plans.

MATERIALS

162-2.1 FABRIC. Chain-link fabric shall be 9-gage, Type I (zinc-coated steel), Class D coating, 2-inch mesh, meeting the requirements of AASHTO M 181.

162-2.2 BARBED WIRE. Barbed wire shall be 3-strand 12-1/2-gage zinc-coated wire with 14-gage round 4-point barbs, 5-inch spacing, and shall conform to the requirements of ASTM A 121, Class 3, Chain Link Fence Grade.

162-2.3 POSTS, RAILS AND BRACES. Line posts, rails, and braces shall be galvanized steel pipe conforming to the requirements of AASHTO M 181, Type I, Grade 1.

The dimensions of the posts, rails, and braces shall be as shown on the Plans.

162-2.4 GATES. Gate frames shall consist of galvanized steel pipe and shall conform to AASHTO M 181, Type I, Grade 1. The fabric shall be of the same type material as used in the fence.

162-2.5 WIRE TIES AND TENSION WIRES. Wire ties for use in conjunction with a given type of fabric shall be of the same material and coating weight identified with the fabric type. Tension wire shall conform to AASHTO M 181, Type I, Class 3 coating.

162-6 MISCELLANEOUS FITTINGS AND HARDWARE. Miscellaneous steel fittings and hardware shall meet AASHTO M 181, Type I, Grade 1 Barbed wire support arms shall withstand a load of 250 pounds applied vertically to the outermost end of the arm.

162-2.7 CONCRETE. Concrete shall be of a commercial grade with a minimum 28-day compressive strength of 2,500 psi or an approved, pre-mixed, sacked concrete.

162-2.8 MARKING. Each roll of fabric shall carry a tag showing the kind of base metal, kind of coating, the gage of the wire, the length of fencing in the roll, and the name of the manufacturer. Posts, wire, and other fittings shall be identified as to manufacturer, kind of base metal, and kind of coating.

162-2.9 GATE LOCKS. Gate locks shall be provided for each gate and shall be brass, restricted keyway padlocks with a shackle that is 3/8 inch in diameter having a closed clearance of 2-1/4 inches. The locks shall have control key removable cores and each lock shall have a separate replacement core. All cores shall be keyed differently. The Contractor shall provide 4 keys per lock, and 2 core-removal keys.

162-2.10 KEYLESS LOCKS. When specified, a changeable combination lock shall be furnished with pedestrian gates. The keyless lock shall have a 4- or 5-digit mechanism and shall be an Ilco Unican Model 1011 or approved equal. A sign, 12 inches by 12 inches, shall be securely mounted on the inside of the gate. The sign shall be shielded from view from outside of the gate by means of a hinged 12-inch by 12-inch cover or other means approved by the Engineer. The cover shall have the legend “LIFT AND RECORD COMBINATION FOR REENTRY”. The sign shall be aluminum sheet with white reflective coating. Letters shall be black and a minimum of 3/4 inch tall.

CONSTRUCTION METHODS

162-3.1 GENERAL. The fence shall be constructed in accordance with the details on the Plans and as specified herein using new materials. The Contractor shall be responsible for establishing the fence alignment as shown on the Plans. After the fence line has been staked and prior to fence installation, the Contractor shall review the alignment with the Engineer and make required adjustments to avoid conflicts.

162-3.2 CLEARING FENCE LINE. All trees, brush, stumps, logs, and other debris which would interfere with the proper construction of the fence in the required location shall be removed a minimum width of 10 feet on each side of the fence centerline before starting fencing operations.

162-3.3 INSTALLING POSTS. All end posts, corner posts and pull posts shall be set in concrete at the required dimensions and depths and at the spacing shown on the Plans. Line posts may be either set in concrete as shown on the Plans or driven a minimum of 5 feet embedment. Pull posts shall have a maximum spacing of 250 feet.

Posts shall be spaced as shown on the Plans but in no case shall spacing be more than 10 feet. The post holes shall be in proper alignment so that there is a minimum of 3 inches of concrete on all sides of the posts. The concrete shall be thoroughly compacted around the posts by tamping or vibrating and shall have a smooth finish slightly higher than the ground and sloped to drain away from the posts. All posts shall be set plumb and to the required grade and alignment. No materials shall be installed on the posts, nor shall the posts be disturbed in any manner within 7 days after the individual post footing is completed.

Should rock be encountered at a depth less than the planned embedment depth, a hole 2 inches larger than the greatest dimension of the posts shall be drilled to a depth of 12 inches. After the posts are set, the remainder of the drilled hole shall be filled with grout, composed of one part Portland cement and two parts mortar sand. Any remaining space above the rock shall be filled with concrete in the manner described above.

In lieu of drilling, the rock may be excavated to the required embedment depth.

162-3.4 INSTALLING TOP RAILS. The top rail shall be continuous and shall pass through the post tops. The coupling used to join the top rail lengths shall allow for expansion.

162-3.5 INSTALLING BRACES. Horizontal brace rails, with diagonal truss rods and turnbuckles, shall be installed at all terminal posts.

162-3.6 INSTALLING FABRIC. The wire fabric shall be firmly attached to the posts and braced in the manner shown on the Plans. All wire shall be stretched taut and shall be installed to the required elevations. The fence shall generally follow the contour of the ground, with the bottom of the fence fabric no less than 1 inch or more than 4 inches from the ground surface. Grading shall be performed where necessary to provide a neat appearance.

At locations of small natural swales or drainage ditches and where it is not practical to have the fence conform to the general contour of the ground surface, longer posts may be used and multiple strands of barbed wire stretched thereon to span the opening below the fence. The vertical clearance between strands of barbed wire shall be 6 inches or less.

162-3.7 ELECTRICAL GROUNDS. Electrical grounds shall be installed along the fence between gate openings and at intervals not exceeding 500 feet. Electrical grounds shall also be installed where a power line passes over the fence. The ground shall be accomplished with a copper clad rod 8 feet long and a minimum of 5/8 inch diameter driven vertically until the top is 6 inches below the ground surface. A No. 6 solid copper conductor shall be clamped to the rod and to the fence in such a manner that each element of the fence is grounded.

METHOD OF MEASUREMENT

162-4.1. Chain-link fence will be measured along the top of the fence from center to center of end posts, excluding the length occupied by gate openings.

162-4.2. Gates will be measured as complete units.

BASIS OF PAYMENT

162-5.1 Payment will be made at the contract unit price per linear foot for fence and per each for gates.

Work and materials involved in clearing and disposal of material along the fence line, rock excavation, and ground rod installation are subsidiary.

Payment will be made under:

Item F-162a	(Height) Chain-Link Fence - per linear foot

Item F-162b	(Width) Single Swing Gate - per each

Item F-162c	(Width) Double Swing Gate - per each

Item F-162d	(Width) Single Cantilever Gate - per each

Item F-162e	(Width) Double Cantilever Gate - per each

Item F-162f	(Width) Pedestrian Gate (w/Keyless Lock) - per each

MATERIAL REQUIREMENTS

AASHTO M 181	Chain-Link Fence

ASTM A 121	Zinc-Coated (Galvanized) Steel Barbed Wire

PART IX – DRAINAGE

ITEM D-701	STORM DRAINS AND CULVERTS

DESCRIPTION

701-1.1 This item shall consist of the construction of pipe culverts and storm drains in accordance with these Specifications and in reasonably close conformity with the lines and grades shown on the Plans.

MATERIALS

701-2.1 Materials shall meet the requirements shown on the Plans and specified below.

701-2.2 PIPE. The pipe shall be of the type called for on the Plans and shall be in accordance with the following appropriate requirements.

Metallic Coated Corrugated Steel Pipe (Type I, IR or II)		ASTM A 760

Galvanized Steel Corrugated Structural Plates and Fasteners		ASTM A 761

for Pipe, Pipe-Arches, and Arches

Polymer Precoated Corrugated Steel Pipe for Sewers and Drains	ASTM A 762

Post-Coated and Lined (Bituminous or Concrete) 			ASTM A 849

Corrugated Steel Sewer and Drainage Pipe

Steel Sheet, Zinc and Aramid Fiber Composite Coated for

Corrugated Steel Sewer, Culvert, and Underdrain Pipe		ASTM A 885

Corrugated Aluminum Alloy Culvert Pipe				ASTM B 745

Non-Reinforced Concrete Pipe					ASTM C 14

Reinforced Concrete Pipe						ASTM C 76

Reinforced Concrete D-Load Pipe					ASTM C 655

Reinforced Concrete Arch Pipe					ASTM C 506

Reinforced Concrete Elliptical Pipe					ASTM C 507

Precast Reinforced Concrete Box Sections				ASTM C 789 and C 850

Poly (Vinyl Chloride) Ribbed Drain Pipe & Fittings Based		ASTM F 794

on Controlled Inside Diameter

Poly (Vinyl Chloride) (PVC) Corrugated Sewer Pipe			ASTM F 949

With a Smooth Interior and Fittings

Bituminous-Coated Corrugated Metal Pipe and Pipe Arches		AASHTO M 190

Bituminous-Coated Corrugated Aluminum Alloy Culvert Pipe		AASHTO M 190 and M 196

Bituminous-Coated Structural Plate Pipe, Pipe Arch, and Arches	AASHTO M 167 and M 243

Aluminum Alloy Structural Plate for Pipe, Pipe Arch, and Arches	AASHTO M 219

Polyvinyl Chloride (PVC) Pipe					ASTM D 3034

Corrugated Polyethylene Drainage Tubing				AASHTO M 252

Corrugated Polyethylene Pipe, 300 mm to 1200 mm Diameter		AASHTO M 294

Poly (Vinyl Chloride) (PVC) Profile Wall Drain Pipe and Fittings		AASHTO M 304

Based on Controlled Inside Diameter

701-2.3 CONCRETE. Concrete for pipe cradles shall have a minimum compressive strength of 2,000 psi at 28 days and conform to the requirements of ASTM C 94.

701-2.4 RUBBER GASKETS. Rubber gaskets for rigid pipe shall conform to the requirements of ASTM C 443. Rubber gaskets for PVC pipe and polyethylene pipe shall conform to the requirements of ASTM F 477. Rubber gaskets for zinc-coated steel pipe and precoated galvanized pipe shall conform to the requirements of ASTM D 1056, for the ``RE'' closed cell grades.

701-2.5 JOINT MORTAR. Pipe joint mortar shall consist of one part portland cement and two parts sand. The portland cement shall conform to the requirements of ASTM C 150, Type I. The sand shall conform to the requirements of ASTM C 144.

701-2.6 JOINT FILLERS. Poured filler for joints shall conform to the requirements of ASTM D 1190.

701-2.7 PLASTIC GASKETS. Plastic gaskets shall conform to the requirements of AASHTO M 198 (Type B).

CONSTRUCTION METHODS

701-3.1 EXCAVATION. The width of the pipe trench shall be sufficient to permit satisfactory jointing of the pipe and thorough tamping of the bedding material under and around the pipe, but it shall not be less than the external diameter of the pipe plus 6 inches on each side. The trench walls shall be approximately vertical.

Where rock, hardpan, or other unyielding material is encountered, the Contractor shall remove it from below the foundation grade for a depth of at least 12 inches or 1/2 inch for each foot of fill over the top of the pipe (whichever is greater) but for no more than 75% of the nominal diameter of the pipe. The width of the excavation shall be at least 1 foot greater than the horizontal outside diameter of the pipe. The excavation below grade shall be backfilled with selected fine compressible material, such as silty clay or loam, and lightly compacted in layers not over 6 inches in uncompacted depth to form a uniform but yielding foundation.

Where a firm foundation is not encountered at the grade established, due to soft, spongy, or other unstable soil, the unstable soil shall be removed and replaced with approved granular material for the full trench width. The Engineer shall determine the depth of removal necessary. The granular material shall be compacted to provide adequate support for the pipe.

The excavation for pipes that are placed in embankment fill shall not be made until the embankment has been completed to a height above the top of the pipe as shown on the Plans.

701-3.2 BEDDING. The pipe bedding shall conform to the class specified on the Plans. When no bedding class is specified or detailed on the Plans, the requirements for Class C bedding shall apply.

- Rigid Pipe. Class A bedding shall consist of a continuous concrete cradle conforming to the plan details.

Class B bedding shall consist of a bed of granular material having a thickness of at least 6 inches below the bottom of the pipe and extending up around the pipe for a depth of not less than 30% of the pipe's vertical outside diameter. The layer of bedding material shall be shaped to fit the pipe for at least 10% of the pipe's vertical diameter and shall have recesses shaped to receive the bell of bell and spigot pipe. The bedding material shall be sand or selected sandy soil, all of which passes a 3/8 inch sieve and not more than 10% of which passes a No. 200 sieve.

Class C bedding shall consist of bedding the pipe in its natural foundation to a depth of not less than 10% of the pipe's vertical outside diameter. The bed shall be shaped to fit the pipe and shall have recesses shaped to receive the bell of bell and spigot pipe.

- Flexible Pipe. For flexible pipe, the bed shall be roughly shaped to fit the pipe, and a bedding blanket of sand or fine granular material shall be provided as follows:

| Pipe Corrugation Depth, in. | Minimum Bedding Depth, in. |
| --- | --- |
| 1/2 | 1 |
| 1 | 2 |
| 2 | 3 |
| 2-1/2 | 3-1/2 |

- PVC and Polyethylene Pipe. For PVC and polyethylene pipe, the bedding material shall consist of coarse sands and gravels with a maximum particle size of 3/4 inch. For pipes installed under paved areas, no more than 12% of the material shall pass the No. 200 sieve. For all other areas, no more than 50% of the material shall pass the No. 200 sieve. The bedding shall have a thickness of at least 6 inches below the bottom of the pipe and extend up around the pipe for a depth of not less than 50% of the pipe's vertical outside diameter.

701-3.3 LAYING PIPE. The pipe laying shall begin at the lowest point of the trench and proceed upgrade. The lower segment of the pipe shall be in contact with the bedding throughout its full length. Bell or groove ends of rigid pipes and outside circumferential laps of flexible pipes shall be placed facing upgrade.

Paved or partially lined pipe shall be placed so that the longitudinal center line of the paved segment coincides with the flow line.

Elliptical and elliptically reinforced pipes shall be placed with the manufacturer's top of pipe mark within five degrees of a vertical plane through the longitudinal axis of the pipe.

701-3.4 JOINING PIPE. Joints shall be made with (1) portland cement mortar, (2) portland cement grout, (3) rubber gaskets, (4) plastic gaskets, or (5) coupling bands.

Mortar joints shall be made with an excess of mortar to form a continuous bead around the outside of the pipe and shall be finished smooth on the inside. Molds or runners shall be used for grouted joints in order to retain the poured grout. Rubber ring gaskets shall be installed to form a flexible watertight seal.

- Concrete Pipe. Concrete pipe may be either bell and spigot or tongue and groove. The method of joining pipe sections shall be such that the ends are fully entered and the inner surfaces are reasonably flush and even. Joints shall be thoroughly wetted before mortar or grout is applied.

- Metal Pipe. Metal pipe shall be firmly joined by form fitting bands conforming to the requirements of ASTM A 760 for steel pipe and AASHTO M 196 for aluminum pipe.

- PVC and Polyethylene Pipe. Joints for PVC and polyethlyene pipe shall conform to the requirements of ASTM D 3212 when water tight joints are required. Joints for PVC and polyethlyene pipe shall conform to the requirements of AASHTO M 304 when soil tight joints are required. Fittings for polyethylene pipe shall conform to the requirements of AASHTO M 252 or M 294.

701-3.5 BACKFILLING. Pipes shall be inspected before any backfill is placed; any pipes found to be out of alignment, unduly settled, or damaged shall be removed and relaid or replaced at the Contractor's expense.

Material for backfill shall be fine, readily compatible soil, or granular material selected from the excavation or a source of the Contractor's choosing. It shall not contain frozen lumps, stones that would be retained on a 2-inch sieve, chunks of highly plastic clay, or other objectionable material. No less than 95% of a granular backfill material shall pass through a 1/2-inch sieve, and no less than 95% of it shall be retained on a No. 4 sieve.

When the top of the pipe is even with or below the top of the trench, the backfill shall be compacted in layers not exceeding 6 inches on both sides of the pipe and shall be brought up 1 foot above the top of the pipe or to natural ground level, whichever is greater. Care shall be exercised to thoroughly compact the backfill material under the haunches of the pipe. Material shall be brought up evenly on both sides of the pipe.

When the top of the pipe is above the top of the trench, the backfill shall be compacted in layers not exceeding 6 inches and shall be brought up evenly on both sides of the pipe to 1 foot above the top of the pipe. The width of backfill on each side of the pipe for the portion above the top of the trench shall be equal to twice the pipe's diameter or 12 feet, whichever is less.

For PVC and polyethylene pipe, the backfill shall be placed in two stages; first to the top of the pipe and then at least 12 inches over the top of the pipe. The backfill material shall meet the requirements of paragraph 701-3.2c.

All backfill shall be compacted to the density required under Item P-152.

METHOD OF MEASUREMENT

701-4.1 Pipe. The length of pipe will be measured in linear feet of pipe in place, completed, and approved. It will be measured along the centerline of the pipe from end or inside face of structure to the end or inside face of structure, whichever is applicable. The several classes, types and size will be measured separately. All fittings and end sections will be included in the length of the pipe being measured.

701-4.2 Concrete. The volume of concrete for pipe cradles to be paid for will be the number of cubic yards of concrete which is completed in place and accepted.

701-4.3 Rock. The volume of rock to be paid for will be the number of cubic yards of rock excavated. No payment will be made for the cushion material placed for the bed of the pipe.

BASIS OF PAYMENT

701-5.1 Payment will be made at the contract unit price per linear foot for each kind of pipe of the type and size designated; at the contract unit price per cubic yard of concrete for pipe cradles; and at the contract unit price per cubic yard for rock excavation.

Payment will be made under:

Item D-701a	( Type ) Pipe,  ( Diam. ) inch - per linear foot

Item D-701b	Concrete for pipe cradles - per cubic yard

Item D-701c	Rock excavation - per cubic yard

MATERIAL REQUIREMENTS

AASHTO M 190	Bituminous-Coated Corrugated Metal Culvert Pipe and Pipe Arches

AASHTO M 196	Corrugated Aluminum Alloy Culverts and Underdrains

AASHTO M 198	Joints for Circular Concrete Sewer and Culvert Pipe Using Flexible Watertight Gaskets

AASHTO M 219	Aluminum Alloy Structural Plate for Pipe, Pipe-Arches, and Arches

AASHTO M 243	Field Applied Coating of Corrugated Metal Structural Plate for Pipe, Pipe-Arches, and Arches

AASHTO M 252	Corrugated Polyethylene Drainage Tubing

AASHTO M 294	Corrugated Polyethylene Pipe, 300 to 1200 mm Diameter

AASHTO M 304	Poly (Vinyl Chloride) (PVC) Profile Wall Drain Pipe and Fittings Based on Controlled Inside Diameter

ASTM A 760	Corrugated Steel Pipe, Metallic-Coated for Sewers and Drains

ASTM A 761	Steel Galvanized, Corrugated Structural Plates and Fasteners for Pipe, Pipe-Arches, and Arches

ASTM A 762	Precoated (Polymeric) Galvanized Steel Sewer and Drainage Pipe

ASTM A 849	Post-Coated and Lined (Bituminous or Concrete) Corrugated Steel Sewer and Drainage Pipe

ASTM A 885	Steel Sheet, Zinc and Aramid Fiber Composite Coated for Corrugated Steel Sewer, Culvert, and Underdrain Pipe

ASTM B 745	Corrugated Aluminum Alloy Culvert Pipe

ASTM C 14	Concrete Sewer, Storm Drain, and Culvert Pipe

ASTM C 76	Reinforced Concrete Culvert, Storm Drain, and Sewer Pipe

ASTM C 94	Ready Mixed Concrete

ASTM C 144	Aggregate for Masonry Mortar

ASTM C 150	Portland Cement

ASTM C 443	Joints for Circular Concrete Sewer and Culvert Pipe, Using Rubber Gaskets

ASTM C 506	Reinforced Concrete Arch Culvert, Storm Drain, and Sewer Pipe

ASTM C 507	Reinforced Concrete Elliptical Culvert, Storm Drain and Sewer Pipe

ASTM C 655	Reinforced Concrete D-Load Culvert, Storm Drain and Sewer Pipe

ASTM C 700	Vitrified Clay Pipe, Extra Strength, Standard Strength, and Perforated

ASTM C 789	Precast Reinforced Concrete Box Sections for Culverts, Storm Drains, and Sewers

ASTM C 850	Precast Reinforced Concrete Box Sections for Culverts, Storm Drains, and Sewers with Less than 2 feet of Cover

ASTM D 1056	Flexible Cellular Materials--Sponge or Expanded Rubber

ASTM D 1190	Concrete Joint Sealer, Hot Poured Elastic Type

ASTM D 3034	Type PSMPoly (Vinyl Chloride) (PVC) Sewer Pipe and Fittings

ASTM D 3212	Joints for Drain and Sewer Plastic Pipes Using Flexible Elastomeric Seals

ASTM F 477	Elastomeric Seals (Gaskets) for Joining Plastic Pipe

ASTM F 794	Poly (Vinyl Chloride) Ribbed Drain Pipe & Fittings Based on Controlled Inside Diameter

ASTM F 949	Poly (Vinyl Chloride) (PVC) Corrugated Sewer Pipe With a Smooth Interior and Fittings

ITEM D-702	SLOTTED DRAINS

DESCRIPTION

702-1.1 This item shall consist of the construction of steel slotted drains or cast iron slotted vane drains in accordance with these Specifications and in reasonably close conformity with the lines and grades shown on the Plans. Type detail shall be shown on the Plans.

MATERIALS

702-2.1 GENERAL. All slotted drains shall meet the requirements shown on the Plans and specified below. All slotted drains shall meet specified hydraulic design requirements and shall support the loadings specified.

Standard details can be found in AASHTO-AGC-ARTBA publication A Guide to Standardized Highway Drainage Products. All products used shall meet the strict airport loading and tire pressure requirements.

702-2.2 PIPE.

- Steel slotted Drain. Pipe shall be metallic coated (galvanized or aluminized steel type II) corrugated steel type I meeting the requirements of ASTM A760. Pipe diameter and gage shall be as shown on the Plans.

The corrugated steel pipe shall have a minimum of two rerolled annular ends.

- Cast Iron Slotted Vane Drain. Polyvinyl Chloride (PVC) pipe shall meet the requirements of ASTM D 3034. Pipe diameter shall be as shown on the Plans. The pipe shall have an open slot to accept the cast iron slotted vane drain castings.

702-2.3 GRATES AND CASTINGS.

- Steel Slotted Drain. Grates shall be manufactured from ASTM A 36 or A 570, Grade 36 steel. Spacers and bearing bars (sides) shall be 3/16-inch material. The spacers shall be welded to each bearing bar with four 1-1/4-inch long by 3/16-inch wide fillet welds on each side of the bearing bar at spacings not exceeding 6 inches. The grates shall be 6 inches high or as shown on the Plans and shall have a maximum 1 3/4-inch opening in the top.

Grates shall be galvanized in accordance with ASTM A 123 except with a 2 ounces per square foot galvanized coating.

The grates shall be fillet welded to the corrugated steel pipe with a minimum weld 1 inch long on each side of the grate at every other corrugation. Weld areas and the heat affected zones where the slot is welded to the corrugated pipe shall be thoroughly cleaned and painted with a zinc-rich paint in accordance with repair of damaged coatings in ASTM A 760.

Each 20-foot length of drain delivered to the job site shall be within the following tolerances: vertical bow ± 3/8 inch, horizontal bow ± 5/8 inch, twist ± 1/2 inch.

- Cast Iron Slotted Vane Drain. Castings shall meet the requirements of ASTM A 48, Class 35B gray iron. Castings shall be furnished with no coatings.

Castings shall be designed to fit on open slots in 15-inch PVC pipe. Casting sections shall not exceed 3 feet in length. Casting sections shall have a built-in vane configuration with bar spacings not exceeding 6 inches. The opening at the surface shall not exceed 3 3/4 inches, and the vane shall be constructed on a radius so that the opening shall be less than 1-1/2 inches at a depth of 1-1/2 inches as measured vertically from the surface. Casting sections shall integrally lock into the concrete by use of top and bottoms flanges and shear tabs. Castings shall accept bolts for bolting sections together and shall accept wire for fitting to pipe.

702-2.3 CONCRETE. Plain or reinforced concrete used shall conform to the requirements of Item P-610.

- Steel Slotted Drain. Concrete shall have a minimum compressive strength of 1,000 psi at 28 days when tested in accordance with ASTM C 39.

- Cast Iron Slotted Vane Drain. Concrete shall have a minimum compressive strength of 3,000 psi at 28 days when tested in accordance with ASTM C 39.

CONSTRUCTION METHODS

702-3.1 EXCAVATION. The width of the trench shall be sufficient to permit satisfactory installation and jointing of the slotted drain and placing of a high slump concrete backfill material under and around the drain, but shall not be less than the external pipe diameter plus 6 inches on each side. The depth of the trench shall be a minimum of 2 inches below the invert for steel slotted drain and 6 inches below the invert for cast iron slotted vane drain.

The trench may be roughly shaped to the slotted drain bed.

702-3.2 INSTALLATION. Steel slotted drain shall be laid in sections joined firmly together with coupling bands, or as shown on the Plans. Cast iron drains shall be wired to the top of the PVC pipe in the slot cut in to receive the castings. The top of all drains shall be held firmly in place to the proper grade, to preclude movement during the backfilling operation.

702-3.3 JOINING. Slotted steel drain joints shall be firmly joined by modified hugger type bands, or as indicated, to secure the pipe and prevent infiltration of the backfill. When the slotted steel drain is banded together, the adjacent grates shall have a maximum 3-inch gap. Cast iron drain castings shall be bolted together.

702-3.4 BACKFILLING. Slotted drains shall be inspected before any backfill is placed. Damaged drains shall be aligned or replaced at the expense of the Contractor.

The slotted drain assembly shall be backfilled with concrete that will easily flow under and around the drain and the trench wall. The opening in the top of grates and castings shall be covered to prevent unwanted material from entering the drain during the backfilling and subsequent surfacing operations.

METHOD OF MEASUREMENT

702-4.1 The length of slotted drain will be measured in linear feet of slotted drain in place, completed, and approved. It will be measured along the centerline of the drain from end or inside face of structure to the end or inside face of structure, whichever is applicable. The several classes, types, and sizes will be measured separately. All fittings will be included in the length as typical pipe sections being measured.

BASIS OF PAYMENT

702-5.1 Payment will be made at the contract unit price per linear foot for each kind of slotted drain type and size designated and at the contract unit price per cubic yard of concrete for backfill.

Payment will be made under:

Item D-702a	Slotted Drain, [ diam. ] inch diameter, [ gage ] gage pipe - per linear foot

Item D-702b	Concrete for backfill - per cubic yard

TESTING REQUIREMENTS

ASTM C 39	Compressive Strength of Cylindrical Concrete Specimens

MATERIAL REQUIREMENTS

ASTM A 36	Structural Steel

ASTM A 123	Zinc (Hot-Dipped Galvanized) Coatings on Iron and Steel Products

ASTM A 570	Steel, Sheet and Strip, Carbon, Hot-Rolled, Structural Quality

ASTM A 760	Corrugated Steel Pipe, Metallic-Coated for Sewers and Drains

ASTM D 3034	Polyvinyl Chloride (PVC) Pipe

Information	A Guide to Standardized Highway Drainage Products disseminated under the sponsorship of the American Association of State Highway and Transportation Officials, Associated General Contractors, and the American Road and Transportation Builders Association

ITEM D-705	PIPE UNDERDRAINS

DESCRIPTION

705-1.1 This item shall consist of the construction of pipe drains in accordance with these Specifications and in reasonably close conformity with the lines and grades shown on the Plans.

MATERIALS

705-2.1 GENERAL. Materials shall meet the requirements shown on the Plans and specified below.

705-2.2 PIPE. The pipe shall be of the type called for on the Plans or in the bid and shall be in accordance with the following appropriate requirements.

Perforated Concrete Pipe 					ASTM C 444

Porous Concrete Pipe 					ASTM C 654

Polymer Precoated Perforated Corrugated Steel Pipe		ASTM A 762

Perforated Corrugated Aluminum Alloy Pipe			AASHTO M 196

Smooth-Wall Perforated PVC Pipe 				ASTM F 758

Poly (Vinyl Chloride) Ribbed Drain Pipe & Fittings 		ASTM F 794

Based on Controlled Inside Diameter

Poly (Vinyl Chloride)(PVC) Corrugated Sewer			ASTM F 949

Pipe With a Smooth Interior and Fittings

Perforated Corrugated Steel Pipe 				ASTM A 760

Bituminous-Coated Perforated Corrugated			AASHTO M 196 and M 190

Aluminum Alloy Pipe

Corrugated Polyethylene Drainage Tubing			AASHTO M 252

Corrugated Polyethylene Pipe, 300 to 1200 mm Diameter	AASHTO M 294

Poly (Vinyl Chloride) (PVC) Profile Wall Drain Pipe and 	AASHTO M 304

Fittings Based on Controlled Inside Diameter

705-2.3 JOINT MORTAR. Pipe joint mortar shall consist of one part portland cement and two parts sand. The portland cement shall conform to the requirements of ASTM C 150, Type I. The sand shall conform to the requirements of ASTM C 144.

705-2.4 ELASTOMERIC SEALS. Elastomeric seals shall conform to the requirements of ASTM F 477.

705-2.5 POROUS BACKFILL. Porous backfill shall be free of clay, humus, or other objectionable matter, and shall conform to the gradation in Table 1 when tested in accordance with ASTM C 136.

TABLE 1.    GRADATION OF POROUS BACKFILL

| Sieve Designation (square openings) | Percentage by Weight Passing Sieves |
| --- | --- |
|  | Porous Material No. 1 | Porous Material No. 2 |
| 1-1/2 in. |  | 100 |
| 1 in. |  | 90 - 100 |
| 3/8 in. | 100 | 25 - 60 |
| No. 4 | 95 - 100 | 5 - 40 |
| No. 8 | --- | 0 - 20 |
| No. 16 | 45 - 80 | --- |
| No. 50 | 10 - 30 | --- |
| No. 100 | 0 - 10 | --- |

When two courses of porous backfill are specified in the Plans, the finer of the materials shall conform to particle size tabulated herein for porous material No. 1. The coarser granular material shall meet the gradation given in the tabulation for porous material No. 2.

705-2.6. GRANULAR MATERIAL. Granular material used for backfilling shall conform to the requirements of ASTM D 2321 for Class IA, IB, or II materials, or shall meet the requirements of AASHTO Standard Specification for Highway Bridges Section 30.

705-2.7. FILTER FABRIC. The filter fabric shall conform to the requirements of AASHTO M 288, Class 2.

CONSTRUCTION METHODS

705-3.1 EQUIPMENT. All equipment necessary and required for the proper construction of pipe underdrains shall be on the project, in first-class working condition, and approved by the Engineer before construction is permitted to start.

705-3.2 EXCAVATION. The width of the pipe trench shall be sufficient to permit satisfactory jointing of the pipe and thorough tamping of the bedding material under and around the pipe, but shall not be less than the external diameter of the pipe plus 6 inches on each side. The trench walls shall be approximately vertical.

Where rock, hardpan, or other unyielding material is encountered, it shall be removed below the foundation grade for a depth of at least 4 inches. The excavation below grade shall be backfilled with selected fine compressible material, such as silty clay or loam, and lightly compacted in layers not over 6 inches in uncompacted depth to form a uniform but yielding foundation.

Where a firm foundation is not encountered at the grade established, due to soft, spongy, or other unstable soil, the unstable soil shall be removed and replaced with approved granular material for the full trench width. The engineer shall determined the depth of removal necessary. The granular material shall be compacted to provide adequate support for the pipe.

Excavated material not required or acceptable for backfill shall be disposed of by the Contractor as directed by the Engineer. The excavation shall not be carried below the required depth; when this is done, the trench shall be backfilled at the Contractor's expense with material approved by the Engineer and compacted to the density of the surrounding earth material.

The bed for the pipe shall be so shaped that at least the lower quarter of the pipe shall be in continuous contact with the bottom of the trench. Spaces for the pipe bell shall be excavated accurately to size to clear the bell so that the barrel supports the entire weight of the pipe.

The Contractor shall do such trench bracing, sheathing, or shoring necessary to perform and protect the excavation as required for safety and conformance to governing laws. Unless otherwise provided, the bracing, sheathing, or shoring shall be removed by the Contractor after the completion of the backfill to at least 12 inches over the top of the pipe. The sheathing or shoring shall be pulled as the granular backfill is placed and compacted to avoid any unfilled spaces between the trench wall and the backfill material. The cost of bracing, sheathing, or shoring, and the removal of same, shall be included in the unit price bid per linear foot for the pipe.

705-3.3 LAYING AND INSTALLING PIPE.

- Clay or Concrete Pipe. The laying of the pipe in the finished trench shall be started at the lowest point and laid upgrade. When bell and spigot pipe is used, the bells shall be laid upgrade. If tongue and groove pipe is used, the groove end shall be laid upgrade. Holes in perforated pipe shall be placed down, unless otherwise shown on the Plans. The pipe shall be firmly and accurately set to line and grade so that the invert will be smooth and uniform. Pipe shall not be laid on frozen ground.

Pipe which is not true in alignment, or which shows any settlement after laying, shall be taken up and relaid without extra compensation.

- Metal and Fiber Pipe. The metal pipe shall be laid with the separate sections joined firmly together with bands, with outside laps of circumferential joints pointing upgrade, and with longitudinal laps on the sides. Any metal in the pipe or bands which is not protected thoroughly by galvanizing shall be coated with a suitable asphaltum paint.

The sections of bituminized-fiber pipe shall be securely fastened together with suitable fittings. When the fiber couplings are tapered, they shall provide a tight, driven fit.

During installation, the asphalt-protected pipe shall be handled without damaging the asphalt coating. Any breaks in the bitumen or treatment of the pipe shall be refilled with the type and kind of bitumen used in coating the pipe originally.

- PVC or Polyethylene Pipe. PVC or polyethylene pipe shall be installed in accordance with the requirements of ASTM D 2321 or AASHTO Standard Specification for Highway Bridges Section 30. Perforations shall meet the requirements of AASHTO M 252 or M 294 Class 2, unless otherwise indicated on the Plans. The pipe shall be laid accurately to line and grade.

- All Types of Pipe. The upgrade end of pipelines, not terminating in a structure, shall be plugged or capped as approved by the Engineer.

Unless otherwise shown on the Plans, a 4-inch bed of granular backfill material shall be spread in the bottom of the trench throughout the entire length under all perforated pipe underdrains.

Pipe outlets for the underdrains shall be constructed when required or shown on the Plans. The pipe shall be laid with tight-fitting joints. Porous backfill is not required around or over pipe outlets for underdrains. All connections to other drainage pipes or structures shall be made as required and in a satisfactory manner. If connections are not made to other pipes or structures, the outlets shall be protected and constructed as shown on the Plans.

- Filter Fabric. The filter fabric shall be installed in accordance with the manufacturer's recommendations, or in accordance with AASHTO M 288 APPENDIX, unless otherwise shown on the Plans.

705-3.4 MORTAR. The mortar shall be of the desired consistency for caulking and filling the joints of the pipe and for making connections to other pipes or to structures. Mortar that is not used within 45 minutes after water has been added shall be discarded. Retempering of mortar shall not be permitted.

705-3.5 JOINTS IN CLAY OR CONCRETE PIPE. When open or partly open joints are required or specified, they shall be constructed as indicated on the Plans. The pipe shall be laid with the ends fitted together as designed. If bell and spigot pipe is used, mortar shall be placed along the inside bottom quarter of the bell to center the following section of pipe.

The open or partly open joints shall be surrounded with granular material meeting requirements of porous backfill No. 2 or as indicated on the Plans. This backfill shall be placed so its thickness will be not less than 3 inches nor more than 6 inches, unless otherwise shown on the Plans.

When the original material excavated from the trench is impervious, commercial concrete sand or granular material meeting requirements of porous backfill No. 1 shall surround porous backfill No. 2, as shown on the Plans or as directed by the Engineer.

When the original material excavated from the trench is previous and suitable, it may be used as backfill in lieu of porous backfill No. 1, when indicated on the Plans or as directed by the Engineer.

705-3.6 BACKFILLING.

- Earth. All trenches and excavations shall be backfilled within a reasonable time after the pipes are installed, unless other protection of the pipe is directed. The backfill material shall be selected material from excavation or borrow; material which is placed within a nominal pipe diameter distance at the sides of the pipe and 1 foot over the top shall be material which can be readily compacted. It shall not contain stones retained on a 3-inch sieve, frozen lumps, chunks of highly plastic clay, or any other material which is objectionable to the Engineer. The material shall be moistened or dried, if necessary to be compacted by the method in use. Backfill material shall be approved by the Engineer. Special care shall be taken in placing the backfill. Great care shall be used to obtain thorough compaction under the haunches and along the sides to the top of the pipe.

The backfill shall be placed in loose layers not exceeding 6 inches in depth under and around the pipe, and not exceeding 8 inches over the pipe. Successive layers shall be added and thoroughly compacted by hand and pneumatic tampers, approved by the Engineer, until the trench is completely filled and brought to the proper elevation. Backfilling shall be done in a manner to avoid injurious top or side pressures on the pipe.

In embankments and for other areas outside of pavements, the backfill shall be compacted to the density required for embankments in unpaved areas under Item P-152. Under paved areas, the subgrade and any backfill shall be compacted to the density required for embankments for paved areas under Item P-152.

- Granular Material. When granular backfill is required, its placement in the trench and about the pipe shall be as shown on the Plans. Special care shall be taken in placing the backfill. The granular backfill shall not contain a damaging amount of foreign matter, nor shall earth from the sides of the trench or from the windrow be allowed to filter into the backfill. When required by the Engineer, a template shall be used to properly place and keep separate the two sizes of backfill. The backfill shall be placed in loose layers not exceeding 6 inches in depth and compacted by hand and pneumatic tampers to the requirements as given for earth backfill. Backfilling shall be done in a manner to avoid injurious top or side pressure on the pipe. The granular backfill shall be made to the elevation of the trench, as shown on the Plans.

When perforated pipe is specified, granular backfill material shall be placed along the full length of the pipe. The position of the granular material shall be as shown on the Plans. If the original material excavated from the trench is pervious and suitable, it shall be used in lieu of porous backfill No. 1.

When porous backfill is to be placed in paved or adjacent areas prior to the completion of grading or subgrade operations, the backfill material shall be placed immediately after laying the pipe. The depth of this granular backfill shall be not less than 12 inches, measured from the top of the underdrain. During subsequent construction operations, this minimum backfill of 12 inches of depth shall not be disturbed until such time as the underdrains are to be completed. When the underdrains are to be completed, the unsuitable material shall be removed until the porous backfill is exposed. That part of the porous backfill which contains objectionable material shall be removed and replaced with suitable material. The cost of removing and replacing any such unsuitable material shall be borne by the Contractor.

Whenever a granular subbase blanket course is to be used under pavements which extends beyond the edge of paving to the outside edge of the underdrain trench, the granular backfill material over the underdrains shall be placed in the trench up to an elevation of 2 inches above the bottom surface of the granular subbase blanket course. Immediately prior to the placing of the granular subbase blanket course, the Contractor shall blade this excess trench backfill from the top of the trench onto the adjacent subgrade where it can be incorporated into the granular subbase blanket course. Any unsuitable material which remains over the underdrain trench shall be removed and replaced. The subbase material shall be placed to provide clean contact between the subbase material and the underdrain granular backfill material for the full width of the underdrain trench.

- Deflection Testing. The Engineer may at any time, not withstanding previous material acceptance, reject or require re-installation of pipe that exceeds 5% deflection when measured in accordance with ASTM D 2321, including Appendices.

705-3.7 CONNECTIONS. When the Plans call for connections to existing or proposed pipe or structures, these connections shall be watertight and made so that a smooth uniform flow line will be obtained throughout the drainage system.

METHOD OF MEASUREMENT

705-4.1 The length of pipe to be paid for will be the number of linear feet of pipe underdrains in place, completed, and approved; measured along the centerline of the pipe from end or inside face of structure to the end or inside face of structure, whichever is applicable. The several classes, types, and sizes will be measured separately. All fittings will be included in the length as typical pipe sections in the pipeline being measured.

705-4.2 The quantity of porous backfill to be paid for will be the number of cubic yards of porous backfill No. 1 and No. 2, complete in place and accepted, and will be determined from the dimensions given on the Plans by typical trench sections indicating the placement of porous backfill or dimensions ordered by the Engineer.

705-4.3 The quantity of filter fabric to be paid for will be the number of square yards of filter fabric in place, completed, and approved; and will be determined from the dimensions given on the Plans by typical trench sections indicating the placement of filter fabric or dimensions ordered by the Engineer.

BASIS OF PAYMENT

705-5.1 Payment will be made at the contract unit price per linear foot for pipe underdrains of the type, class, and size designated; at the contract unit price per cubic yard for porous backfill No.1; at the contract unit price per cubic yard for porous backfill No. 2, and at the contract unit price per square yard for filter fabric.

Payment will be made under:

Item D-705a	[Type, Class] Underdrain, [Diam.] inch - per linear foot

Item D-705b	Porous Backfill No. 1 - per cubic yard

Item D-705c	Porous Backfill No. 2 - per cubic yard

Item D-705d	Filter Fabric - per square yard

MATERIAL REQUIREMENTS

AASHTO M 190	Bituminous Coated Corrugated Metal Culvert Pipe and Pipe Arches

AASHTO M 196	Corrugated Aluminum Alloy Culverts and Underdrains

AASHTO M 252	Corrugated Polyethylene Drainage Tubing

AASHTO M 288	Geotextile Specification for Highway Applications

AASHTO M 294	Corrugated Polyethylene Pipe, 300 to 1200 mm Diameter

AASHTO M 304	Poly (Vinyl Chloride) (PVC) Profile Wall Drain Pipe and Fittings Based on Controlled Inside Diameter

AASHTO Standard Specifications for Highway Bridges

ASTM A 760	Corrugated Steel Pipe, Metallic-Coated for Sewers and Drains

ASTM A 762	Corrugated Steel Pipe, Polymer Precoated for Sewers and Drains

ASTM C 136	Sieve or Screen Analysis of Fine and Coarse Aggregates

ASTM C 144	Aggregate for Masonry Mortar

ASTM C 150	Portland Cement

ASTM C 444	Perforated Concrete Pipe

ASTM C 654	Porous Concrete Pipe

ASTM D 2321	Underground Installation of Flexible Thermoplastic Sewer Pipe

ASTM D 3034	Type PSM Poly(Vinyl Chloride) (PVC) Sewer Pipe and Fittings

ASTM F 477	Elastomeric Seals (Gaskets) for Joining Plastic Pipe

ASTM F 758	Smooth-Wall Poly(Vinyl Chloride) (PVC) Plastic Underdrain Systems for Highway, Airport, and Similar Drainage

ASTM F 949	Poly (Vinyl Chloride)(PVC) Corrugated Sewer Pipe with a Smooth Interior and Fittings

ITEM D-751	MANHOLES, CATCH BASINS, INLETS, AND INSPECTION HOLES

DESCRIPTION

751-1.1 This item shall consist of construction of manholes, catch basins, inlets, and inspection holes, in accordance with these Specifications, at the specified locations and conforming to the lines, grades, and dimensions shown on the Plans or required by the Engineer.

MATERIALS

751-2.1 BRICK. The brick shall conform to the requirements of ASTM C 32, Grade SM.

751-2.2 MORTAR. Mortar shall consist of one part portland cement and two parts sand. The portland cement shall conform to the requirements of ASTM C 150, Type I. The sand shall conform to the requirements of ASTM C 144.

751-2.3 CONCRETE. Plain and reinforced concrete used in structures, connections of pipes with structures, and the support of structures or frames shall conform to the requirements of Item P-610.

751-2.4 PRECAST CONCRETE PIPE MANHOLE RINGS. Precast concrete pipe manhole rings shall conform to the requirements of ASTM C 478. Unless otherwise specified, the risers and offset cone sections shall have an inside diameter of not less than 36 inches nor more than 48 inches.

751-2.5 CORRUGATED METAL. Corrugated metal shall conform to the requirements of AASHTO M 36.

751-2.6 FRAMES, COVERS, AND GRATES. The castings shall conform to one of the following requirements:

- Gray iron castings shall meet the requirements of ASTM A 48, Class 30B and 35B.

- Malleable iron castings shall meet the requirements of ASTM A 47.

- Steel castings shall meet the requirements of ASTM A 27.

- Structural steel for grates and frames shall conform to the requirements of ASTM A 283, Grade D.

- Ductile iron castings shall conform to the requirements of ASTM A 536.

- Austempered ductile iron castings shall conform to the requirements of ASTM A 897.

All castings or structural steel units shall conform to the dimensions shown on the Plans and shall be designed to support the loadings, aircraft gear configuration and/or direct loading, specified.

Each frame and cover or grate unit shall be provided with fastening members to prevent it from being dislodged by traffic but which will allow easy removal for access to the structure.

All castings shall be thoroughly cleaned. After fabrication, structural steel units shall be galvanized to meet the requirements of ASTM A 123.

751-2.7 STEPS. The steps or ladder bars shall be gray or malleable cast iron or galvanized steel. The steps shall be the size, length, and shape shown on the Plans and those steps that are not galvanized shall be given a coat of bituminous paint, when directed.

CONSTRUCTION METHODS

751-3.1 UNCLASSIFIED EXCAVATION.

- The Contractor shall do all excavation for structures and structure footings to the lines and grades or elevations, shown on the Plans, or as staked by the Engineer. The excavation shall be of sufficient size to permit the placing of the full width and length of the structure or structure footings shown. The elevations of the bottoms of footings, as shown on the Plans, shall be considered as approximately only; and the Engineer may order, in writing, changes in dimensions or elevations of footings necessary to secure a satisfactory foundation.

- Boulders, logs, or any other objectionable material encountered in excavation shall be removed. All rock or other hard foundation material shall be cleaned of all loose material and cut to a firm surface either level, stepped, or serrated, as directed by the Engineer. All seams or crevices shall be cleaned out and grouted. All loose and disintegrated rock and thin strata shall be removed. When concrete is to rest on a surface other than rock, special care shall be taken not to disturb the bottom of the excavation, and excavation to final grade shall not be made until just before the concrete or reinforcing is to be placed.

- The Contractor shall do all bracing, sheathing, or shoring necessary to implement and protect the excavation and the structure as required for safety or conformance to governing laws. The cost of bracing, sheathing, or shoring shall be included in the unit price bid for the structure.

- Unless otherwise provided, bracing, sheathing, or shoring involved in the construction of this item shall be removed by the Contractor after the completion of the structure. Removal shall be effected in a manner which will not disturb or mar finished masonry. The cost of removal shall be included in the unit price bid for the structure.

- After each excavation is completed, the Contractor shall notify the Engineer to that effect; and concrete or reinforcing steel shall be placed after the Engineer has approved the depth of the excavation and the character of the foundation material.

751-3.2 BRICK STRUCTURES.

- Foundations. A prepared foundation shall be placed for all brick structures after the foundation excavation is completed and accepted. Unless otherwise specified, the base shall consist of reinforced concrete mixed, prepared, and placed in accordance with the requirements of Item P-610.

- Laying Brick. All brick shall be clean and thoroughly wet before laying so that they will not absorb any appreciable amount of additional water at the time they are laid. All brick shall be laid in freshly made mortar. Mortar that is not used within 45 minutes after water has been added shall be discarded. Retempering of mortar shall not be permitted. An ample layer of mortar shall be spread on the beds and a shallow furrow shall be made in it which can be readily closed by the laying of the brick. All bed and head joints shall be filled solid with mortar. End joints of stretchers and side or cross joints of headers shall be fully buttered with mortar and a shoved joint made to squeeze out mortar at the top of the joint. Any bricks that may be loosened after the mortar has taken its set, shall be removed, cleaned, and relaid with fresh mortar. No broken or chipped brick shall be used in the face, and no spalls or bats shall be used except where necessary to shape around irregular openings or edges; in which case, full bricks shall be placed at ends or corners where possible, and the bats shall be used in the interior of the course. In making closures, no piece of brick shorter than the width of a whole brick shall be used; and wherever practicable, whole brick shall be used and laid as headers.

- Joints. All joints shall be slushed with mortar at every course, but slushing alone will not be considered adequate for making an acceptable joint. Exterior faces shall be laid up in advance of backing. Exterior faces shall be back plastered or pargeted with a coat of mortar not less than 3/8 inch thick before the backing is laid up. Prior to pargeting, all joints on the back of face courses shall be cut flush. Unless otherwise noted, joints shall be not less than 1/4 inch nor more than 1/2 inch wide and whatever width is adopted shall be maintained uniform throughout the work.

- Pointing. Face joints shall be neatly struck, using the weather joint. All joints shall be finished properly as the laying of the brick progresses. When nails or line pins are used the holes shall be immediately plugged with mortar and pointed when the nail or pin is removed.

- Cleaning. Upon completion of the work all exterior surfaces shall be thoroughly cleaned by scrubbing and washing down with water and, if necessary to produce satisfactory results, cleaning shall be done with a 5% solution of muriatic acid which shall then be rinsed off with liberal quantities of clean fresh water.

- Curing and Cold Weather Protection. In hot or dry weather, or when directed by the Engineer, the brick masonry shall be protected and kept moist for at least 48 hours after laying the brick. Brick masonry work or pointing shall not be done when there is frost in the brick or when the air temperature is below 50 °F unless the Contractor has on the project ready to use, suitable covering and artificial heating devices necessary to keep the atmosphere surrounding the masonry at a temperature of not less than 60 °F for the duration of the curing period.

751-3.3 CONCRETE STRUCTURES. Concrete structures shall be built on prepared foundations, conforming to the dimensions and form indicated on the Plans. The construction shall conform to the requirements specified in Item P-610. Any reinforcement required shall be placed as indicated on the Plans and shall be approved by the Engineer before the concrete is poured.

All invert channels shall be constructed and shaped accurately so as to be smooth, uniform, and cause minimum resistance to flowing water. The interior bottom shall be sloped downward toward the outlet.

751-3.4 PRECAST CONCRETE PIPE STRUCTURES. Precast concrete pipe structures shall be constructed on prepared or previously placed slab foundations and shall conform to the dimensions and locations shown on the Plans. All precast concrete pipe sections necessary to build a completed structure shall be furnished. The different sections shall fit together readily, and all jointing and connections shall be cemented with mortar. The top of the upper precast concrete pipe member shall be suitably formed and dimensioned to receive the metal frame and cover or grate, or other cap, as required. Provision shall be made for any connections for lateral pipe, including drops and leads that may be installed in the structure. The flow lines shall be smooth, uniform, and cause minimum resistance to flow. The metal steps which are embedded or built into the side walls shall be aligned and placed at vertical intervals of 12 inches. When a metal ladder replaces the steps, it shall be securely fastened into position.

751-3.5 CORRUGATED METAL STRUCTURES. Corrugated metal structures shall be constructed on prepared foundations, conforming to the dimensions and locations as shown on the Plans. The structures shall be prefabricated. standard or special fittings shall be furnished to provide pipe connections or branches of correct dimensions. The connections or branches shall be of sufficient length to accommodate connecting bands. The fittings shall be welded in place to the metal structures. When indicated, the structures shall be placed on a reinforced concrete base. The top of the metal structure shall be designed so that either a concrete slab or metal collar may be attached to which can be fastened a standard metal frame and grate or cover. Steps or ladders shall be furnished as shown on the Plans.

751-3.6 INLET AND OUTLET PIPES. Inlet and outlet pipes shall extend through the walls of the structures for a sufficient distance beyond the outside surface to allow for connections but shall be cut off flush with the wall on the inside surface, unless otherwise directed. For concrete or brick structures, the mortar shall be placed around these pipes so as to form a tight, neat connection.

751-3.7 PLACEMENT AND TREATMENT OF CASTINGS, FRAMES, AND FITTINGS. All castings, frames, and fittings shall be placed in the positions indicated on the Plans or as directed by the Engineer, and shall be set true to line and to correct elevation. If frames or fittings are to be set in concrete or cement mortar, all anchors or bolts shall be in place and position before the concrete or mortar is placed. The unit shall not be disturbed until the mortar or concrete has set.

When frames or fittings are to be placed upon previously constructed masonry, the bearing surface or masonry shall be brought true to line and grade and shall present an even bearing surface in order that the entire face or back of the unit will come in contact with the masonry. The unit shall be set in mortar beds and anchored to the masonry as indicated on the Plans or as directed and approved by the Engineer. All units shall set firm and secure.

After the frames or fittings have been set in final position and the concrete or mortar has been allowed to harden for 7 days, then the grates or covers shall be placed and fastened down.

751-3.8 INSTALLATION OF STEPS. The steps shall be installed as indicated on the Plans or as directed by the Engineer. When the steps are to be set in concrete, they shall be placed and secured in position before the concrete is poured. When the steps are installed in brick masonry, they shall be placed as the masonry is being built. The steps shall not be disturbed or used until the concrete or mortar has hardened for at least 7 days. After this period has elapsed, the steps shall be cleaned and painted, unless they have been galvanized.

When steps are required with precast concrete pipe structures, they shall be cast into the sides of the pipe at the time the pipe sections are manufactured or set in place after the structure is erected by drilling holes in the concrete and cementing the steps in place.

When steps are required with corrugated metal structures, they shall be welded into aligned position at a vertical spacing of 12 inches.

In lieu of steps, prefabricated ladders may be installed. In the case of brick or concrete structures, the ladder shall be held in place by grouting the supports in drilled holes. In the case of metal structures, the ladder shall be secured by welding the top support and grouting the bottom support into drilled holes in the foundation or as directed.

751-3.9 BACKFILLING.

- After a structure has been completed, the area around it shall be filled with approved material, in horizontal layers not to exceed 8 inches in loose depth, and compacted to the density required in Item P-152. Each layer shall be deposited all around the structure to approximately the same elevation. The top of the fill shall meet the elevation shown on the Plans or as directed by the Engineer.

- Backfilling shall not be placed against any structure until permission is given by the Engineer. In the case of concrete, such permission shall not be given until the concrete has been in place 7 days, or until tests made by the laboratory under supervision of the Engineer establish that the concrete has attained sufficient strength to provide a factor of safety against damage or strain in withstanding any pressure created by the backfill or the methods used in placing it.

- Backfill shall not be measured for direct payment. Performance of this work shall be considered as a subsidiary obligation of the Contractor covered under the contract unit price for the structure involved.

METHOD OF MEASUREMENT

751-4.1 Manholes, catch basins, inlets, and inspection holes will be measured by the unit.

BASIS OF PAYMENT

751-5.1 The accepted quantities of manholes, catch basins, inlets, and inspection holes will be paid for at the contract unit price per each, complete and in place. This price shall be full compensation for furnishing and installation of such specials and connections to pipes and other structures as may be required to complete the item as shown on the Plans.

Payment will be made under:

Item D-751a 	Manholes - per each

Item D-751b 	Catch Basins - per each

Item D-751c 	Inlets - per each

Item D-751d 	Inspection Holes - per each

MATERIAL REQUIREMENT

AASHTO M 36	Zinc Coated (Galvanized) Corrugated Iron or Steel Culverts and Underdrains

ASTM A 27	Mild to Medium-Strength Carbon-Steel Castings for General Application

ASTM A 47	Malleable Iron Castings

ASTM A 48	Gray Iron Castings

ASTM A 123	Zinc (Hot-Galvanized) Coatings on Products Fabricated from Rolled, Pressed, and Forged Steel Shapes, Plates, Bars and Strip

ASTM A 283	Low and Intermediate Tensile Strength Carbon Steel Plates, Shapes, and Bars

ASTM A 536	Ductile Iron Castings

ASTM A 897.	Austempered Ductile Iron Castings

ASTM C 32	Sewer and Manhole Brick

ASTM C 144	Aggregate for Masonry Mortar

ASTM C 150	Portland Cement

ITEM D-752	CONCRETE CULVERTS, HEADWALLS,

AND MISCELLANEOUS DRAINAGE STRUCTURES

DESCRIPTION

752-1.1 This item shall consist of plain or reinforced concrete culverts, headwalls, and miscellaneous drainage structures constructed in accordance with these Specifications, at the specified locations and conforming to the lines, grades, and dimensions shown on the Plans or required by the Engineer.

MATERIALS

752-2.1 CONCRETE. Concrete shall meet the requirements of Item P-610.

CONSTRUCTION METHODS

752-3.1 UNCLASSIFIED EXCAVATION.

- Trenches and foundation pits for structures or structure footings shall be excavated to the lines and grades or elevations shown on the Plans. The excavation shall be of sufficient size to permit the placing of the full width and length of the structure or structure footings shown. The elevations of the bottoms of footings, as shown on the Plans, shall be considered as approximate only; and the Engineer may order, in writing, changes in dimensions or elevations of footings necessary to secure a satisfactory foundation.

- Boulders, logs, or any other objectionable material encountered in excavation shall be removed. All rock or other hard foundation material shall be cleaned of all loose material and cut to a firm surface either level, stepped, or serrated, as directed by the Engineer. All seams or crevices shall be cleaned out and grouted. All loose and disintegrated rock and thin strata shall be removed. When concrete is to rest on a surface other than rock, special care shall be taken not to disturb the bottom of the excavation, and excavation to final grade shall not be made until just before the concrete or reinforcing steel is to be placed.

- The Contractor shall do all bracing, sheathing, or shoring necessary to perform and protect the excavation and the structure as required for safety or conformance to governing laws. The cost of bracing, sheathing, or shoring shall be included in the unit price bid for excavation.

- Unless otherwise provided, bracing, sheathing, or shoring involved therewith shall be removed by the Contractor after the completion of the structure. Removal shall be effected in a manner which will not disturb or mar finished concrete. The cost of removal shall be included in the unit price bid for excavation.

- After each excavation is completed, the Contractor shall notify the Engineer to that effect, and concrete or reinforcing steel shall be placed after the Engineer has approved the depth of the excavation and the character of the foundation material.

752-3.2 BACKFILLING.

- After a structure has been completed, backfill with approved material, in horizontal layers not to exceed 8 inches in loose depth, and compact. The field density of the compacted material shall be at least 90% of the maximum density for cohesive soils and 95% of the maximum density for noncohesive soils. The maximum density shall be determined in accordance with ASTM D 698. The field density shall be determined in accordance with ASTM D 1556 or ASTM D 2167.

- No backfilling shall be placed against any structure until permission is given by the Engineer. In the case of concrete, such permission shall not be given until the concrete has been in place 7 days, or until tests made by the laboratory under the supervision of the Engineer establish that the concrete has attained sufficient strength to provide a factor of safety against damage or strain in withstanding any pressure created by the backfill or the methods used in placing it.

- Fill placed around concrete culverts shall be deposited on both sides at the same time and to approximately the same elevation. All slopes bounding or within the areas to be backfilled shall be stepped or serrated to prevent wedge action against the structure.

- Backfill will not be measured for direct payment. Performance of this work under the contract is not payable directly but shall be considered as a subsidiary obligation of the Contractor, covered under the contract unit price for "unclassified excavation for structures."

752-3.3 WEEP HOLES. Weep holes shall be constructed as shown on the Plans.

METHOD OF MEASUREMENT

752-4.1 Unclassified excavation for structures will be measured in original position, between vertical planes 18 inches outside of and parallel to the neat lines of the footings.

752-4.2 Concrete will be measured by the dimensions shown on the Plans or ordered by the Engineer, complete in place and accepted. No measurements or other allowances will be made for forms, false work, cofferdams, pumping, bracing, expansion joints, or finishing of the concrete. No deductions will be made for the volumes of reinforcing steel or embedded items.

752-4.3 Reinforcing steel will be measured by the theoretical weight shown on the Plans, complete in place and accepted. The unit weight used for deformed bars will be the weight of plain square or round bars, as the case may be, of equal nominal size.

BASIS OF PAYMENT

752-5.1 Payment will be made at the contract unit price per cubic yard for unclassified excavation for structures; at the contract unit price per cubic yard for concrete for the structures; and at the contract unit price per pound for reinforcing steel.

Payment will be made under:

Item D-752a	Unclassified Excavation for Structures - -per cubic yard

Item D-752b	Structural Concrete - per cubic yard

Item D-752c	Reinforcing Steel - per pound

TESTING REQUIREMENTS

ASTM D 698	Moisture-Density Relations of Soils and Soil-Aggregate Mixtures Using 5.5 lb. Rammer and 12-in Drop

ASTM D 1556	Density of Soil in Place by the Sand-Cone Method

ASTM D 2167	Density of Soil in Place by the Rubber-Balloon Method

ITEM D-754	CONCRETE GUTTERS, DITCHES, AND FLUMES

DESCRIPTION

754-1.1 This item shall consist of portland cement concrete gutters, ditches, and flumes constructed in accordance with these Specifications at the specified locations in accordance with the dimensions, lines, and grades as shown on the Plans.

MATERIALS

754-2.1 CONCRETE. Plain and reinforced concrete shall meet the requirements of Item P-610.

754-2.2 JOINTS. Joint filler materials and premolded joint material shall conform to Item P-610.

CONSTRUCTION METHODS

754-3.1 PREPARING SUBGRADE. Excavation shall be made to the required width and depth, and the subgrade upon which the item is to be built shall be compacted to a firm uniform grade. All soft and unsuitable material shall be removed and replaced with suitable approved material. When required, a layer of approved granular material, compacted to the thickness indicated on the Plans, shall be placed to form a subbase. The underlying course shall be checked and accepted by the Engineer before placing and spreading operations are started.

754-3.2 PLACING. The forms for and the mixing, placing, finishing, and curing of concrete shall conform to the requirements of Item P-610 and shall be in accordance with the following requirements.

The concrete shall be tamped and spaded until it is consolidated and mortar entirely covers and forms the top surface. The surface of the concrete shall be floated smooth and the edges rounded to the radii shown on the Plans. Before the concrete is given the final finishing, the surface shall be tested with a 10-foot straightedge, and any irregularities of more than 1/4 inch in 10 feet shall be eliminated.

The concrete shall be placed with dummy-grooved joints not to exceed 25 feet apart, except where shorter lengths are necessary for closures, but no section shall be less than 4 feet long.

Expansion joints of the type called for in the Plans shall be constructed to replace a dummy groove at spacings of approximately 100 feet. When the gutter is placed next to concrete pavement, expansion joints in the gutter shall be located opposite expansion joints in the pavement. When a gutter abuts a pavement or other structure, an expansion joint shall be placed between the gutter and the other structure.

Forms shall not be removed within 24 hours after the concrete has been placed. Minor defects shall be repaired with mortar containing 1 part cement and 2 parts fine aggregate.

The operations of depositing, compacting, and finishing the item shall be conducted so as to build a satisfactory structure. If any section of concrete is found to be porous, other than minor defects which may be plastered, or is otherwise defective, it shall be removed and replaced by the Contractor without additional compensation.

754-3.3 BACKFILLING. After the concrete has set sufficiently, the spaces adjacent to the structure shall be refilled to the required elevation with material specified on the Plans and compacted by mechanical equipment to at least 90% of the maximum density as determined by ASTM D 698. The in-place density shall be determined in accordance with ASTM D 1556 or ASTM D 2167.

METHOD OF MEASUREMENT

754-4.1 Concrete will be measured by the dimensions shown on the Plans or ordered by the Engineer. No deductions will be made for the volume occupied by reinforcing steel, anchors, conduits, weep holes, or piling.

754-4.2 Reinforcing steel will be measured by the theoretical weight shown on the Plans or ordered by the Engineer. No allowance will be made for clips, wire, or other material used for fastening reinforcement in place.

BASIS OF PAYMENT

754-5.1 The accepted quantities of structural concrete will be paid for at the contract unit price per cubic yard, complete in place.

754-5.2 The accepted quantities of reinforcing steel will be paid for at the contract price per pound, complete in place.

Payment will be made under:

Item D-754a	Structural Concrete - per cubic yard

Item D-754b	Reinforcing Steel - per pound

TESTING REQUIREMENTS

ASTM D 698	Moisture-Density Relations of Soils and Soil-Aggregate Mixtures Using 5.5 lb. Rammer and 12-inch Drop

ASTM D 1556	Density of Soil in Place by the Sand-Cone Method

ASTM D 2167	Density of Soil in Place by the Rubber-Balloon Method

PART X – TURFING

ITEM T-901	SEEDING

DESCRIPTION

901-1.1 This work consists of preparing the ground and applying seed and fertilizer in conformance with the Plans and Specifications.

The intent of this work is to provide a living vegetative cover in the areas indicated on the Plans and to maintain the cover for the term of the Contract.

MATERIALS

901-2.1 Seed. Furnish the seed mixture listed in the Special Provisions.

Meet the applicable requirements of the State of Alaska Seed Regulations, 11 AAC 34, Articles 1 and 4.

Meet or exceed 95% pure seed and 74% germination.

Furnish 4 signed copies of a report for each lot of seed, certifying it has been tested by an approved laboratory within 9 months of date of seed application. Submit these certifications no later than 10 days prior to seeding. Include the following in each certification:

- name and address of laboratory

- date of test

- lot number

- seed name

- percent pure seed

- percent germination

- percent weed content

- percent inert matter

901-2.2 Fertilizer. Furnish a 20-20-10 fertilizer containing no cyanamid compounds or hydrated lime. Tolerances of the chemical ingredients shall be plus or minus 2%.

Use standard commercial fertilizer supplied separately or in mixtures, and in moisture proof containers. Mark each container with the total net weight and with the manufacturer’s guaranteed analysis of the contents showing the percentage for each ingredient.

CONSTRUCTION METHODS

901-3.1 SOIL PREPARATION. Clear all areas to be seeded of stones 4 inches in diameter and larger and of all sticks, stumps, noxious weeds, and other debris or irregularities that might interfere with the seeding operation, growth of grass, or subsequent maintenance of the grass covered areas.

Just prior to seeding, roughen the surface of all areas to be seeded by track-walking transversely up and down the slopes or using a scarifying slope board. Round the top and bottom of the slopes, when necessary, to facilitate tracking and to create a pleasing appearance, but do not disrupt drainage flow lines. Where fill is adjacent to wetlands, keep the equipment entirely on the fill slope.

901-3.2 SEEDING SEASONS. Seed and fertilize between May 15 and August 15.

Do not seed during windy conditions or when climatic conditions or ground conditions would hinder placement or proper growth.

901-3.3 APPLICATION. Apply seed and fertilizer at the rates specified in the Special Provisions. Use either of the following methods:

a.	Hydraulic Method.

- Mix a slurry of seed, fertilizer, water, and other components as required by the Special Provisions. Add seed to the slurry mixture no more than 30 minutes before application.

- Use hydraulic seeding equipment that will maintain a continuous agitation and apply a homogeneous mixture through a spray nozzle. The pump must produce enough pressure to maintain a continuous nonfluctuating spray that will reach the extremities of the seeding area, without causing damage to the seed bed. Use a hose attachment to reach areas where a fixed nozzle cannot reach.

- If mulch material is required, add it to the water slurry in the hydraulic seeder after adding the proportionate amounts of seed and fertilizer.

- Apply slurry at a rate that distributes all materials evenly.

b.	Dry Method.

- Use mechanical spreaders, seed drills, landscape seeders, cultipacker seeders, fertilizer spreaders, or other approved mechanical spreading equipment.

- Moisten the soil prior to the application of seed and fertilizer and immediately afterwards.

- Mix or rake the seed and fertilizer into the seed bed to a depth of 1/2 inch, unless mulch material is to be applied immediately.

901-3.4 MAINTENANCE OF SEEDED AREAS. Protect seeded areas against traffic using approved warning signs or barricades. Promptly repair surfaces that are gullied or otherwise damaged following seeding by regrading and reseeding, as directed. Maintain seeded areas in a satisfactory condition until final inspection and acceptance of the work.

Keep temporary erosion control measures in place until the vegetation is accepted.

Water the seeded areas, as required, for proper germination and growth. Use equipment that can acceptably water all seeded areas without vehicular traffic on seeded areas.

Reseed any seeded areas not showing evidence of satisfactory growth, as directed.

Final acceptance will be based on the following criteria and must provide 70% vegetative coverage of the seeded area. If seeding is completed by July 15th, coverage must be attained by September 30th. If seeding is completed by August 15th, coverage must be attained by June 15th of the following season. Final acceptance will be based on the Engineers approval.

METHOD OF MEASUREMENT

901-4.1 The work will be measured in accordance with Subsection 90-02, and as follows:

a.	Seeding by the acre. By the area of ground surface acceptably seeded, fertilized, and maintained. Required reseeding is subsidiary.

b.	Seeding by the pound. By the weight of seed acceptably placed. Fertilizer is subsidiary. Any other work required will be measured separately.

c.	Water for maintenance. By the M-gal (1,000 gallons) acceptably placed. Use a conversion factor of 8.34 pounds per gallon, if measured by weight. Use a conversion factor of 7.48 gallons per cubic foot, if measured by volume.

BASIS OF PAYMENT

901-5.1 At the contract unit price per unit of measure for the pay items listed below that appear on the bid schedule.

Water for hydraulic application of seed mixtures is subsidiary.

Mulching will be measured and paid for under Item T-908.

Payment will be made under:

Item T-901a	Seeding - per acre

Item T-901b	Seeding - per pound

Item T-901c	Water for Maintenance - per M-gal

ITEM T-905	TOPSOILING

# DESCRIPTION

905-1.1 This work consists of furnishing and spreading topsoil where shown on the Plans.

MATERIALS

905-2.1 TOPSOIL. Furnish a natural friable surface soil without admixtures of undesirable subsoil, refuse, or foreign materials and reasonably free from roots, clods, hard clay, noxious weeds, tall grass, brush sticks, stubble or other litter, and which is free draining and non-toxic.

Meet the grading requirements in Table 1 for the class of topsoil shown on the Plans:

### TABLE 1.    TOPSOIL GRADING

| Sieve Designation | Percent Passing By Weight |
| --- | --- |
|  | CLASS A | CLASS B |
| 3 in | - | 100 |
| 1/2 in. | 100 | - |
| No. 4 | 95-100 | 75-100 |
| No. 16 | 64-90 | 50-95 |
| No. 200 | 30-60 | 20-80 |
| Organic Matter | 10-40 | 5 min. |

Percent of organic matter will be determined by loss-on-ignition of oven dried samples using ATM 203.

When necessary, amend natural topsoil to meet the above specifications, using approved materials and methods.

CONSTRUCTION METHODS

905-3.1 PREPARING THE GROUND SURFACE. Where grades in the areas to be topsoiled have not been established, smooth-grade the areas to the grades shown on the Plans. Maintain the prescribed grades in an even and properly compacted condition to prevent the formation of low places or pockets where water will stand.

Clear the surface of the area to be topsoiled of all stones larger than 2 inches in any diameter and all litter or other material which may be detrimental to proper bonding, the rise of capillary moisture, or the proper growth of the desired planting.

Immediately prior to dumping and spreading the topsoil, loosen the surface, by approved means, to a minimum depth of 2 inches to facilitate bonding of the topsoil to the covered subgrade soil.

905-3.2 OBTAINING TOPSOIL. Prior to the stripping of topsoil from designated areas, remove any vegetation, stumps and large roots, rubbish or stones found on such areas, which may interfere with subsequent operations, using approved methods.

When suitable topsoil is available on the site, remove this material from the designated areas to the depth directed. Spread the topsoil on areas already tilled and smooth-graded, or stockpile in approved areas. Grade the stockpile sites and adjacent areas which have been disturbed if required and put into a condition acceptable for seeding.

When suitable topsoil is secured off the airport site, locate and obtain the supply, subject to approval. Notify the Engineer sufficiently in advance of operations in order that necessary measurements and tests can be made. Remove the topsoil from approved areas and to the depth as directed. Haul the topsoil to the site of the work and stockpile or spread as required.

905-3.4 PLACING TOPSOIL. Spread the topsoil evenly on the prepared areas to a uniform depth of 4 inches after compaction. Do not spread when the ground or topsoil is frozen or excessively wet.

After spreading, break up any large stiff clods and hard lumps with a pulverizer or other effective means. Rake up and dispose of all stones or rocks (2 inches or more in diameter), roots, litter, or any foreign matter. After spreading, compact the topsoil with a cultipacker or by other approved means. The compacted topsoil surface shall conform to the required lines, grades, and cross sections. Promptly remove any topsoil or other dirt falling upon pavements or other surface courses.

METHOD OF MEASUREMENT

905-4.1 By the square yard, in accordance with Subsection 90-02, acceptably placed.

BASIS OF PAYMENT

905-5.1 Payment will be made at the contract unit price per square yard.

Stockpiling and rehandling of topsoil are subsidiary.

Payment will be made under:

Item T-905a	Topsoiling - per square yard

ITEM T-908	SOIL STABILIZATION

DESCRIPTION

908-1.1 This work consists of furnishing, placing, and maintaining soil stabilization material where shown on the Plans.

## MATERIALS

908-2.1 MULCH. Virgin/recycled wood fiber, recycled paper (wood cellulose), or an acceptable blend containing up to 50% recycled paper, with the following characteristics:

- Contains no growth or germination inhibiting factors.

- Will remain in uniform suspension in water under agitation and will blend with grass seed, fertilizer and other additives to form a homogeneous slurry, when required.

- Will form a uniform, blotter-like ground cover on application, having moisture absorption and percolation properties and the ability to cover and hold grass seed in contact with soil.

- Will not form a hard crust upon drying.

- Dyed a suitable color to facilitate inspection of its placement.

Ship the mulch in packages of uniform weight (plus or minus 5%) bearing the name of the manufacturer and the air-dry weight content.

Use a commercial tackifier on all slopes 4:1 or steeper Use the amount recommended by the manufacturer.

908-2.2 ROLLED MATTING. Use materials that conform to one of the following standards:

- Unbleached single jute yarn. Use yarn that is loosely twisted and not varying in thickness more than one-half its normal diameter. Furnish jute mesh in rolled strips conforming to the following requirements.

- Width: 45 to 48 inches, ( 1 inch.

- 78 warp-ends per width of cloth (minimum).

- 41 weft-ends per yard (minimum).

- Weight: 1.22 pounds per linear yard, ( 5%

- Knitted Straw Matting. Commercially manufactured erosion control blanket. Use netting which is biodegradable. Straw shall be from oats, wheat, rye, rice, or other approved grain crops that are free from noxious weeds, mold, or other objectionable material. May contain coconut or other natural fiber to reinforce the straw. Follow the manufacturer’s published recommendations.

908-2.4 STAPLES. U-shaped staples for anchoring matting, approximately 6 inches long and 1 inch wide. Machine-made: No. 11 gage or heavier steel wire. Hand-made: 12-inch lengths of No. 9 gage or heavier steel.

## CONSTRUCTION REQUIREMENTS

908-3.1 SURFACE PREPARATION. Smooth the surface and backfill all gullies and potholes before application.

Remove all sticks and other foreign matter that prevents contact of the mulch or matting and the soil.

Ensure that the surface is moist at the time of placement.

If area is to be seeded, soil preparation shall conform to Section 901-3.1.

908-3.2 APPLICATION. Apply soil stabilization material at the rate specified in the Special Provisions.

If seeding is specified, complete the application of mulch or matting within 24 hours after seed is placed.

Staple matting every 5 feet at overlapped joints and edges or as recommended by the manufacturer.

Do not use vehicles or equipment which cause rutting or displacement of the subgrade or topsoil.

908-3.3 MAINTENANCE. Reshape and reseed any damaged areas and repair the mulch or matting as required.

Maintain the mulch or matting until all work on the project is complete and accepted.

METHOD OF MEASUREMENT

908-4.1 By the square yard, in accordance with Subsection 90-02, acceptably placed. Water, maintenance, and repair are subsidiary.

## BASIS OF PAYMENT

908-5.1 At the contract unit price per unit of measure for the pay items listed below that appear on the bid schedule.

Payment will be made under:

Item T-908a	Mulching - per square yard

Item T-908b	Rolled Matting - per square yard

PART XI - LIGHTING INSTALLATION

ITEM L-100	RUNWAY AND TAXIWAY LIGHTING

100-1.1 DESCRIPTION. This item consists of furnishing and installing runway and taxiway lighting systems as indicated on the Plans and as specified herein.

100-2.1 MATERIALS. Obtain approval of all materials and equipment to be used or incorporated in the work, prior to their shipment to the project site. Submit to the Engineer 5 complete listings of materials and equipment specified herein and on the Plans. Clearly identify the material or equipment by item, name, or designation used on the Plans or specifications and indicate where specified. Include applicable catalog numbers, cuts, wiring diagrams, performance data, and operation and maintenance manuals. Neatly bind and clearly index the submittals. In addition, when specified, include in the submittals certificates of compliance, manufacturer's instructions and/or shop drawings, or proposed construction or installation procedures.

- Certified Airport Lighting Equipment. The following items shall conform to the applicable FAA specifications, except as shown on the Plans and/or modified herein. The equipment shall be certified and listed under AC 150/5345-53, Airport Lighting Equipment Certification Program. This AC, the latest certified equipment list, and the address list of certified airport lighting equipment manufacturers are available on the Internet home page for the FAA Office of the Associate Administrator for Airports (ARP). The direct Internet address is <www.faa.gov/arp/arphome.htm>.

ITEM	FAA AC 150/

- Constant Current Regulator, L-828, class, style, and size as indicated on Plans, 60 Hz input, with brightness control for remote operation.	5345-10

- Runway Edge Light, Bi-directional High-Intensity, L-862, and Threshold Light, L-862E, with lamp, support column, metal frangible coupling, stainless steel bolts, and upper plug and cord assembly. The lens shall be clamp band style. Complete with lens coloration, lamp wattage, and specified support column height.	5345-46

- Runway Edge Light, Medium Intensity, L-861, and Threshold Light, L-861E, with incandescent 6.6 A lamp and Lexan lens with support column, metal frangible coupling with stainless steel hex head set screws, and upper plug and cord assembly with separable connector and stainless steel lens encircling clamp band. Complete with lens coloration, lamp wattage, and specified support column height.	5345-46

- Taxiway Edge Light, Medium Intensity, L861T, with incandescent 6.6 A lamp and Lexan lens, with support column, metal frangible coupling with stainless steel hex head set screws, and upper plug and cord assembly with separable connector and stainless steel lens encircling clamp band.	5345-46

- Airport Signs, L-858, internally lighted.	5345-44

- Airport Signs, L-858, unlighted.	5345-44

- Airport Light Base, L-867, transformer housing, Class I, Size B or D, 24 inches deep, one piece with internal grounding lug, gasket, steel cover, base extension, drain opening, and conduit.	5345-42

- Airport Light Base, L-867, Watertight, transformer housing, shall be 12 inch x 24 inch, non-steel light bases, meeting the requirements for non-vehicle loading light bases, type L-867. The bases shall be made from Type III, ultra-high molecular weight, heavy-wall, high-density polyethylene pipe having a cell classification of 345434C or better in accordance with ASTM D 3350. A conduit stub made of the same material as the light bases shall be sidewall fused to the bases using saddle fittings, or other approved method for a watertight connection.	5345-42

- Airport Light Base, L-868, transformer housing, Class I, Steel, Size B, 12 inches deep , two section light base assembly with grooved and "O" ringed flange ring with concrete ring. Complete with any necessary spacer rings, internal grounding lug, mud plate, anti-rotational fins and conduit hubs.	5345-42

- Isolating Transformer, L-830, individual lamp type, series-to-series, 5000 V, 6.6 A to 6.6 A, 30/45 W or 200 W	5345-47

- Isolating Transformer, L-830, individual lamp type, series-to-series, 5000 V, 20 A to 6.6 A, 100 W, 200 W or 300 W. Transformers shall have leads of the length shown on the plans.	5345-47

- Isolating Transformer, L-830-1, individual lamp type, series-to-series, 5000 V, 6.6 A to 6.6 A, 30/45 W.	5345-47

- Isolating Transformer, L-830-6, individual lamp type, series-to-series, 500 V, 6.6 A to 6.6 A, 200 W.	5345-47

- Radio Control Equipment, L-854, Type I, with enclosure for surface mounting, antenna and feedline and set to the Common Traffic Advisory Frequency (CTAF) for the project airport as found in the Alaska Supplement of the U.S. Government Flight Publication.	5345-49

- Flush Taxiway Centerline Light Fixture, Uni or Bi-Directional, Type L-852A, or L-852B, Class 2, Mode 1, Style 3, a flat fixture with 1/4 inch or less clearance above finish surface, with 30 W lamps and color filters, plug and cord assembly, 1/2 inch watertight connector, stainless steel bolts, vibration proof fasteners, "Dry" system with the optical assembly sealed above and below with "O" rings .	5345-46

- Flush Runway Light Fixture, Uni or Bi-Directional, Type L-850A or L-850B, Class 2, Mode 1, Style 3, as indicated, with 1/4 inch or less clearance above finish surface, with 80 W lamps, color filters, a single 100 or 200 W transformer, plug and cord assembly, 1/2-inch watertight connector, stainless steel bolts, vibration proof fasteners, "Dry" system with the optical assembly sealed above and below with "O" rings. 	5345-46

- Primary Handhole, L-868, class 1, size B, steel, 24 inches deep x 12 inches diameter, 1-3/8 inch N.P.T. conduit hubs (with number and location of hubs as indicated, 4 inch bottom drain hole, steel cover and gasket, internal ground lug with connector and other misc. items. Handhole and cover shall be suitable for vehicle and aircraft wheel loading.	5345-42

- Wind Cone Primary Handhole, L-867, class 1, size D, steel, 24 inches deep x 16 inch diameter, one piece with internal ground lug with connector, steel cover with gasket, 4 inch drain hole, 2-1/8 inch N.P.T. and 1-3/8 inch N.P.T. conduit hubs with number and location of hubs indicated, and other misc. items.	5345-42

- Sealer. Adhesive sealant shall be a self-leveling silicone sealer.

- Transformer Support Platform. When called for on the Plans, light bases equipped with L-830 type isolating transformers shall, in addition to the other specified items, be provided with 13-3/4 inch high prefabricated steel, fixed height or folding type, transformer support platforms as shown on the Plans.

- Power Adapter. Power adapter, when called for in the plans shall be a series primary to 120 V regulated-voltage power supply suitable for use with a 3-step constant current regulator source. The power adapter shall be oil filled and include two replaceable internal fuses. Power adapter ratings shall be 670 VA at 120 V ac with ± 3% regulation @ 2.8 to 6.6 A primary current.

- Regularly Used Commercial Items. All other regularly used commercial items of electrical equipment not covered by FAA equipment specifications shall conform to the applicable NEMA rulings and standards for equipment of its type.

- Lock Washers. Lock washers shall be two piece cam-type lock washer.

- Free Flowing Insulating Material. Insulating material for filling of light bases shall be an inorganic, non-flammable, free-flowing granular material. The material shall be chemically treated to be hydrophobic. It shall be free of asbestos. The material shall have a density of 40 to 42 lb/ft3, and a load bearing strength of 83 psi.

- Lubricant and Sealant. Lubricant and sealant shall be a general purpose "O"-ring and valve lubricant. Temperature range shall be -40 (F to +400 (F.

- Soft Gasket. Gaskets to be installed between the base plate and base in watertight lighting systems shall be soft neoprene.

CONSTRUCTION METHODS

100-3.1 General. All work in connection with the airport lighting system shall be in accordance with the applicable provisions of the current NEC of the National Fire Protection Association and all State and local codes. Location of all new fixtures, conduit, cables, etc., shall be as shown on the Plans.

Level and align light fixtures according to manufacturer’s instructions. Level to within 1 degree. Align to within 1/2 inch at right angles to centerline and to within 1 inch parallel to centerline.

Where electrical cable or duct is required, such work will be covered under Item L-108 or L-110, as applicable.

Where remote relay assembly and/or remote control panel is required, such work will be covered under item L-109.

Provide all labor, materials, systems, equipment, facilities, and other incidental items as may be required to provide temporary electrical power for construction and testing of all contract work.

100-3.2 Installation of non-WATERTIGHT EDGE LIGHTS. The light base shall be placed on a layer of bedding material of minus 1/4 inch material that is not less than 6 inches in depth. Bedding material shall be, sand, gravel, crushed aggregate, or other suitable material containing no organic, frozen, or other deleterious material. If the light base is placed in the structural section (P-154, P-208, P-209) of a pavement such as for a runway or taxiway, the Contractor shall construct the backfill in accordance with the specifications for the material in which the duct is placed. The material shall be compacted to the requirements of the material into which it is placed. The light base shall be placed to between 3/8 inch and 3/4 inch of finished grade. The base shall be level to within (1/4 inch.

Connect the insolating transformer with L-823 connector kits and heat shrink tubing. Ensure that all field installed primary cable connectors have the plug pin connectors and receptacle socket connectors properly positioned within their respective connector bodies, as detailed by the connector manufacturer, prior to the shrinking of heat shrink tubing at the cable-connector interface.

Install isolating transformers in the light bases as shown on the Plans. Where called for on the Plans, install isolating transformers in all light bases by placing on top of a 14 inch (extended height) approved transformer supporting platform as specified. Train all connections to the isolating transformer to lay in the upper section of the light base, above the transformer platform and below the cover flange, as shown on the Plans. Provide adequate primary and secondary cable slack in each light base to assure that all connectors can be grouped and trained in the upper section of the light base without subjecting the connector to tension.

Label each edge light assembly with the letter and number designation as indicated on the Plans. Label by permanently die-stamping the letter and number designation onto the light base and base cover plate with 1/4 inch figures.

Install the light fixtures with stainless steel hardware and coat the bolts and frangible couplings with a suitable corrosion inhibitor prior to being installed. Install the light fixtures with lamp, clean the lenses, align and adjust each optical system in accordance with the manufacturer's instructions.

100-3.3 Installation of Flush Lights. Install flush light fixtures in accordance with the Plans and specifications.

Install flush runway edge and centerline light fixtures and taxiway centerline light fixtures after the old pavement has been cold planed, and before the asphalt is placed. Install flush taxiway and runway centerline and touchdown zone light fixtures on new runways or taxiways after the first asphalt lift and before the final lift.

Core remaining asphalt at the runway centerline light base locations a minimum diameter of 24 inches and remove the base course material to the depth shown. Compact the bottom of the cored hole before pouring concrete.

Use a setting jig to install the bottom section of the light base assembly, as shown in the Plans. The bottom of the light base shall be at least 6 inches above the bottom of the excavation. Provide no more than 4 threaded hubs for the bottom section of the light base, as shown on the Plans. Connect the bottom section of the light bases to the rigid steel conduit system, using rubber grommets or waterproof nipples and couplings. Usually one waterproof sealtite flexible coupling will suffice for each two-hubbed light base.

Call for inspection of the light base assembly prior to the backfilling of the excavations. Backfill with poured PCC meeting the requirements of Item P-610. Fill the excavation only to the level shown. Allow a 3 inch thickness of asphalt pavement over the PCC and over the light base mudplate.

After the PCC has cured at least 72 hours, apply tack coat and overlay with Asphalt Concrete Pavement.

Plug the conduit ends during the course of construction to prevent accumulation of water or debris in the conduit.

When ready to install the inset lights, determine the location of the light base and drill a small diameter core hole to locate the center of the mud plate. Next, drill a 16 inch diameter core hole over the center of the mud plate (± 1/4 inch). Use a coring machine of adequate stability to prevent "wobble". After removing the core, mud plate, plywood cover, and any water or debris that has accumulated, apply a thin layer of self-leveling silicone sealer between the bottom flange of the top section and the top flange of the bottom section and bolt the top section using 18-8, 410, or 416 stainless steel all-thread bolts. Coat the bolts with a suitable corrosion inhibitor prior to installing. Use two-piece cam-type lock washers and torque the bolts to 180 inch-pounds or as recommended by the manufacturer.

Make a "dry system" light fixture installation, using a grooved flange ring, "O" ring, and concrete ring. If the actual elevation of the pavement overlay does not equal the estimated elevation, provide spacer rings or flange rings of different thickness. Bolt the fixture to the top section using 18-8, 410, or 416 stainless steel bolts. Coat the bolts with a suitable corrosion inhibitor prior to installing. Use two piece cam-type lock washers, and torque the bolts to 180 inch-pounds, or as recommended by the manufacturer. Set the outboard edge of the fixture 1/4 to 3/8 inch below the adjacent finished pavement.

Install the light fixtures per the Plans and the specifications and the manufacturers recommended procedure. Do not deviate from these procedures, or the materials shown or specified, without the prior approval of the Engineer.

100-3.4 Installation of WATERTIGHT EDGE LIGHTS. Test the base assemblies, saddle fittings, and plastic duct as a complete system or in sections to insure that it is watertight. If a pneumatic test is performed to meet this requirement, the minimum pressure shall be 10 psi for a minimum of 10 minutes.

Base assemblies shall be sealed watertight and conduit openings and any holes shall be caulked with duct seal to prevent any water from entering the base assemblies. After the connection of the isolating transformer with L-823 connector kits the light bases shall be completely filled with free flowing insulating material.

The light base assemblies shall be sealed watertight using the following method and materials or approved equal:

- Spot weld the weep hole in the bottom of the base plate hub, if present.

- To insure that no water leaks into the can, use a soft neoprene gasket under the base plate. The gasket shall be covered on both sides with a generous coating of lubricant and sealant to prevent water seepage during freeze-thaw cycles.

- Install seal washers with stainless steel cups under the bolt heads. The torque on the six bolts should be approximately 25 plus or minus 5 inch-pounds. A torque wrench must be used.

- After installation of the base plate, plug in the edge light. Using clear adhesive sealant, coat the threads of the frangible coupling and screw into place. Plug the weep hole with adhesive sealant. Put adhesive sealant around the bottom of the frangible coupling at the junction with the base plate.

- Install the edge light stem securely. Then, using more adhesive sealant, fill the space between the edge light stem and the inside diameter of the frangible coupling. Install the light fixtures with lamp, clean the lenses, align and adjust each optical system in accordance with the manufacturer's instructions.

100-3.5 INSPECTION. Notify the Engineer in writing and request inspection at least 48 hours prior to installing lighting fixtures, making any splices, or covering any buried or concealed work. Immediately correct any deficiencies found during the inspection.

100-3.6 RECORD DOCUMENTS. Maintain at the project site a complete set of contract Plans, specifications and approved changes thereto. In addition to the above, 2 complete sets of electrical plans shall be maintained for as-built purposes upon which all changes, connections, part numbers and conductor routings shall be legibly shown and noted. Where changes to Plans are involved, make notations to show the dates and authorities approving the changes. Permanently store one set of annotated electrical plans in a dry, secure location at the project site. Deliver the second set to the Engineer.

As-built plans shall show locations of all buried items such as conduit, including any existing active lines encountered. All dimensions shall be from runway and taxiway centerlines or other permanent objects. As-built plans shall include complete wiring diagrams, (both power and control), identifying terminals, cables, and connections. As-built plans shall be kept current as the work progresses.

100-3.7 GUARANTEE. Furnish a written guarantee that any materials or workmanship found defective within one year of final acceptance shall be replaced at no additional cost to the Department, promptly upon notification and to the satisfaction of the Engineer.

100-4.1 METHOD OF MEASUREMENT.

- Lump Sum. No measurement of quantities will be made.

- Unit Prices. The quantity to be paid for will be the number of units installed, complete, in place, accepted, and ready for operation, or the number of units acceptably removed.

100-5.1 BASIS OF PAYMENT. At the contract lump sum or unit prices for the completed and accepted job.

All work and materials required to install cable, conduit, and ground rods is paid for under Items L-108, and L-110.

All work and materials required to install remote relay assembly and remote control panel are paid for under item L-109.

Payment will be made under:

Item L-100a	Airport Lighting - per lump sum

Includes all work required under this item to provide the complete airport lighting system, except work listed above which is paid for under other items.

Item L-100b	Regulator, L-828 - per each

Includes mounting, electrical connection (with all input control and output circuits), painting and stenciling. Size as indicated on Plans.

Item L-100c	High Intensity Runway Edge and Threshold Light, L-862 and L-862E - per each

Includes L-868 base assembly, gasket, frangible coupling, L-830-6, 200 W isolating transformer, and L-823 cable connectors.

Item L-100d	Medium Intensity Runway Edge and Threshold Light, L-861 and L-861E - per each

Includes L-867 base assembly, grounding lug and connector, cover, gasket, support column, frangible coupling, 30/45 W L-830-1 isolating transformer, transformer mounting platform (when shown on Plans), and L-823 cable connectors.

Item L-100e	Taxiway Edge Light, L-861T - per each

Includes L-867 base assembly, grounding lug and connector, cover, gasket, support column, frangible coupling, 30/45 W L-830-1 isolating transformer, transformer mounting platform (when shown on Plans), and L-823 cable connectors.

Item L-100f	Wind Cone Handhole, L-867, Size D - per each

Includes steel cover and gasket, grounding lug and connector, L-823 primary and secondary cable connectors, and PA-4 power adapter (when specified on the Plans).

Item L-100g	Primary Handhole, L-868, Size B – per each

Includes traffic rated steel cover and gasket, grounding lug and connector.

Item L-100h	Remove existing Runway and Taxiway Light - per each

Includes removal of fixtures, transformers, and bases.

Item L-100i	Flush Runway Centerline Light, L-850A or L-850B - per each

Includes L-868 base assembly, spacer rings, flange ring, steel cover, concrete work, asphalt patching and sealing.

Item L-100j	Flush Taxiway Centerline Light, L-852A or L-852G - per each

Includes L-868 base assembly, spacer rings, flange ring, L-830 isolating transformer, L-823 Cable connectors, concrete work, asphalt patching and sealing.

Item L-100k	Flush Runway Edge Light, L-850C - per each

Includes L-868 base assembly, spacer rings, flange ring, L-830 isolating transformer, L-823 Cable connectors, concrete work, asphalt patching and sealing.

Item L-100l	Relocate Existing Airport Sign, Type L-858 - per each

Includes L-867 base, frangible couplings, transformer, concrete base, and sign faces as shown.

Item L-100m	Runway Guard Light, L-804 - per each

Includes L-867 base assembly.

Item L-100n	Airport Sign, Type L-858 - per each

Includes sign, L-867 base, frangible couplings, transformer, concrete base, sign faces as shown.

MATERIAL REQUIREMENTS

AC 150/5345-10 	Constant Current Regulators and Regulator Monitors

AC 150/5345-42	Airport Light Bases, Transformer Houses, Junction Boxes and Accessories

AC 150/5345-44	Taxiway and Runway Signs

AC 150/5345-46	Runway and Taxiway Light Fixtures

AC 150/5345-47	Isolation Transformers for Airport Lighting Systems

AC 150/5345-49	L-854, Radio Control Equipment

AC 150/5345-53	Airport Lighting Equipment Certification Program

ASTM D 1557	Moisture-Density Relations of Soils and Soil-Aggregate Mixtures Using 10-lb. Rammer and 18-in Drop

ITEM L-101	ROTATING BEACON

DESCRIPTION

101-1.1 This item shall consist of furnishing and installing airport rotating beacons. This work shall include the mounting, leveling, wiring, painting, servicing, and testing of the beacon and all materials and incidentals necessary to place the beacon in operating condition as a completed unit to the satisfaction of the Engineer. This item shall include a mounting platform if specified in the Plans.

EQUIPMENT AND MATERIALS

101-2.1 GENERAL.

- Airport lighting equipment and materials covered by FAA specifications shall be certified and listed under AC 150/5345-53, Airport Lighting Equipment Certification Program. This AC, the latest certified equipment list, and the address list of certified airport lighting equipment manufacturers are available on the Internet home page for the FAA Office of the Associate Administrator for Airports (ARP). The direct Internet address is <www.faa.gov/arp/arphome.htm>.

- All other equipment and materials covered by other referenced specifications shall be subject to acceptance through manufacturer's certification of compliance with the applicable specification when requested by the Engineer.

101-2.2 BEACON. The beacon shall meet the requirements of AC 150/5345-12, Specification for Airport and Heliport Beacons. The beacon shall be a L-801A or L-802A, Class II, with metal-halide lamp(s).

- The beacon shall be supplied with an arctic kit to provide supplemental heating to the beacon mechanisms and bearings for operations in extreme weather. If the manufacturer does not offer an optional arctic kit, the beacon shall be modified as outlined in this paragraph. The beacon shall, at a minimum, be equipped with a 150 W strip heater installed to keep the motor and beacon housing warm during extreme cold weather conditions. An air-sensing thermostat shall be supplied with contacts rated for 16 A, 120 V. The thermostat shall be constructed so that contacts close on descending temperatures adjustable between 0 °F and 30 °F, +/- 4 °F. The contacts shall open on rising temperatures at 15 °F above closing temperature.

- The internal heater and internal thermostatic control kit shall be field wired separate from the beacon lights and motor (see beacon wiring diagram on the Plans).

- The beacon contactor shall be 2-pole, 30 A, with an operating coil designed for 120 V, 60 Hz., and shall be mounted in the control panel with its operating coil circuit connected through an on-off-auto switch as shown on the Plans.

101-2.3 PANEL BOARDS AND BREAKERS. Panel boards and breakers shall conform to the requirements of Fed. Spec. W-P-115.

101-2.4 WEATHERPROOF CABINETS. The weatherproof cabinets shall conform to NEMA Standards and shall be constructed of steel not less than No. 16 USS gauge.

101-2.5 WIRE. Wire in conduit rated up to 5,000 V shall conform to AC 150/5345-7, Specification for L-824 Underground Electrical Cable for Airport Lighting Circuits, for Rubber Insulated Neoprene Covered Wire, or Fed. Spec. J-C-30, Type RHW, for rubber insulated fibrous covered wire. For ratings up to 600 V, the thermoplastic wire conforming to Fed. Spec. J-C-30, Types TW, THW, and THWN, shall be used. The wires shall be of the type, size, number of conductors, and voltage shown in the Plans or in the specifications.

101-2.6 CONDUIT. Rigid steel conduit and fittings shall conform to the requirements of UL Standard 6, 514, and 1242.

101-2.7 PAINT.

- Priming paint for ungalvanized metal surfaces shall be a high solids alkyd primer conforming to Fed. Spec. TT-P-664D.

- Priming paint for galvanized metal surfaces shall be zinc dust-zinc oxide primer paint conforming to MIL-P-24441/19B. If necessary, add not more than 1/2 pint of turpentine to each gallon of paint.

- Orange paint for the body and the finish coats on metal and wood surfaces shall consist of a ready-mixed non-fading paint meeting the requirements of Fed. Spec. TT-E-489. The color shall be in accordance with Federal Standard 595, Aviation Gloss Orange, Number 12197.

- White paint for body and finish coats on metal and wood surfaces shall be ready-mixed paint conforming to Commercial Item Description A-A-3067.

- Priming paint for wood surfaces shall be mixed on the job by thinning the above specified orange or white paint with 1/2 pint of raw linseed oil to each gallon.

CONSTRUCTION METHODS

101-3.1 PLACING THE BEACON. The beacon shall be mounted on a beacon tower, platform, or building roof as shown in the Plans.

101-3.2 HOISTING AND MOUNTING. The beacon shall be hoisted to the mounting platform by using suitable slings and hoisting tackle. Before fastening the beacon to the mounting platform, the mounting holes shall be checked for correct spacing. Beacon base or mounting legs shall not be strained or forced out of position to fit incorrect spacing of mounting holes. The beacon base shall be raised first, set in position, and bolted in place. The beacon shall then be raised and assembled to the base.

101-3.3 LEVELING. After the beacon has been mounted in place, it shall be accurately leveled. The leveling shall be checked in the presence of the Engineer and shall be to the Engineer's satisfaction.

101-3.4 SERVICING. Before placing the beacon in operation, the Contractor shall accomplish the following:

- Clean and polish all glassware, both inside and outside, using a type of cleaner which will not scratch the lens, and clean the interior of the beacon.

- Clean interior of beacon base and check for alignment of parts.

- Clean and lubricate all mechanical system in accordance with manufacturer’s recommendations. Assure that all subassemblies are properly aligned and working properly.

- Secure lamps properly in the sockets.

101-3.5 BEAM ADJUSTMENT. After the beacon has been mounted and leveled, the vertical angle of the beams shall be adjusted. The final beam adjustments shall be made at night so that results can be readily observed. The beams shall be adjusted to the vertical angle directed by the Engineer or as shown in the Plans, except that, in no case shall the vertical angle of the beams be less than 2( above the horizontal.

101-3.6 BEACON MOUNTING PLATFORM. Where the beacon is to be mounted at a location other than a beacon tower and where a special mounting platform is required, the construction of this mounting platform and any necessary lightning protection equipment shall be in accordance with the details shown in the Plans.

101-3.7 WIRING. The Contractor shall furnish all necessary labor and materials and shall make complete above ground electrical connections in accordance with the wiring diagram furnished with the project Plans.

If underground cable for the power feed from the transformer vault to the beacon site and duct for this cable installation under paved areas is required, the cable and duct shall be installed in accordance with L-108, Underground Cable, and Item L-110, Underground Electrical Duct. No separate measurement or payment will be made for underground wire or conduit.

If obstruction lighting is specified, the Contractor shall connect the tell-tale relay mechanism in the beacon to energize the tower obstruction light circuit when failure of the beacon service (primary) lamp occurs.

If lightning protection is specified in the Plans or specifications as a part of this item, it shall be in accordance with 103-2.3, 2.4, 2.5, 2.6, and 3.4 in Item L-103, Beacon Tower.

101-3.8 PANEL AND CABINET. Unless otherwise specified, the Contractor shall furnish and install, at the top of the beacon tower or mounting platform, a circuit-breaker panel consisting of four 15-ampere breakers mounted in a weather-proof cabinet to provide separate protection for the circuits to the beacon lamps, motor, obstruction lights, and other equipment. The cabinet shall be located on the side of the beacon platform, as directed by the Engineer.

101-3.9 CONDUIT. All exposed wiring shall be run in not less than 1/2 inch galvanized rigid steel conduit. No conduit shall be installed on top of a beacon platform floor. All conduit shall be installed to provide for drainage. If mounted on a steel beacon tower, the conduit shall be fastened to the tower members with "wraplock" straps, clamps, or approved fasteners, spaced approximately 5 feet apart. The conduit shall be fastened to wooden structures with galvanized pipe straps and with galvanized wood screws not less than No. 8 nor less than 1-1/4 inches long. There shall be at least two fastenings for each 10-foot length.

101-3.10 BOOSTER TRANSFORMER. If shown in the Plans or specified in job specifications, a booster transformer to compensate for voltage drop to the beacon shall be installed in a suitable weatherproof housing under or on the tower platform or at the base of the tower. The installation shall be as indicated in the Plans and described in the specifications. If the booster transformer is required for installation in the transformer vault, it shall be installed in accordance with L-109, Transformer Vault and Vault Equipment. No separate measurement or payment will be made for the booster transformer.

101-3.11 PHOTOELECTRIC CONTROL. If shown in the Plans or specified in job specifications, the Contractor shall furnish and install an automatic control switch at the location indicated in the Plans. The switch shall be a photoelectric type. It shall be a standard commercially available unit suitable for aviation service. It shall be installed, connected, and adjusted in accordance with the manufacturer's instructions.

101-3.12 OBSTRUCTION LIGHTS. Unless otherwise specified, the Contractor shall install on the top of the beacon tower two L-810 obstruction lights on opposite corners. These lights shall be mounted on conduit extensions to a height of not less than 4 inches above the top of the beacon. They shall be connected in series into the tell-tale circuit with the necessary relay and wiring connections.

101-3.13 PAINTING. If construction of a wooden mounting platform is stipulated in the specifications as part of this item, all wooden parts of the platform shall be given one priming coat of white or aviation-orange paint after fabrication but before erection and one body and one finish coat of aviation-orange paint after erection. Steel mounting platforms shall be given one priming coat of corrosion-inhibiting primer before erection and one body and one finish coat of aviation-orange paint after erection. All equipment installed under this contract and exposed to the weather shall be given one body and one finish coat of aviation-orange or white paint as required. This shall include beacon (except glass surfaces), beacon base, breaker cabinet, all conduit, and transformer cases. It shall not include lightning rods or obstruction light globes.

The paint shall be applied uniformly in the proper consistency by skilled painters. The finished paint shall be free from sags, holidays, and smears. Each coat of paint shall be given ample time to dry and harden before the next coat of paint is applied. A minimum of 3 days shall be allowed for drying on wood surfaces, and a minimum of 4 days shall be allowed for drying on metal surfaces. Painting shall not be done in cold, damp, foggy, dusty, or frosty atmospheres, or when air temperature is below 40 °F, nor started when the weather forecast indicates such conditions for the day.

All surfaces shall be cleaned before painting. The surfaces shall be dry and free from scale, grease, rust, dust, and dirt when paint is applied. All knots in wood surfaces shall be covered with shellac immediately before applying the priming coat of paint. Nail holes and permissible imperfections shall be filled with putty.

The ready-mixed paint shall be thinned for the priming and body coats in accordance with the manufacturer's recommendations. In the absence of such recommendations, the following shall apply:

- Body coats (for both wood and steel surfaces) - add 1/2 pint of turpentine to each gallon of ready-mixed paint for body coats.

- Finish coats (for both wood and steel surfaces) - the ready-mixed paint shall be used as it comes from the container for finish coats.

101-3.14 TESTING. The installation shall be fully tested in operation as a completed unit prior to acceptance. These tests shall include operation of the lamp-changer and taking megger and voltage readings. The insulation resistance to ground of the beacon supply circuit shall be not less than 50 megohms when measured ungrounded. Testing equipment shall be furnished by the Contractor. Tests shall be conducted in the presence of the Engineer and shall be to his/her satisfaction.

METHOD OF MEASUREMENT

101-4.1 The quantity to be paid for shall be the number of beacons installed as completed units in place, accepted, and ready for operation.

BASIS OF PAYMENT

101-5.1 Payment will be made at the contract unit price for each completed and accepted job.

Payment will be made under:

Item L-101a	Rotating Beacon, High Intensity, L-801A - per each

Item L-101b	Rotating Beacon, Medium Intensity, L-802A - per each

MATERIAL REQUIREMENTS

AC 150/5345-7	L-824 Underground Cable for Airport Lighting Circuits

AC 150/5345-12	Airport and Heliport Beacons

Commercial Item

Description A-A-3067	Paint: Alkyd, Exterior, Low VOC

Fed.Spec. J-C-30	Cable and Wire, Electrical (Power, Fixed Installation)

Fed. Spec. TT-E-489	Enamel, Alkyd, Gloss, Low VOC Content

Fed. Spec. TT-P-664D	Primer Coating, Alkyd, Corrosion-Inhibiting, Lead and Chromate Free, VOC-Compliant

Fed.Spec. W-P-115	Panel, Power Distribution

Fed. Std. 595	Colors

MIL-P-24441/19B	Paint, Epoxy-Polyamide, Zinc Primer, Formula 159, Type III

UL Standard 6	Rigid Metal Conduit

UL Standard 514	Fittings for Conduit and Outlet Boxes

UL Standard 1242	Intermediate Metal Conduit

ITEM L-103	BEACON TOWER

DESCRIPTION

103-1.1 This item shall consist of furnishing and installing an airport beacon tower of the type shown in the Plans, in accordance with these specifications. This work shall include the clearing of the site, erection of the tower, installation of lightning protection (when specified), painting, and all incidentals necessary to place it in operating condition as a completed unit to the satisfaction of the Engineer.

EQUIPMENT AND MATERIALS

103-2.1 GENERAL. All equipment and materials covered by referenced specifications shall be subject to acceptance through manufacturer's certification of compliance with the applicable specification when requested by the Engineer.

103-2.2 TOWER. The beacon tower shall be either of the following:

- Fixed Tubular Steel Tower. The beacon tower shall conform to the requirements of AC 150/5340-21, Airport Miscellaneous Lighting Visual Aids, Section 3.

- Hinged Pole Tower. The beacon tower shall be a hinged steel pole with guide wires as shown on the Plans. The pole shall be of the length shown on the Plans and have a winch or other approved mechanism to lower the top of the beacon pole to ground level.

103-2.3 LIGHTING ROD. The lightning rod shall consist of a galvanized steel, copper, or copper-clad rod with the upper end drawn to a point and of sufficient length to extend from the point of fastening to not less than 6 inches above the top of the beacon.

103-2.4 DOWN CONDUCTOR. The down conductor cable for lightning protection shall consist of No. 8 AWG or larger bare stranded copper wire.

103-2.5 GROUND ROD. The ground rod shall be of the diameter and length specified in the Plans. It shall be copper or copper clad.

103-2.6 GROUND CLAMP. Ground clamp shall be similar and equal to the Type GR as manufactured by FCI.

103-2.7 PAINT.

- Priming paint for galvanized steel towers shall be zinc dust-zinc oxide primer paint conforming to MIL-P-24441/19B. If necessary, add not more than 1/2 pint of turpentine to each gallon of paint.

- Priming paint for ungalvanized steel towers shall be a high solids alkyd primer conforming to Fed. Spec. TT-P-664D.

- Orange paint for the body and finished coats on metal and wood surfaces shall consist of a ready-mixed nonfading paint meeting the requirements of Fed. Spec. TT-E-489. The color shall be in accordance with Federal Standard 595, Aviation Gloss Orange, Number 12197.

- White paint for steel tower shall be ready-mixed paint conforming to Commercial Item Description A-A-3067.

CONSTRUCTION METHODS

103-3.1 CLEARING AND GRADING. The site on which the beacon tower is to be erected shall be cleared and leveled. All trees and brush shall be removed from the area within a distance of 25 feet from the tower or as called for in the Plans. Stumps shall be removed to a depth of 1-1/2 feet below finished grade and the excavation filled with earth and tamped. If a transformer vault or other structure is included as part of the installation, the area shall be cleared to a distance of 25 feet from these structures. The ground near the tower shall be leveled to permit the operation of mowing machines. The leveling shall extend at least 2 feet outside the tower legs. All debris removed from the tower site shall be disposed of by the Contractor to the satisfaction of the Engineer and in accordance with Federal, state, or local regulations.

103-3.2 EXCAVATION AND FILL. Excavation for the tower footings or base shall be carried to a minimum of 4 inches below the footing depth. The excess excavation below the footing depth shall then be backfilled with gravel or crushed stone meeting the requirements of either P-154, P-208, or P-209 and compacted to the required level. The footing plates shall be installed, and a thickness of not less than 18 inches of the same gravel or crushed stone shall be placed immediately above the footing plates in layers of not over 6 inches. Each layer above the footing plates shall be thoroughly tamped in place. The remainder of the backfill may be of excavated earth placed in layers not to exceed 6 inches. Each layer shall be thoroughly compacted by tamping.

Where solid rock is encountered, which prevents the carrying of the foundation legs to the required depth but which is of sufficient strength to use holddown bolts, the tower anchor posts shall be cut off at the required length and the holddown bolts shall be installed as indicated in the Plans with the approval of the Engineer. Each tower leg shall be anchored to the rock by means of two 7/8 inch diameter by 3 foot long expansion or split bolts and shall be grouted with neat portland cement into holes drilled into the natural rock. Except as required for rock foundations, the footing members shall not be cut off or shortened. If excavated material is of such character that it will not readily compact when backfilled, the Engineer may order the excavation backfilled with concrete or other suitable material.

The concrete footing for fixed towers shall be installed in accordance with the manufacturer's recommendations. Portions of the footing in the topsoil layer shall not be included in the footing height.

Concrete foundation for hinged pole shall be as shown on the Plans. Concrete shall meet the requirements of P-610, Structural Portland Cement Concrete.

103-3.3 ERECTION. Detail erection drawings furnished by the manufacturer shall be strictly followed during construction.

Fixed towers shall be erected in sections from the ground up unless otherwise specified. In final assembly, all bolts and fastenings shall be installed, and the structure shall be plumb, true, square, and level. Nuts shall be taken up to a firm bearing after which the bolts shall, if necessary, be cut to proper length to protrude three full threads. Approved locknuts shall be placed on each bolt over the regular nut. Ladder bolts shall be inserted with the head to the outer face of the tower. Diagonal, leg, and handrail bolts shall be installed with nuts on the outer face of the tower, unless otherwise specified. Bent parts shall be straightened before erection without damage to the protective coating. Surfaces abraded or bared of protective coating shall be painted with the proper priming paint as specified in these specifications.

The Contractor shall install the ladder on the side of the tower adjacent to the driveway or most accessible approach to the tower. Tubular beacon towers shall be erected in accordance with the manufacturer's recommendations. The safety cable shall be located on the side of the tower adjacent to the driveway or most accessible approach to the tower.

103-3.4 LIGHTNING PROTECTION. The Contractor shall furnish and install a lightning rod, down conductor, and at least one ground plate or rod for each beacon tower. The lightning rod shall be installed at the top of the tower with the tip of the rod extending not less than 6 inches above the top of the beacon.

Down-conductor cables shall be securely fastened to the surface of the tower leg at 5-foot intervals with suitable bronze fasteners having bronze or noncorrosive metal bolts. Sharp turns or bends in the down conductor will not be permitted.

All connections of cable to cable, cable to lightning rods, and cable to ground plates or rods shall be made with approved type solderless connectors or noncorrosive metal and shall be of substantial construction.

The down-conductor cable shall be securely attached to ground rods or plates placed at least 2 feet away from the tower foundations. The ground rod shall be driven into the ground so that the top is at least 0.5 foot below grade. The down-conductor shall be firmly attached to the ground plate or rod by means of a ground connector or clamp. Plates shall be embedded in the area of permanent moisture.

The complete lightning protection installation shall be accomplished to the satisfaction of the Engineer. The resistance to ground of any part of the lightning protection system shall not exceed 25 ohms.

103-3.5 PAINTING. The Contractor shall furnish all materials and labor for painting the beacon tower. The color scheme for the steel tower shall be as shown in the Plans.

- Parts to be Painted. Tower parts (except those parts to be exposed to earth) shall not be treated or primed before erection. All tower parts placed below ground level or within 12 inches above ground level shall be given two coats of approved bituminous paint.

The paint shall be applied uniformly in the proper consistency by skilled painters. The finished paint shall be free from sags, holidays, and smears. Division lines between colors shall be sharply defined. Each coat of paint shall be given ample time to dry and harden before the next coat is applied. A minimum of 4 days shall be allowed for drying on metal surfaces. Painting shall not be done in cold, damp, foggy, dusty, or frosty atmospheres, or when air temperature is below 40 °F, nor started when the weather forecast indicates such conditions for the day.

All surfaces shall be cleaned before painting. The surfaces shall be dry and free from scale, grease, rust, dust, and dirt when paint is applied.

The number of coats of paint applied shall be in accordance with the following instructions:

- Steel Towers, Galvanized. One priming coat of zinc dust-zinc oxide primer after erection and one body and one finish of white or orange paint (as required by the color scheme) applied after erection.

- Steel Towers, Not Galvanized. One priming coat of corrosion-inhibiting primer and one body and one finish coat of white or orange paint (as required by the color scheme) applied after erection.

The above specified orange and white ready-mixed paints shall be thinned for the body coats in accordance with the manufacturer's recommendations. In the absence of such recommendations, the following shall apply:

- Body Coats. Add not more than 1/2 pint of turpentine to each gallon of ready-mixed paint.

- Finish Coats. The ready-mixed paint shall be used as it comes from the container.

METHOD OF MEASUREMENT

103-4.1 The quantity to be paid for under this item will be the number of airport beacon towers installed as completed units, in place and accepted.

BASIS OF PAYMENT

103-5.1 Payment will be made at the contract unit price for each completed and accepted job.

Payment will be made under:

Item L-103a	Beacon Tower - per each

MATERIAL REQUIREMENTS

AC 150/5340-21	Airport Miscellaneous Lighting Visual Aids

Commercial Item

Description A-A-3067	Paint, Alkyd, Exterior, Low VOC

Fed. Spec. TT-E-489	Enamel, Alkyd, Gloss, Low VOC Content

Fed. Spec. TT-P-664D	Primer Coating, Alkyd, Corrosion-Inhibiting, Lead and Chromate Free, VOC-Compliant

Fed. Std. 595	Colors

MIL-P-24441/19B	Paint, Epoxy-Polyamide, Zinc Primer, Formula 159, Type III

ITEM L-107	WIND CONE

DESCRIPTION

107-1.1 This item shall consist of furnishing and installing lighted and unlighted airport wind cones in accordance with these specifications and in accordance with the dimensions, design, and details shown in the Plans.

For lighted wind cones, the work shall include the furnishing and installation of a support for mounting the wind cone, the furnishing and installing of the specified wire from the wind cone to the electrical control panel, and a concrete foundation. The item shall also include all cable connections, the furnishing and installing of the conduit and conduit fittings from the wind cone base to the first hand hole, the furnishing and installation of all lamps, ground rod and ground connection, the testing of the installation, and all incidentals necessary to place the wind cone in operation as a completed unit to the satisfaction of the Engineer.

For unlighted wind cones, the work shall include the furnishing and installation of a support for mounting the wind cone and a concrete foundation.

EQUIPMENT AND MATERIALS

107-2.1 GENERAL.

- Airport lighting equipment and materials covered by FAA specifications shall be certified and listed under AC 150/5345-53, Airport Lighting Equipment Certification Program. This AC, the latest certified equipment list, and the address list of certified airport lighting equipment manufacturers are available on the Internet home page for the FAA Office of the Associate Administrator for Airports (ARP). The direct Internet address is <www.faa.gov/arp/arphome.htm>.

- All other equipment and materials covered by other referenced specifications shall be subject to acceptance through manufacturer’s certification of compliance with the applicable specification when requested by the Engineer.

107-2.2 WIND CONES. The 8-foot and 12-foot wind cones and assemblies shall conform to the requirements of AC 150/5345-27, Specification for Wind Cone Assemblies. The pole shall be a steel pole hinged in the middle.

- Type L-807, Style I, Size 1, externally lighted wind cone.

- Type L-807, Style I, Size 2, externally lighted wind cone.

- Type L-807, Style II, Size 1, unlighted wind cone.

- Type L-807, Style II, Size 2, unlighted wind cone.

107-2.3 WIRE. Wire in conduit rated up to 5,000 V shall conform to AC 150/5345-7, Specification for L-824 Underground Cable for Airport Lighting Circuits, Type C cross-linked polyethylene insulated wire. For ratings up to 600 V, cross-linked polyethylene insulated wire type XHHW, shall be used. The wires shall be of the type, size, number of conductors, and voltage shown in the Plans.

107-2.4 CONDUIT. Rigid steel conduit and fittings shall conform to the requirements of UL Standard 6, 514, and 1242.

107-2.5 CONCRETE. The concrete for foundations shall be proportioned, placed, and cured in accordance with Item P-610, Structural Portland Cement Concrete.

107-2.6 PAINT.

- Primer for ungalvanized metal surfaces shall be a high solids alkyd primer conforming to Federal Specification TT-P-664D.

- Primer for galvanized metal surfaces shall be zinc dust-zinc oxide primer paint conforming to MIL-P-24441/19B. If necessary, thin with not more than 1/2 pint of turpentine per gallon of primer.

- Orange paint for the body and the finish coats on metal surfaces shall consist of a ready-mixed nonfading paint meeting the requirements of Fed. Spec. TT-E-489. The color shall be in accordance with Federal Standard 595, Aviation Gloss Orange, Number 12197.

107-2.7 WIND CONE. The wind cone fabric shall be standard international orange.

CONSTRUCTION METHODS

107-3.1 INSTALLATION. The hinged pole shall be installed on the concrete foundation as shown in the Plans.

- Notify the Engineer at least 24 hours prior to placement of concrete. Allow concrete bases to cure for 7 days after pouring before installing the hinged pole

- Backfill. Material used as backfill around the footing of the lighted wind cone shall be gravel or sand consisting of crushed or naturally occurring granular material. All materials shall be free of frozen lumps and clay particles.

107-3.2 COUNTERWEIGHT. The Contractor shall furnish and install a counterweight on the hinged support for the 12-foot wind cone. The counterweight may consist of lead weights which may be furnished with the “A” frame assembly or it may consist of concrete poured around the bottom of the hinged support. Where concrete is used, the counterweight shall be approximately 12 inches wide by 2 feet deep and should weigh approximately 500 pounds. The counterweight shall be 25 to 50 pounds less than the weight needed to balance the assembly. The counterbalancing must operate to the satisfaction of the Engineer.

107-3.3 ELECTRICAL CONNECTION. The Contractor shall furnish all labor and materials and shall make complete electrical connections in accordance with the wiring diagram furnished with the Plans.

If underground cable from the transformer vault to the wind cone site and duct for this cable installation under paved areas is required, the cable and duct will be paid for as part of the wind cone pay item.

107-3.4 BOOSTER TRANSFORMER. If shown in the Plans or specified in the Special Provisions, a booster transformer to compensate for voltage drop to the lamps shall be installed in a suitable weatherproof housing. The booster transformer shall be installed as indicated in the Plans and described in the Special Provisions. If the booster transformer is required for installation in the transformer vault, it will be paid for as part of the wind cone pay item.

107-3.5 GROUND CONNECTION AND GROUND ROD. The Contractor shall furnish and install a ground rod, grounding cable, and ground clamps for grounding the “A” frame of the 12-foot assembly or pipe support of the 8-foot support near the base. The ground rod shall be of the diameter and length specified in the Plans and shall be copper or copper clad. The ground rod shall be driven into the ground adjacent to the concrete foundation so that the top is at least 0.5 foot below grade. The grounding cable shall consist of No. 8 AWG bare stranded copper wire or larger and shall be firmly attached to the ground rod by means of a ground connector or clamp. The other end of the grounding cable shall be securely attached to a leg of the “A” frame or to the base of the pipe support with noncorrosive metal and shall be of substantial construction. The resistance to ground shall not exceed 25 ohms.

107-3.6 PAINTING. Three coats of paint shall be applied (1 prime, 1 body, and 1 finish) to all exposed material installed under this item except the fabric cone, obstruction light globe, and lamp reflectors. The wind cone assembly, if painted on receipt, shall be given 1 finish coat of paint in lieu of the 3 coats specified above.

107-3.7 LAMPS. The Contractor shall furnish and install four 200-W, 115-V general lighting service lamps in the reflectors for the 12-foot cone or four 150-W, 115-V lamps for the 8-foot cone. A clear 100-W, 107-W, or 116-W, 115-V traffic signal lamp with a medium screw base, or a 100-W. A 69 W, L-810, 115 V, medium prefocus base lamp shall be furnished and installed in the obstruction light as required.

107-3.8 WINCH AND PADLOCK. The Contractor shall furnish and install a suitable locking ratchet winch for lowering and raising the hinged top section.

A padlock shall also be furnished by the Contractor on the 8-foot wind cone for securing the hinged top section to the fixed lower section. Three keys for the padlock shall be delivered to the Engineer.

107-3.9 TESTING. Furnish all necessary labor, equipment and appliances for testing all material and equipment as specified herein. No work will be accepted until all applicable tests have been performed. Tests shall not begin until the work has been approved by the Engineer. All tests shall be neatly tabulated on a reproducible "Test Sheet" which shall be signed and dated by the Contractor upon completion of the test. Test and demonstrate to the Engineer the following:

- That all lighting, power, and control circuits are continuous, and free from short circuits.

- That all circuits are free from unspecified grounds.

- That the resistance to ground of all non-ground 5000 V circuits is not less than 50 megohms. Where additions are made to existing circuits, only the new section shall be tested. The resistance to ground of 600 V capacity shall be 10 megohms for the insulation test.

- That all circuits are properly connected in accordance with applicable wiring diagrams.

- That all circuits are operable.

107-3.10 GUARANTEE. Furnish a written guarantee that any materials or workmanship found defective within 1 year of final acceptance shall be replaced at the Contractor's expense, promptly upon notification and to the satisfaction of the Engineer.

METHOD OF MEASUREMENT

107-4.1 The quantity to be paid for will be the number of wind cones installed as completed units in place, accepted, and ready for operation.

BASIS OF PAYMENT

107-5.1 Payment will be made at the contract unit price for each completed and accepted job.

Payment will be made under:

Item L-107a	8-foot Lighted Wind Cone, in place - per each

Item L-107b	12-foot Lighted Wind Cone, in place - per each

Item L-107c	8-foot Unlighted Wind Cone, in place - per each

Item L-107d	12-foot Unlighted Wind Cone, in place - per each

MATERIAL REQUIREMENTS

AC 150/5345-7	L-824 Underground Cable for Airport Lighting Circuits

AC 150/5345-27	Wind Cone Assemblies

ASTM A 615	Deformed and Plain Billet-Steel Bars for Concrete Reinforcement

Commercial Item

Description A-A-3067	Paint: Alkyd, Exterior, Low VOC

Fed. Spec. J-C-30	Cable and Wire, Electrical (Power, Fixed Installation)

Fed. Spec. TT-E-489	Enamel, Alkyd, Gloss, Low VOC Content

Fed. Spec. W-P-115	Panel, Power Distribution

Fed. Std. 595	Colors

MIL-P-24441/19B	Paint, Epoxy-Polyamide, Zinc Primer, Formula 159, Type III

UL Standard 6	Rigid Metal Conduit

UL Standard 514	Fittings For Conduit and Outlet Boxes

UL Standard 1242	Intermediate Metal Conduit

ITEM L-108	UNDERGROUND CABLE

DESCRIPTION

108-1.1 This item shall consist of furnishing and installing underground cable in accordance with these specifications at the locations shown in the Plans. This item shall include the excavation and backfill of the trench, where direct buried cable is specified, and the installation of cable, grounding and counterpoise wire in trench, duct or conduit. It shall include splicing, cable marking, and testing of the installation and all incidentals necessary to place the cable in operating condition as a completed unit to the satisfaction of the Engineer. This item shall not include the installation of the duct or conduit.

EQUIPMENT AND MATERIALS

108-2.1 GENERAL.

- Airport lighting equipment and materials covered by FAA specifications shall be certified and listed under AC 150/5345-53, Airport Lighting Equipment Certification Program. This AC, the latest certified equipment list, and the address list of certified airport lighting equipment manufacturers are available on the Internet home page for the FAA Office of the Associate Administrator for Airports (ARP). The direct Internet address is <www.faa.gov/arp/arphome.htm>.

- All other equipment and materials covered by other referenced specifications shall be subject to acceptance through manufacturer's certification of compliance with the applicable specification, when requested by the Engineer.

108-2.2 CABLE. Underground cable shall conform to the requirements of AC 150/5345-7, Specification for L-824 Underground Electrical Cable for Airport Lighting Circuits, and meet the following requirements.

5000 V cable shall be non-shielded, single conductor, FAA type C, with cross-linked polyethylene insulation or FAA type B, ICEA S-19-81 ozone-resistant butyl rubber insulated with overall jacket of heavy duty neoprene. Conductor shall be lead alloy coated, soft annealed stranded copper.

600 V cable shall be non–shielded, single conductor, with stranded annealed copper conductor, rated 190 °F, with cross-linked polyethylene insulation classified as UL type-2 and FAA type C.

Underground Electrical Cable shall be No. 14 AWG, copper, 600 V, Type SOOW-A/SOOW. Cable shall remain flexible down to -40 (F. The cable connectors shall be secondary connector kits for the plug and the receptacle meeting specification L-823.

If telephone control cable is specified, copper shielded, polyethylene insulated and jacketed, No. 19 AWG telephone cable conforming to ICEA-S-85-625, Standard, Aircore, Polyolefin, Copper Conductor Telecommunications Cable for direct burial, shall be used.

Where counterpoise conductors are to be installed and where soil conditions would adversely affect bare copper wire, cross-linked polyethylene wire conforming to Fed. Spec. J-C-30, Type XHHW, 600 volt, may be used.

Cable type, size, number of conductors, strand and service voltage will be specified in the Plans and/or specifications.

108-2.3 BARE COPPER WIRE (COUNTERPOISE OR GROUNDING). Bare copper wire for counterpoise or grounding installations shall be solid or stranded wire conforming to ASTM B 3 and B 8.

108-2.4 CABLE CONNECTIONS. In-line connections of underground primary cables shall be of the type called for in the Plans or in the specifications, and shall be one of the types listed below. When the Plans or the specifications permit a choice of connection, the Contractor shall indicate in the bid the type of connection he proposes to furnish.

- Cast Splice. A cast splice, employing a plastic or metal mold and using epoxy resin manufactured by Minnesota Mining and Manufacturing Company, "Scotchcast" Kit No. 82B, or approved equal, is to be used for potting the splice. This means of splicing is the only type approved for telephone control cable.

- Vulcanized Splice. A vulcanized splice with proper molds for various cable sizes shall be used.

- Field-attached Plug-in Splice. Figure 3 of AC 150/5345-26, Specification for L-823 Plug and Receptacle, Cable Connectors, employing connector kits, is approved for field attachment to single conductor cable. 600 V cord sets shall include a Type II, Class A, Style I plug on a 16/2 SJO cord. 600 V secondary receptacles shall be Type II, Class B, Style II. 600 V plugs shall be Type II, Class B, Style 4. 5000 V plugs shall be Type I, Class B, Style 3. 5000 V receptacles shall be Type I, Class B, Style 10.

- Factory-Molded Plug-in Splice. Specification for L-823 Connectors, Factory-Molded to Individual Conductors, are approved.

- Taped Splice. Taped splices employing field-applied rubber, or synthetic rubber tape covered with plastic tape are approved. The rubber tape should meet the requirements of ASTM D 4388 and the plastic tape should comply with Mil. Spec. MIL-I-24391 or Commercial Item Description A-A-55809. In all the above cases, connections of cable conductors shall be made using crimp connectors utilizing a crimping tool designed. To make a complete crimp before the tool can be removed. No. 19 AWG telephone control wires may be connected by means of wrapped and soldered splice, 3M Company Moisture Proof UR Type Connector, or approved equal, or by a method approved by the Engineer. Electrical insulating tape shall be "Scotch" No. 88 or approved equal.

108-2.5 CONCRETE. Concrete for cable markers shall conform to Specification Item P-610, "Structural Portland Cement Concrete."

108-2.6 MARKER TAPE. Marker tape shall be APWA-ULCC compliant, red polyethylene plastic, printed "Caution - Buried Electric Line Below".

108-2.7 INTERSTICE FILLER. When called for on the Plans underground conduit runs shall contain, in addition to the specified conductor(s), one or more runs of compressible interstice filler (as shown on the Plans). Compressible interstice filler shall be 5/8-inch closed cell backer rod (caulk backer).

CONSTRUCTION METHODS

108-3.1 GENERAL. The Contractor shall install the specified cable at the approximate locations indicated in the airport lighting layout plans. The Engineer will indicate specific locations.

Notify the Engineer in writing and request inspection at least 48 hours prior to installing cables, making any splices, or covering any buried or concealed work. Immediately correct any deficiencies found during the inspection. Install cable in a manner to prevent harmful stretching of the conductors, injury to the insulation, damage to tapes and fillers or damage to the outer protective jacket or covering.

Label the circuit conductors in each manhole or handhole by attaching a heat stamped nylon identification tag bearing the circuit designation "R" or "T", as required.

Cable connections between lights will be permitted only at the light locations for connecting the underground cable to the primary leads of the individual insulating transformers. The Contractor shall be responsible for providing cable in continuous lengths for home runs or other long cable runs without connections, unless otherwise authorized in writing by the Engineer or shown in the Plans.

108-3.2 INSTALLATION IN DUCT OR CONDUIT. This item includes the installation of the cable in duct or conduit as described below. The maximum number and voltage ratings of cables installed in each single duct or conduit, and the current-carrying capacity of each cable shall be in accordance with the latest NEC, or the code of the local agency having jurisdiction.

The Contractor shall make no connections or joints of any kind in cables installed in conduits or ducts. Provide and install cables in continuous lengths free of splices between the points of connection indicated on the Plans.

The duct or conduit shall be installed as a separate item in accordance with Item L-110, "Underground Electrical Duct." The Contractor shall make sure that the duct is open, continuous, and clear of debris before installing cable. The cable shall be installed in a manner to prevent harmful stretching of the conductor, injury to the insulation, or damage to the outer protective covering. The ends of all cables shall be sealed with moisture-seal tape before pulling into the conduit and it shall be left sealed until connections are made. Where more than one cable is to be installed in a duct under the same contract, all cable shall be pulled in the duct at the same time. The pulling of a cable through ducts or conduits may be accomplished by hand winch or power winch with the use of cable grips or pulling eyes. Pulling tensions should be governed by recommended standard practices for straight pulls or bends. A lubricant recommended for the type of cable being installed shall be used where pulling lubricant is required. Duct or conduit markers temporarily removed for excavations shall be replaced as required.

Compressible interstice filler (when shown on the Plans and as specified) shall be installed in place with the cable(s). It shall be taped as required to attach and secure it to the conductor(s) during installation.

Where runway and taxiway series lighting circuit conductors are to be installed together through the same conduit, identify the individual conductors at both ends of the duct by applying identification ties which have been heat stamped with the circuit identification "R", "T1" or "T2" as needed.

Assemble connections in the runway and taxiway series lighting cable at the light assemblies using approved L-823 connector kits. The male end shall be coated with silicone compound. Properly seat both plug and receptacle ends onto cable and check for proper connector pin positioning prior to taping. When completed, wrap the L-823 connection with 2 layers of electrical insulating tape, 1/2 lapped extending at least 1-1/2 inch on each side of the joint. Install heat shrinkable tubing with internal adhesive as shown on Plans. Leave sufficient slack in the cables at points of connection consistent with standard trade practices; and, in the case of the runway and taxiway series lighting cable, leave sufficient slack at each light assembly to permit the connection to be made 1 foot above grade.

108-3.3 TRENCHING. Where turf is well established and the sod can be removed, it shall be carefully stripped and properly stored. Trenches for cables may be excavated manually or with mechanical trenching equipment. Walls of trenches shall be essentially vertical so that a minimum of shoulder surface is disturbed. Road patrols or graders shall not be used to excavate the trench with their blades. The bottom surface of trenches shall be essentially smooth and free from coarse aggregate. Unless otherwise specified, cable trenches shall be excavated to a minimum depth of 1.5 feet below finished grade, except as follows:

- When off the airport or crossing under a roadway or driveway, the minimum depth shall be 3 feet unless otherwise specified.

- Minimum cable depth when crossing under a railroad track, shall be 3.5 feet unless otherwise specified.

The Contractor shall excavate all cable trenches to a width not less than 6 inches. The trench shall be widened where more than two cables are to be installed parallel in the same trench. Unless otherwise specified in the Plans, all cables in the same location and running in the same general direction shall be installed in the same trench.

When rock excavation is encountered, the rock shall be removed to a depth of at least 3 inches below the required cable depth and it shall be replaced with bedding material of earth or sand containing no mineral aggregate particles that would be retained on a 1/4 inch sieve. The Contractor shall ascertain the type of soil or rock to be excavated before bidding. All excavation shall be unclassified.

108-3.4 INSTALLATION IN TRENCHES. The Contractor shall not use a cable plow for installing the cable. Mechanical cable-laying equipment may be used in conjunction with a trenching machine if specified on project Plans and specifications; and it should provide for physical inspection of cable prior to backfilling. Sharp bends or kinks in the cable will not be permitted.

Cables shall be unreeled in place alongside or in the trench and shall be carefully placed along the bottom of the trench. Inspect cable as it is removed from the reel to determine that the cable is free of visible defects. Support reel so that is turns easily and without undue strain on the cable. The cable shall not be unreeled and pulled into the trench from one end.

Where two or more cables are laid parallel in the same trench, they shall be placed laterally a minimum distance of 3 inches apart, and the trench shall be widened sufficiently to accomplish this.

Cables crossing over each other shall have a minimum of 3 inch vertical displacement with the topmost cable depth at or below the minimum required depth below finished grade.

Not less than 12 inches of cable slack shall be left on each side of all connections, insulating transformers, light units, and at all other points where cable is connected to field equipment. The slack cable shall be placed in the trench in a series of S-curves. Additional slack cable shall be left in runway light bases, handholes, manholes, etc., where it is required to bring the cable above ground level to make connections. The amount of slack cable will be stipulated by the Engineer, or as shown in the Plans and specifications.

108-3.5 BACKFILLING. After the cable has been installed, the trench shall be backfilled. The initial layer of backfill material shall be 3 inches deep, loose measurement, and shall be either earth or sand containing no mineral aggregate particles that would be retained on a 1/4-inch sieve. This layer shall not be compacted. The second layer shall be 5 inches deep, loose measurement, and shall contain no particles that would be retained on a 1-inch sieve. The remainder of the backfill shall be excavated or imported mineral and shall not contain stone or aggregate larger than 4 inches maximum diameter. The third and subsequent layers of the backfill shall not exceed 8 inches in maximum depth, loose measurement.

The second, and subsequent layers shall be thoroughly tamped and compacted to at least the density of the adjacent undisturbed soil, and to the satisfaction of the Engineer. If necessary to obtain the desired compaction, the backfill material shall be moistened or aerated as required.

Trenches shall not be excessively wet and shall not contain pools of water during backfilling operations. The trench shall be completely backfilled and tamped level with the adjacent surface, except that when sod is to be placed over the trench, the backfilling shall be stopped at a depth equal to the thickness of the sod to be used, with proper allowance for settlement. Any excess excavated material shall be removed and disposed of in accordance with instructions issued by the Engineer.

108-3.6 RESTORATION. Where sod has been removed, it shall be replaced as soon as possible after the backfilling is completed. All areas disturbed by the trenching, storing of dirt, cable laying, pad construction, and other work shall be restored to its original condition. The restoration shall include any necessary topsoiling, fertilizing, liming, seeding, sodding, sprigging or mulching. All such work shall be performed in accordance with the FAA standard turfing specifications. The Contractor will be held responsible for maintaining all disturbed surfaces and replacements until final acceptance.

108-3.7 CABLE MARKERS. The location of runway light circuits shall be marked by a concrete slab marker, 2 feet square and 4 inches thick, extending approximately 1 inch above the surface. Each cable run from the line of runway lights to the equipment vault shall also be marked at approximately every 200 feet along the cable run, with an additional marker at each change of direction of cable run. All other cable buried directly in the earth shall be marked in the same manner. The Contractor shall not install slab markers where cable lies in straight lines between obstruction light poles which are spaced 300 feet apart, or less. Cable markers shall be installed immediately above the cable. The Contractor shall impress the word "CABLE" and directional arrows on each cable marking slab. The letters shall be approximately 4 inches high and 3 inches wide, with width of stroke 1/2 inch and 1/4 inch deep.

The location of each underground cable connection, except at lighting units or insulating transformers, shall be marked by a concrete marker slab placed above the connection. The Contractor shall impress the word "SPLICE" on each slab. He also shall impress additional circuit identification symbols on each slab if so desired by the Engineer.

108-3.8 SPLICING. Connections of the type shown in the Plans shall be made by experienced personnel regularly engaged in this type of work and shall be made as follows:

- Cast Splices. These shall be made by using crimp connectors for jointing conductors. Molds shall be assembled, and the compound shall be mixed and poured in accordance with manufacturer's instructions and to the satisfaction of the Engineer.

- Vulcanized Splices. These shall be made by using crimp connectors for joining conductors. The splice shall be made, using compounds furnished by the manufacturer, in accordance with his/her instructions and to the satisfaction of the Engineer.

- Field-attached Plug-in Splices. These shall be assembled in accordance with manufacturer's instructions. These splices shall be made by plugging directly into mating connectors. In all cases the joint where the connectors come together shall be wrapped with at least one layer of rubber or synthetic rubber tape and one layer of plastic tape, one-half lapped, extending at least 1-1/2 inches on each side of the joint.

- Factory-Molded Plug-in Splices. These shall be made by plugging directly into mating connectors. In all cases, the joint where the connectors come together shall be wrapped with at least one layer of rubber or synthetic rubber tape and one layer of plastic tape, one-half lapped, extending at least 1-1/2 inches on each side of the joint.

- Taped Splices. A taped splice shall be made in the following manner:

Bring the cables to their final position and cut so that the conductors will butt. Remove insulation and jacket allowing for bare conductor of proper length to fit compression sleeve connector with 1/4 inch of bare conductor on each side of the connector. Use a sharp knife to pencil insulation and jacket at approximately the same angle as a pencil point. Care must be taken to avoid nicking or injuring the conductor during removal of insulation or penciling. Do not use emery paper on splicing operation since it contains metallic particles. The copper conductors shall be thoroughly cleaned. Join the conductors by inserting them equidistant into the compression connection sleeve. Crimp conductors firmly in place with crimping tool that requires a complete crimp before tool can be removed. Test the crimped connection by pulling on the cable. Scrape the insulation to assure that the entire surface over which the tape will be applied (plus 3 inches on each end) is clean. After scraping wipe the entire area with a clean lint-free cloth. Do not use solvents.

Apply high-voltage rubber tape one-half lapped over bare conductor. This tape should be tensioned as recommended by the manufacturer. Voids in the connector area may be eliminated by highly elongating the tape stretching it just short of its breaking point. Throughout the rest of the splice less tension should be used. Always attempt to exactly half-lap to produce a uniform buildup. Continue buildup to 1-1/2 times cable diameter over the body of the splice with ends tapered a distance of approximately 1 inch over the original jacket. Cover rubber tape with two layers of vinyl pressure-sensitive tape one-half lapped. Do not use glyptol or lacquer over vinyl tape as they react as solvents to the tape. No further cable covering or splice boxes are required.

If shielded cable is to be spliced, prepare cable as for a regular taped splice, except that the neoprene jacket shall be removed a distance not less than 5 inches from the beginning of the penciled portion. Carefully unwrap the shielding tape from that portion where jacket has been removed and cut off so that it extends about 1 inch from end of the jacket. Proceed with the taped splice as described above and tape up to 1/4 inch from the shield on both ends. Build up rubber tape to a thickness equal to the insulation thickness or 5/16 inch over connector.

Next wrap one-half lapped layer of semi-conducting tape tape, conforming to ASTM D 4388, Type IV, over splicing tape and 1/4 inch onto the shielding tape. Wrap a fine, flat shielding braid one-half lapped over the splice extending 1/2 inch onto the metallic shielding. Solder ends of braid to metallic shielding tape. A bonding wire, (Minimum No. 14 Stranded Copper) equal to the current carrying capacity of the metallic shield, should have the individual strands wrapped around the metallic shield at both ends of the splice. These strands should be tack soldered to the shield in several places. The cable sheath should be replaced by wrapping with two one-half lapped layers of vinyl tape extending 2 inches onto the cable jacket.

The above described splice is for a straight-through splice with continuity of shielding.

108-3.9 BARE COUNTERPOISE WIRE INSTALLATION AND GROUNDING FOR LIGHTNING PROTECTION. If shown in the Plans or specified in job specifications, a stranded bare copper wire, No. 8 AWG minimum size, shall be installed for lightning protection of the underground cables. The bare counterpoise wire shall be installed in the same trench for the entire length of the insulated cables it is designed to protect, and shall be placed at a distance of approximately 4 inches from the insulated cable. The counterpoise wire shall be securely attached to each light fixture base, or mounting stake. The counterpoise wire shall also be securely attached to copper or copper-clad ground rods installed not more than 1,000 feet apart around the entire circuit. The ground rods shall be of the length and diameter specified in the Plans, but in no case shall they be less than 8 feet long nor less than 5/8 inch in diameter.

The counterpoise system shall terminate at the transformer vault or at the power source. It shall be securely attached to the vault or equipment grounding system. The connections shall be made as shown in the project Plans and specifications.

108-3.10 GROUNDING SYSTEM. If shown in the Plans or specified in specifications, a stranded bare copper wire, No. 8 AWG minimum size, shall be installed as grounding for the lighting system. The bare ground wire shall be installed in the same trench for the entire length of the insulated cables or conduit it is designed to protect, and shall be placed at a distance of approximately 4 inches from the insulated cable or conduit. The ground wire shall be securely attached to each light fixture base. The ground wire shall also be securely attached to copper or copper-clad ground rods installed not more than 1,000 feet apart around the entire circuit. The ground rods shall be of the length and diameter specified in the Plans, but in no case shall they be less than 8 feet long nor less than 5/8 inch in diameter.

The ground system shall terminate at the transformer vault or at the power source. It shall be securely attached to the vault or equipment grounding system. The connections shall be made as shown in the project Plans and specifications.

108-3.11 TESTING. The Contractor shall furnish all necessary equipment and appliances for testing the underground cable circuits after installation. The Contractor shall test and demonstrate to the satisfaction of the Engineer the following:

- That all lighting power and control circuits are continuous and free from short circuits.

- That all circuits are free from unspecified grounds.

- That the insulation resistance to ground of all nongrounded series circuits is not less than 50 megohms. Where additions to existing circuits, only the new section shall be tested. The resistance to ground of 600 V capacity shall be 10 megohms for the insulation test.

- That the insulation resistance to ground of all nongrounded conductors of multiple circuits is not less than 50 megohms.

- That all circuits are properly connected in accordance with applicable wiring diagrams.

- That all circuits are operable. Operate each control not less than 10 times and operate each lighting and power circuit continuously for not less than 1/2 hour.

METHOD OF MEASUREMENT

108-4.1 Trenching will not be measured for payment. Excavation, backfill, bedding, and reconditioning will be subsidiary.

108-4.2 Cable, ground or counterpoise wire installed in trench shall be measured by the number of linear feet of cable, ground or counterpoise wire installed in trenches, ready for operation, and accepted as satisfactory. Separate measurement will be made for each cable or counterpoise wire installed in trench.

108-4.3 Cable, ground or counterpoise wire, and interstice filler installed in duct or conduit shall be measured by the number of linear feet measured in place, completed, ready for operation, and accepted as satisfactory. Separate measurement will be made for each cable, ground or counterpoise wire installed in duct or conduit.

108-4.4 The quantity of ground rods to be paid for under this item shall be the number of ground rods in place, completed, ready for operation, and accepted as satisfactory.

BASIS OF PAYMENT

108-5.1 Payment will be made at the contract unit price for the items listed below and shown in the Bid Schedule.

Payment will be made under:

Item L-108a	Underground Cable #8 AWG, copper, 5 kV FAA type “B” or type "C" (as specified on Plans), L-824 - per linear foot*

Item L-108b	Underground Cable #8 AWG, copper, 5 kV FAA type “B” or type "C" (as specified on Plans), L-824 - per lump sum

Item L-108c	#6 Bare Copper Ground Conductor - per linear foot*

Item L-108d	#6 Bare Copper Ground Conductor - per lump sum

Item L-108e	Underground Cable, Copper, 600 V, Type "C", L-824 - per linear foot*

Item L-108f	Underground Cable, Copper, 600 V, Type "C", L-824 - per lump sum

Item L-108g	Ground Rod - per each

Item L-108h	Underground cable #14 AWG, copper, 600V, Type "SOOW-A/SOOW", - per linear foot*

Item L-108i	Underground cable #14 AWG, copper, 600V, Type "SOOW-A/SOOW", - per lump sum

Item L-108j	Interstice Filler - per linear foot*

Item L-108k	Interstice Filler - per lump sum

* For payment purposes, 4% will be added to the straight line measurements provided by the Contractor for cable and ground conductor wire.

MATERIAL REQUIREMENTS

AC 150/5345-7	L-824 Underground Electrical Cable for Airport Lighting Circuits

AC 150/5345-26	L-823 Plug and Receptacle Cable Connectors

ASTM B 3	Soft or Annealed Copper Wire

ASTM B 8	Concentric-Lay-Stranded Cooper Conductor, Hard, Medium-Hard, or Soft

ASTM D 4388	Rubber Tapes, Nonmetallic Semi-Conducting and Electrically Insulating

Commercial Item 	Insulation Tape, Electrical, Pressure-Sensitive Adhesive, Plastic

Description A-A-55809

Fed.Spec. J-C-30	Cable and Wire, Electrical Power, Fixed Installation

MIL-I 24391	Insulation Tape, Electrical, Plastic, Pressure Sensitive

ITEM L-109	TRANSFORMER VAULT AND VAULT EQUIPMENT

DESCRIPTION

109-1.1 This item shall consist of constructing an airport transformer vault, a prefabricated metal housing or an electrical enclosure in accordance with these specifications and with the design and dimensions shown in the Plans. This work shall also include the installation of conduits in floor and foundation, painting and lighting of the vault, metal housing or enclosure and the furnishing of all incidentals necessary to produce a completed unit. Included as a separate part under this item or as a separate item where an existing structure (vault, metal housing, enclosure or building) is to be utilized shall be the furnishing of all vault equipment, wiring, electrical buses, cable, conduit, potheads, and grounding systems. This work shall also include the painting of equipment and conduit; the marking and labeling of equipment and the labeling or tagging of wires; the testing of the installation; and the furnishing of all incidentals necessary to place it in operating condition as a completed unit to the satisfaction of the Engineer.

EQUIPMENT AND MATERIALS

109-2.1 GENERAL. Obtain approval of all materials and equipment proposed for the work. Submit to the Engineer 5 complete listings of materials and equipment specified herein and on the Plans. The list shall be prepared to clearly identify the material or equipment by item, name, or designation used on the Plans or specifications and shall indicate where specified. The submittals shall be neatly bound, clearly indexed, and shall include applicable catalog number, cuts, wiring diagrams, performance data, operation and maintenance manuals, etc., for all material or equipment listed below or specified elsewhere in these specifications. In addition, wherever called for elsewhere in these specifications, include in the submittal certificates of compliance, manufacturer's instructions and/or shop drawings, or proposed construction or installation procedures. All materials of similar class or service shall be of one manufacturer. Capacities, sizes, and dimensions given are minimum unless otherwise indicated. All manufactured materials shall be delivered and stored in their original containers, which shall indicate clearly the manufacturer's name, brand, and identifying number.

- Airport lighting equipment and materials covered by FAA specifications shall be certified and listed under AC 150/5345-53, Airport Lighting Equipment Certification Program. This AC, the latest certified equipment list, and the address list of certified airport lighting equipment manufacturers are available on the Internet home page for the FAA Office of the Associate Administrator for Airports (ARP). The direct Internet address is <www.faa.gov/arp/arphome.htm>.

- All other equipment and materials covered by other referenced specifications shall be subject to acceptance through manufacturer's certification of compliance with the applicable specification when requested by the Engineer.

109-2.2 CONCRETE. The concrete for the vault or electrical enclosure shall be proportioned, placed, and cured in accordance with Item P-610, Structural Portland Cement Concrete, using 3/4 inch maximum size coarse aggregate.

109-2.3 REINFORCING STEEL. Reinforcing steel bars shall be intermediate or structural grade deformed-type bars and shall meet the requirements of ASTM A 615.

109-2.4 BRICK. Brick shall conform to ASTM C 62, Grade SW.

109-2.5 ASBESTOS CEMENT DUCT. Asbestos cement duct and fittings shall be in accordance with Fed. Spec. W-C-571.

109-2.6 RIGID STEEL AND INTERMEDIATE CONDUIT. Rigid steel conduit or intermediate conduit and fittings shall be in accordance with UL Standard 6 and 514. They shall be galvanized on the outside. All fittings shall conform to the same specification as the conduit.

109-2.7 LIGHTING. Vault, metal-housing or electrical enclosure light fixtures shall be of a vaporproof type.

109-2.8 OUTLETS. Convenience outlets shall be heavy-duty duplex units designed for industrial service. Outlets shall be specification grade NEMA performance receptacles, grounding-type, AC rated 20 A, 125 V, 2-pole, 3-wire NEMA 5-20R, housed in device boxes with cover plates.

109-2.9 SWITCHES. Vault, metal-housing or electrical enclosure light switches shall be single-pole switches. Switches shall be NEMA Specification Grade Standard, 277 V (ac). Rated for inductive and fluorescent lamp loads, up to 20 A. Switches shall be of the type indicated by symbol on the Plans. Where more than 1 switch is shown at a point, they shall be set under 1 plate, unless otherwise noted.

109-2.10 PAINT.

- Priming paint for ungalvanized metal surfaces shall be a high solids alkyd primer conforming to TT-P-644D

- White paint for body and finish coats on metal and wood surfaces shall be ready-mixed paint conforming to Commercial Item Description A-A-3067.

- Priming paint for wood surfaces shall be mixed on the job by thinning the above specified white paint by adding 1/2 pint of raw linseed oil to each gallon of paint.

- Paint for the floor, ceiling, and inside walls shall be in accordance with Fed. Spec. TT-E-487. Walls and ceiling shall be light gray and the floor shall be medium gray.

- The roof coating for vault shall be hot asphalt material in accordance with ASTM D 2823.

109-2.11 HIGH-VOLTAGE BUS. High-voltage bus shall be standard weight 3/8-inch IPS copper tubing or it may be insulated copper cable of the size and voltage rating specified.

109-2.12 BUS CONNECTORS. Connectors shall be similar to Burndy Type NT (or approved equal) for copper tubing. Connectors for insulated bus cable shall be of the proper size and type for the service intended.

109-2.13 BUS SUPPORTS. Bus supports shall be similar to Westinghouse No. 527892 (or approved equal), insulated for 7,500 volts, single clamp type for 2-bolt flat mounting.

109-2.14 GROUND BUS. Ground bus shall be 1/8 x 3/4 inch copper bus bar.

109-2.15 SQUARE DUCT. Duct shall be square similar to that manufactured by the Square D Company (or approved equal), or the Trumbull Electric Manufacturing Company (or approved equal). The entire front of the duct on each section shall consist of hinged or removable cover for ready access to the interior. The cross section of the duct shall be not less than 4 x 4 inches except where otherwise shown in the Plans.

109-2.16 GROUND RODS. Ground rods shall be copper-cladsteel, 3/4 inch x 10 feet, with copper alloy hex bolt type ground clamps.

109-2.17 POTHEADS. Potheads shall be similar to G&W Type NT, Shape C (or approved equal), unless otherwise specified. Potheads shall be furnished with plain insulator bushings and conduit couplings. Potheads shall have a rating not less than the circuit voltage.

109-2.18 PREFABRICATED METAL HOUSING. The prefabricated metal housing shall be a commercially available unit.

109-2.19 FAA-APPROVED EQUIPMENT. Certain items of airport lighting equipment installed in vaults are covered by individual FAA equipment specifications. The specifications are listed below:

AC 150/5345-3	L-821 Panels for Remote Control of Airport Lighting

AC 150/5345-5	Circuit Selector Switch

AC 150/5345-7	L-824 Underground Electrical Cable for Airport Lighting Circuits

AC 150/5345-10	Constant Current Regulators and Regulator Monitors

AC 150/5345-13	L-841 Auxiliary Relay Cabinet Assembly for Pilot Control of Airport Lighting Circuits

109-2.20 OTHER ELECTRICAL EQUIPMENT. Constant-current regulators, distribution transformers, oil switches, cutouts, relays, terminal blocks, transfer relays, circuit breakers, and all other regularly used commercial items of electrical equipment not covered by FAA equipment specifications shall conform to the applicable rulings and standards of the Institute of Electrical and Electronic Engineers or NEMA. When specified, test reports from a testing laboratory indicating that the equipment meets the specifications shall be supplied. In all cases, equipment shall be new and a first-grade product. This equipment shall be supplied in the quantities required for the specific project and shall incorporate the electrical and mechanical characteristics specified in the specifications and Plans.

109-2.21 WIRE. Wire in conduit rated up to 5,000 volts shall conform to AC 150/5345-7, Specification for L-824 Underground Electrical Cables for Airport Lighting Circuits, for rubber insulated neoprene-covered wire, or Fed. Spec. J-C-30, Type RHW, for rubber insulated fibrous-covered wire. For ratings up to 600 volts, thermoplastic wire conforming to Fed. Spec. J-C-30, Types TW, THW, and THWN, shall be used. The wires shall be of the type, size, number of conductors, and voltage shown in the Plans or in the specifications.

- Control Circuits. Wire shall be not less than No. 12 AWG and shall be insulated for 600 volts. If telephone control cable is specified, No. 19 AWG telephone cable conforming to ICEA S-85-625 specifications shall be used.

- Power Circuits.

- 600 volts maximum: Wire shall be No. 6 AWG or larger and insulated for at least 600 volts.

- 3,000 volts maximum: Wire shall be No. 6 AWG or larger and insulated for at least 3,000 volts.

- Over 3,000 volts: Wire shall be No. 6 AWG or larger and insulated for at least the circuit voltage.

109-2.22 Wood Platform Foundation. If a wood platform foundation is specified, the Contractor shall construct the platform as shown in the Plans. The floor system shall consist of urethane foam core insulated panels with interior and exterior surfaces or similar manufacturer to the building structure. The panels shall be constructed on grade beams of the size shown. Grade beams may be of timber or steel. Timber shall be Douglas Fir-Larch. Timbers shall be pressure treated in accordance with the American Wood Preservers Bureau (AWPB) FDN Standard and shall bear AWPB Quality Mark of an approved inspection agency as described in the AWPB Standard. Preservative salt retention shall be not less than 0.6 lb/ft3. Wood shall be kiln dried after impregnation. Steel grade beams shall be hot-dipped galvanized in accordance with ASTM A-123. The building shall be anchored with soil anchors meeting the requirements of Item P-650.

109-2.23 Electrical Enclosure. The electrical enclosure shall be a pre-engineered structure with minimum dimensions shown on the Plans. The enclosure shall be installed on either a concrete slab or wood platform floor/foundation as shown on the Plans.

The enclosure shall meet the following requirements:

- Panels and Facings.

- The enclosure may be constructed with separate interlocking panels forming the walls and roof or as a single unit. The enclosure exterior walls shall be foamed in place polyurethane core with 1/2 inch plywood on the interior surface. The exterior surface may be either 1/2 inch plywood with a 26 gauge galvanized steel exterior skin or, fiberglass reinforced polyester. The exterior color shall be a factory applied and shall be white.

- The side of the facings which contact the insulation core shall have a coating that will allow core-to-facing bond to be equal or greater than the cohesive strength of the core.

- Insulation core.

- Factory foamed-in-place polyurethane between facings. Insulating value of the composite roof system shall be equal to or greater than R-38, and the wall system equal to or greater than R-19. No voids are allowed in the core.

- Polyurethane shall have a minimum 2 lbs/ft3 density.

- Polyurethane shall be certified UL flame spread 25 or less per ASTM E 84.

- The panel joints shall have tongue and groove or ship lap interlock with continuous silicone sealant tape at interior and exterior faces.

- Panels shall be full length in single piece where practical.

- Panels shall have State Fire Marshals approval.

- Metal flashing and trim at corners, intersections, openings, eaves and ridges shall be of the same finish and 24 gauge thickness to effect a neat appearing, weather tight joint and closure. Provide wrap-around door jamb trim-flashing.

- Enclosure shall have a 12-inch x 12-inch louvered vent installed in one endwall.

- A refrigerator style door(s) of the dimensions shown shall be provided for the enclosure. The door(s) shall be of similar construction to the enclosure. Mounting hardware shall be of stainless steel or of forged brass with chrome plating, Kason Industries No. 1053, or approved equal. Provide neoprene weather-stripping. The door(s) shall be provided with a refrigerator safety lock with pushrod from interior, Kason Industries, No. 56L, cast zinc with chrome plating. Provide lock(s) consisting of a brass, 6-pin E keyway padlock with a shackle that is 3/8 inch in diameter having a closed clearance of 2-1/4 inches. The lock shall have a control key removable core and shall have one separate replacement core. Provide 4 keys and 1 core removal key.

- Enclosure construction shall meet the following.

Live Snow Load 	70 psf

Live Floor Load 	200 psf

Wind Load 	110 mph, Basic wind speed, applied in accordance with the 1997 UBC, Exposure-D, Method 2, Standard Occupancy

Enclosure shall be an Equipment Enclosure for Runway Lighting Systems as manufactured by ALCEM, Inc., of Anchorage, Alaska; Plaschem Shelter as manufactured by Plaschem Supply & Consulting, of Anchorage Alaska; or approved equal.

109-2.24 Flexible Metal Conduit. Conduit shall be water-tight, listed for exposed or direct bury per UL-360, as a grounding conductor per NEC Article 351-9, and rated for temperatures between -67 (F and +220 (F

109-2.25 TAPES.

- Pipe sealing tape: "Scotch" No. 48, Teflon pipe sealing or approved equal.

- Corrosion preventive tape: "Scotch" No. 50 or approved equal.

- Electrical insulating tape: "Scotch" No. 88 or approved equal.

109-2.26 DOORS. Doors, unless otherwise specified, shall be metal-clad fireproof class a doors conforming to requirements of the NEC and local electrical codes.

109-2.27 Radio Control Equipment, L-854. Radio Control Equipment, shall be L-854, Type 1, with a receiver frequency set to the Common Traffic Advisory Frequency (CTAF) for the project airport as found in the Alaska Supplement of the U.S. Government Flight Publication.

109-2.28 Antenna for the receiver-controller. Antenna shall be a heavy-duty omni-directional, tunable, ground plane antenna with vertical polarization in the 118 to 136 MHz band, designed for 100 mph winds. The antenna shall be tuned for the correct system frequency as assigned with a bandwidth of 2 MHz. The antenna shall be of 50 ohms nominal impedance and have an operating VSWR of less than 2:1 at system frequency. The antenna shall be equipped with an integral gap-type lightning arrester. The coaxial cable shall be 50-ohm, type RG-8. Antenna shall be designed to mount on 1-inch pipe support and shall be located on the Snow Removal Equipment Building as shown on the Plans. The antenna ground planes shall be a minimum of 4 feet above the top of the rotating beacon's lamp shields. Antenna mountings shall be fabricated as shown and noted.

109-2.29 Apron Floodlight. Apron floodlight shall be Hubbell Quartzliter Mod. QL-503 or approved equal, 300 W, 120 V, with wire guard .

109-2.30 Photo Electrical Control. Photo electrical control shall be a SPST, 120 V, Tork No. 2100 or approved equal.

109-2.31 Panel Boards. Panel boards snall be single phase, 3-wire, of sizes to provide all circuits and spares indicated. The branch breakers shall be bolt-in type. The enclosure shall be NEMA I with door-in-door front, provided with a circuit index card under plastic on the interior side of the panel door; and the enclosure shall have an engraved phenolic label, lettered to indicate the voltage and current rating of the panel, attached to the panel front exterior.

The panel board circuit breakers shall be bolt-on molded case type, 120/240 V, 10,000 A interrupting capacity, 1- and 2-pole type with current ratings as indicated on Plans. Each pole of the breaker shall provide inverse time delay and instantaneous circuit protection. Breakers shall be operated by toggle type handle and have a quick-make, quick-break over center switching mechanism that is mechanically trip free so that contacts cannot be held closed against short circuits and abnormal currents. Tripping shall be clearly indicated. Non-interchangeable trip breakers shall have sealed covers and interchangeable trip units shall have sealed trip units. Ampere ratings shall be clearly visible.

Panel board circuit breakers shall be UL listed (where procedures exist), conform to the applicable requirements of the latest NEMA Standard and meet the appropriate classifications of Federal Specifications W-A-375a. Breakers shall be standard thermal-magnetic type unless otherwise noted. Circuit breakers for the duplex receptacles shall incorporate overload, short circuit, and UL Class A ground fault circuit interruption.

109-2.32 Transfer Switch. Transfer switch shall be Heavy-duty, 2-pole, 3-wire, S/N, double-throw, non-fusible type in a NEMA I enclosure.

109-2.33 Identification Ties. Identification ties shall be self-locking, heavy duty nylon ties and shall be labeled by heat stamp.

109-2.34 Service Entrance Equipment. The meter/main breaker combination service entrance unit for the Electrical Equipment Enclosure shall be an overhead source or an underground source as shown on the Plans, bottom (under ground) load type, 125 A, 120/240 V, single phase, with 2-pole, 100 A, Q0M2100VH main breaker and 4-jaw kWh meter. The service entrance enclosure shall be raintight NEMA 3R rated with a conduit entry hub fitting on top.

The service entrance disconnect switch shall be mounted on the Snow Removal Equipment Building as shown on the Plans. Disconnect switch shall be 100 A, 240 V, 3-wire (third blade not used), S/N, with NEMA 3R enclosure, non-fused, with field installation kit.

109-2.35 Plug Cutout. The plug cutout shall be a 2-pole type rated 20-amp @ 5kV, 60Hz. The plug shall be insertable in three positions for normal operations, maintenance, and testing. The plug cutout shall be mounted in a NEMA-1 enclosure with a hinged and lockable door sized to allow the plug and key to be operable by a worker standing in front of the enclosure.

109-2.36 Supports for wall-mounted panels, panel boards, and fixtures. Supports for wall mounted panels, panel boards and fixtures shall be metal channels with accessory nuts and fittings; Unistrut or approved equal, or 3/4 inch plywood panels.

109-2.37 Push-Button Stations. Push-button stations shall be off-on, momentary-contact types in water/dust-tight boxes. Provide metal labels identifying the function of each section.

109-2.38 Electric Heater. The electric heater shall be surface mounted and rated 2000 W at 240 V, with mounting kit as required. Thermostat shall be wall mounted on a suitable junction box and be of the line voltage type with an off position and a temperature range of 40 (F to 90 (F. Thermostat current rating shall be suitable to control the specified heater.

109-2.39 Indoor Lighting Fixtures. Indoor lighting fixtures shall be incandescent type with clear prismatic lens, surface mounted with steel extension box, and 100-W lamp.

109-2.40 Hardware. All miscellaneous hardware items, nails, bolts, and screws shall be galvanized steel.

CONSTRUCTION METHODS

CONSTRUCTION OF VAULT, PREFABRICATED METAL HOUSING AND ELECTRICAL ENCLOSURE

109-3.1 GENERAL. The Contractor shall construct the transformer vault, prefabricated metal housing or electrical enclosure at the location indicated in the Plans. Vault construction shall be reinforced concrete, concrete masonry, or brick wall as specified. The metal housing shall be prefabricated equipment enclosure to be supplied in the size specified. The electrical enclosure shall be a pre-engineered building placed on either a poured concrete foundation or a wood platform as specified. The mounting pad or floor details, installation methods, and equipment placement are shown in the Plans.

If the vault, metal housing or electrical enclosure are to be placed on a site not prepared for that purpose under other items of work, the Contractor shall clear, grade, and seed the area around the vault, metal housing or electrical enclosure for a minimum distance of 10 feet on all sides. The slope shall be not less than 4% away from the vault, metal housing or electrical enclosure in all directions. Cost for site work will be considered incidental to this item and no separate payment will be made.

109-3.2 FOUNDATION AND WALLS.

- Reinforced Concrete Construction. The Contractor shall construct the foundation and walls in accordance with the details shown in the Plans. Unless otherwise specified, internal ties shall be of the mechanical type so that when the forms are removed the ends of the ties shall be at least 1 inch beneath the concrete surface; the holes shall be plugged and finished to prevent discoloration. Reinforcing steel shall be placed, as shown in the drawings, and secured in position to prevent displacement during the concrete placement.

The external surfaces of the concrete shall be thoroughly worked during the placing operation to force all coarse aggregate from the surface. Thoroughly work the mortar against the forms to produce a smooth finish free from air pockets and honeycomb.

The surface film of all pointed surfaces shall be removed before setting occurs. As soon as the pointing has set sufficiently, the entire surface inside and outside of the vault shall be thoroughly wet with water and rubbed with a No. 16 carborundum stone, or equal quality abrasive, bringing the surface to a paste. All form marks and projections shall be removed. The surface produced shall be smooth and dense without pits or irregularities. The materials which have been ground into a paste during the rubbing process shall be spread or brushed uniformly over the entire surface (except the interior surfaces that are to be painted shall have all paste removed by washing before painting) and permitted to reset. Final exterior finish shall be obtained by rubbing with No. 30 carborundum stone, or an equal quality abrasive. The surface shall be rubbed until the entire surface is smooth and uniform in color.

- Brick and Concrete Construction. When this type of construction is specified, the foundation shall be concrete conforming to the details shown in the Plans. The outer edge of the foundation at the floor level shall be beveled 1-1/2 inches at 45 degrees. Brick walls shall be 8 inches thick, laid in running bond with every sixth course a header course. Brick shall be laid in cement mortar (1 part masonry cement and 3 parts sand) with full mortar bed and shoved joints. All joints shall be completely filled with mortar, and facing brick shall be back-parged with mortar as work progresses. All joints shall be 3/8 inch thick, exterior joints tooled concave, and interior joints struck flush. Both interior and exterior brick surfaces shall be cleaned and nail holes, cracks and other defects filled with mortar. When specified, a nonfading mineral pigment mortar coloring shall be added to the mortar. Steel reinforcing bars, 3/8 inch in diameter and 12 inches long, shall be set vertically in the center of the brick wall on not more than 2-foot centers to project 2-1/2 inches into the concrete roof slab. Lintels for supporting the brickwork over doors, windows, and louvers shall consist of two 4-inch x 3-inch x 3/8-inch steel angles. Lintels shall be painted with one coat of corrosion-inhibiting primer before installation, and all exposed parts shall be painted similar to doors and window sash after installation.

Window sills may be concrete poured in place or precast concrete as indicated in the Plans. All exposed surfaces shall have a rubbed finish as specified under reinforced concrete construction. After completion, all interior and exterior faces of walls shall be scrubbed with a solution of muriatic acid and water in the proportions of not less than 1 part acid to 10 parts of water. All traces of efflorescence, loose mortar, and mortar stain shall be removed, and the walls washed down with clear water.

- Concrete Masonry Construction. When this type of construction is specified, the foundation shall be concrete conforming to the details shown in the Plans. The concrete masonry units shall be standard sizes and shapes and shall conform to ASTM C 90 and shall include the closures, jambs, and other shapes required by the construction as shown in the Plans. Standard construction practice shall be followed for this type of work including mortar, joints, reinforcing steel for extensions into roof slab, etc. Plaster for interior walls, if specified, shall be portland cement plaster.

109-3.3 ROOF. The vault roof shall be reinforced concrete as shown in the Plans. Reinforcing steel shall be placed as shown in the drawing and secured in position to prevent displacement during the pouring of the concrete. The concrete shall be poured monolithically and shall be free of honeycombs and voids. The surface shall have a steel-troweled finish and shall be sloped as shown in the drawing. The underside of the roof slab shall be finished in the same manner as specified for walls.

One brush or mop coat of hot asphalt roof coating shall be applied to the top surface of the roof slab. The asphalt material shall be heated to within the range specified by the manufacturer and immediately applied to the roof. The finished coat shall be continuous over the roof surface and free from holidays and blisters. Smears and dribbles of asphalt on the roof edges and building walls shall be removed.

109-3.4 REINFORCED CONCRETE FLOOR. The floor shall be reinforced concrete as shown in the drawings either constructed on a previously prepared surface or on natural ground. When present, all sod, roots, refuse, and other perishable material shall be removed from the area under the floor to a depth of 8 inches, unless a greater depth is specified. This area shall be backfilled with materials consisting of sand, cinders, gravel, or stone. Fill shall be placed in layers not to exceed 4 inches and shall be thoroughly compacted by tamping or rolling. A layer of building paper shall be placed over the fill prior to placing concrete. The floor surfaces shall have a steel-troweled finish. The floor shall be level unless a drain is specified, in which case the floor shall be pitched 2% downward toward the drain. A 1/4-inch asphalt felt expansion joint shall be placed between floor and foundation walls. The floor shall be poured monolithically and shall be free of honeycombs and voids.

109-3.5 FLOOR DRAIN. If shown in the Plans, a floor drain and dry well shall be installed in the center of the floor of the equipment room. The dry well shall be excavated 4 foot x 4 foot square and to a depth of 4 feet below the finished floor elevation and shall be backfilled to the elevation of the underside of the floor with gravel which shall all pass a 2 inch mesh sieve and shall all be retained on a 1/4 inch mesh sieve. The gravel backfill shall be placed in 6 inch maximum layers, and the entire surface of each layer shall be tamped either with a mechanical tamper or with a hand tamper weighing not less than 25 pounds and having a face area of not more than 36 square inches nor less than 16 square inches. The drain inlet shall be set flush in the concrete floor. The drain shall have a clear opening of not less than 8 inches in diameter.

109-3.6 CONDUITS IN FLOOR AND FOUNDATION. Conduits shall be installed in the floor and through the foundation walls in accordance with the details shown in the Plans. All underground conduit placed in concrete shall be painted with a bituminous compound. Conduit shall be installed with a coupling or metal conduit adapter flush with the top of the floor. All incoming conduit shall be closed with a pipe plug to prevent the entrance of foreign material during construction. Space conduit entrances shall be left closed.

109-3.7 PAINTING. The floor, ceiling, and inside walls of concrete construction shall first be given a hardening treatment, after which the Contractor shall apply two coats of paint as specified below, except that interior face brick walls need not be painted. The hardening treatment shall consist of applying two coats of either a commercial floor hardener or a solution made by dissolving 2 pounds of magnesium fluosilicate or zinc sulfate crystals in 1 gallon of water. Each coat shall be allowed to dry at least 48 hours before the next application. After the second treating coat has dried, the surfaces shall be brushed clean of all crystals and thoroughly washed with clear water. Paint for walls and ceiling shall be a light gray color approved by the Engineer. The floor paint shall be a medium gray color approved by the Engineer. Before painting, the surfaces shall be dry and clean. The first coat shall be thinned by adding 2/3 quart of spar varnish and 1/3 quart of turpentine to each gallon of paint. The second coat shall be applied without thinning. All doors, lintels, and windows shall be cleaned to remove any rust or foreign material and shall be given one body and one finish coat of white paint. Bare metal surfaces shall be given a prime coat of corrosion-inhibiting primer prior to the body and finish coats.

109-3.9 LIGHTS AND SWITCHES. The Contractor shall furnish and install a minimum of two duplex convenience outlets in the vault room. Where a control room is specified, at least two duplex outlets shall be installed.

INSTALLATION OF EQUIPMENT IN VAULT, PREFABRICATED METAL HOUSING,

ENCLOSURE OR BUILDING

109-3.10 GENERAL. The Contractor shall furnish, install, and connect all equipment, equipment accessories, conduit, cables, wires, buses, grounds, and support necessary to insure a complete and operable electrical distribution center for the airport lighting system as specified herein and shown in the Plans. When specified, an emergency power supply and transfer switch shall be provided and installed.

The equipment installation and mounting shall comply with the requirements of the NEC and local code agency having jurisdiction.

109-3.11 POWER SUPPLY EQUIPMENT. Transformers, regulators, booster transformers, and other power supply equipment items shall be furnished and installed at the location shown in the Plans or as directed by the Engineer. The power supply equipment shall be set on steel "H" sections, "I" beams, channels, or concrete blocks to provide a minimum space of 1-1/2 inches between the equipment and the floor. The equipment shall be placed so as not to obstruct the oil-sampling plugs of the oil-filled units; and name-plates shall, so far as possible, not be obscured.

If specified in the Plans and specifications, equipment for an alternate power source or an emergency power generator shall be furnished and installed. The alternate power supply installation shall include all equipment, accessories, an automatic changeover switch, and all necessary wiring and connections. The emergency power generator set shall be the size and type specified.

109-3.12 SWITCHGEAR AND PANELS. Oil switches, fused cutouts, relays, transfer switches, panels, panel boards, and other similar items shall be furnished and installed at the location shown in the Plans or as directed by the Engineer. Wall or ceiling-mounted items shall be attached to the wall or ceiling with galvanized bolts of not less than 3/8 inch diameter engaging metal expansion shields or anchors in masonry or concrete vaults.

109-3.13 DUCT AND CONDUIT. The Contractor shall furnish and install square-type exposed metallic ducts with hinged covers for the control circuits in the vault. These shall be mounted along the walls behind all floor-mounted equipment and immediately below all wall-mounted equipment. The hinged covers shall be placed to open from the front side with the hinges at the front bottom.

Wall brackets for square ducts shall be installed at all joints 2 feet or more apart with intermediate brackets as specified. Conduit shall be used between square ducts and equipment or between different items of equipment when the equipment is designed for conduit connection. When the equipment is not designed for conduit connection, conductors shall enter the square-type control duct through insulating bushings in the duct or on the conduit risers.

109-3.14 CABLE ENTRANCE AND HIGH-VOLTAGE BUS SYSTEM. Incoming underground cable from field circuits and supply circuits will be installed outside the walls of the transformer vault as a separate item under Item L-108. The Contractor installing the vault equipment shall bring the cables from the trench or duct through the entrance conduits into the vault, cabinet or enclosure and make the necessary electrical connections. For the incoming and outgoing high voltage load circuits, the Contractor shall furnish and install rigid metallic vi conduit risers, surmounted by potheads, from floor level to the level as shown in the Plans.

The incoming high-voltage power supply service to the vault shall enter below the floor of the vault and shall rise from the floor level in a rigid metallic conduit riser, surmounted by a pothead, as described above. Using insulated high-voltage cable, the incoming power service shall be connected from the pothead to the oil-fused cutouts or to the specified disconnecting switch or equipment. From the oil-fused cutouts or disconnecting device, the insulated service conductors shall be connected to the overhead voltage bus system of the vault. The high-voltage bus system shall utilize the materials specified and shall be mounted and installed in accordance with the requirements of the NEC or the local code agency having jurisdiction.

109-3.15 WIRING AND CONNECTIONS. The Contractor shall make all necessary electrical connections in the vault, cabinet or enclosure in accordance with the wiring diagrams furnished and as directed by the Engineer. In wiring to the terminal blocks, the Contractor shall leave sufficient extra length on each control lead to make future changes in connections at the terminal block. This shall be accomplished by running each control lead the longest way around the box to the proper terminal. Leads shall be neatly laced in place.

109-3.16 MARKING AND LABELING. All equipment, control wires, terminal blocks, etc., shall be tagged, marked, or labeled as specified below:

- Wire Identification. The Contractor shall furnish and install self-sticking wire labels or identifying tags on all control wires at the point where they connect to the control equipment or to the terminal blocks. Wire labels, if used, shall be of the self-sticking preprinted type and of the manufacturer's recommended size for the wire involved. Identification markings designated in the Plans shall be followed. Tags, if used, shall be of fiber not less than 3/4 inch in diameter and not less than 1/32 inch thick. Identification markings designated in the Plans shall be stamped on tags by means of small tool dies. Each tag shall be securely tied to the proper wire by a nonmetallic cord.

- Labels. The Contractor shall stencil identifying labels on the cases of regulators, breakers, and distribution and control relay cases with white oil paint as designated by the Engineer. The letters and numerals shall be not less than 1 inch in height and shall be of proportionate width. The Contractor shall also mark the correct circuit designations in accordance with the wiring diagram on the terminal marking strips which are a part of each terminal block.

METHOD OF MEASUREMENT

109-4.1 The quantity of vaults to be paid for under this item shall consist of the number of vaults constructed in place and accepted as a complete unit.

109-4.2 The quantity of prefabricated metal housings to be paid for under this item shall consist of the number of housings constructed in place and accepted as a complete unit.

109-4.3 The quantity of electrical enclosures to be paid for under this item shall consist of the number of enclosures constructed in place and accepted as a complete unit.

109-4.4 The quantity of electrical equipment installed in an existing structure (vault, prefabricated metal housing electrical enclosure or building) to be paid for under this item shall consist of all equipment installed, connected, and accepted as a complete unit ready for operation.

BASIS OF PAYMENT

109-5.1 Payment will be made at the contract unit price for each completed and accepted vault, prefabricated metal housing or electrical enclosure.

109-5.2 Payment will be made at the contract unit price for equipment supplied and installed in a new or existing structure (vault, prefabricated metal housing, electrical enclosure or building) completed and accepted.

Payment will be made under:

Item L-109a	Transformer Vault in Place - per each

Item L-109b	Prefabricated Metal Housing and Foundation in Place - per each

Item L-109c	Electrical Enclosure and Foundation in Place - per each

Item L-109d	Installation of Electrical Equipment in New or Existing Structure - per each

MATERIAL REQUIREMENTS

AC 150/5340-9	Prefabricated Metal Housing for Electrical Equipment

AC 150/5345-3	L-821 Panels for Remote Control of Airport Lighting

AC 150/5345-5	Circuit Selector Switch

AC 150/5345-7	L-824 Underground Electrical Cable for Airport Lighting Circuits

AC 150/5345-10	Constant Current Regulators and Regulator Monitors

AC 150/5345-13A	L-841 Auxiliary Relay Cabinet Assembly for Pilot Control of Airport Lighting Circuits

ANSI/ICEA S-85-625	Aircore, Polyethylene Insulated, Copper Conductor, Telecommunications Cable

ASTM A 615	Deformed and Plain Billet Steel Bars for Concrete Reinforcement

ASTM C 62	Building Brick (Solid Masonry Units Made from Clay or Shale)

ASTM C 90	Concrete Masonry Units, Loadbearing

ASTM D 2823	Asphalt Roof-Coating

Commercial Item	Paint: Alkyd, Exterior, Low VOC

Description A-A-3067

Fed.Spec.J-C-30	Cable and Wire, Electrical (Power, Fixed Installation)

Fed. Spec. TT-E-487	Enamel, Floor and Deck

Fed.Spec.W-C-571	Conduit and Fittings, Nonmetal, Rigid; (Asbestos-Cement or Fire-Clay Cement), (For Electrical Purposes)

ITEM L-110	UNDERGROUND ELECTRICAL DUCT

DESCRIPTION

110-1.1 This item shall consist of underground electrical ducts installed in accordance with this specification at the locations and in accordance with the dimensions, designs, and details shown in the Plans. This item shall include the installation of all underground electrical ducts or underground conduits. It shall also include all trenching, marking, backfilling, removal, and restoration of any paved areas; manholes, concrete encasement, mandreling installation of steel drag wires and duct markers, capping, and the testing of the installation as a completed duct system ready for installation of cables, to the satisfaction of the Engineer.

# EQUIPMENT AND MATERIALS

110-2.1 GENERAL. All equipment and materials covered by referenced specifications shall be subject to acceptance through manufacturer's certification of compliance with the applicable specification when so requested by the Engineer.

110-2.2 BITUMINOUS FIBER DUCT. Bituminous fiber duct and fittings shall conform to the requirements of UL Standard 543.

- Type I, for concrete encasement.

- Type II, for direct burial.

110-2.3 ASBESTOS CEMENT DUCT. Asbestos cement duct and fittings shall conform to the requirements of Fed. Spec. W-C-571 and shall be one of the following, as specified in the proposal:

- Type I, for concrete encasement.

- Type II, for direct burial.

110-2.4 STEEL CONDUIT. Rigid steel conduit and fittings shall conform to the requirements of UL Standard 6, 514, and 1242.

110-2.5 CONCRETE. Concrete shall conform to Item P-610, Structural Portland Cement Concrete, 1 inch maximum size coarse aggregate.

110-2.6 PLASTIC CONDUIT. Plastic conduit and fittings shall conform to the requirements of Fed. Spec. W-C-1094 Type I, suitable for underground use either directly in the earth or encased in concrete. The conduit shall be one of the following as shown on the Plans:

- Underground Plastic Duct shall be rigid, non-metallic, conduit, Schedule 40 PVC conforming to UL Standard 651 and NEMA TC-2, nominal size as indicated on the Plans. All fittings such as elbows, couplings, connectors, expansion joints, adapters, etc., used in the installation shall be Schedule 40 PVC conforming to UL Standard 514 and NEMA TC-3.

- Underground Plastic Duct shall be Type III, rigid, HDPE pipe. The material shall have a cell classification of 345434C or better in accordance with ASTM D 3350. The nominal size shall be as indicated on the Plans with a minimum wall thickness of 5/32 inch. All fittings such as saddle fittings, elbows, couplings, connectors, adapters, etc., used in the installation shall be HDPE and shall be of the same material as the duct.

110-2.7 FLEXIBLE METAL CONDUIT. Flexible metal conduit shall be water-tight, listed for exposed or direct bury per UL-360, as a grounding conductor per NEC Article 351-9, and rated for temperatures between -67 (F and +220 (F.

110-2.8 TAPES.

- Pipe sealing tape shall be Teflon, "Scotch" No. 48 or approved equal.

- Corrosion preventive tape shall be "Scotch" No. 50 or approved equal.

# CONSTRUCTION METHODS

110-3.1 GENERAL. The Contractor shall install underground ducts at the approximate locations indicated in the airport layout plans. The Engineer shall indicate specific locations as the work progresses. Ducts shall be of the size, material, and type indicated in the Plans or specifications. Where no size is indicated in the Plans or specifications, the ducts shall be not less than 3 inches inside diameter. All duct lines shall be laid so as to grade toward handholes, manholes and duct ends for drainage. Grades shall be at least 3 inches per 100 feet. On runs where it is not practicable to maintain the grade all one way, the duct lines shall be graded from the center in both directions toward manholes, handholes, or duct ends. Pockets or traps where moisture may accumulate shall be avoided.

Seal all joints in the rigid steel conduit runs with Teflon pipe sealing tape applied to the threaded couplings. Wrap the completed joint with 2 layers of corrosion preventative tape, 1/2 lapped and extending 1-1/2 inches on both sides of the joints.

After the conduit run has been completed, pull a standard flexible mandrel not less than 12 inches long, having a diameter approximately 1/4 inch less than the inside diameter of the conduit, through the entire length of the conduit run, after which a brush with stiff bristles of at least the diameter of the inside of the conduit shall be pulled through the entire length of the conduit run to make certain that no particles of earth, sand, or gravel have been left in the line.

All ducts installed shall be provided with a No. 10 gauge galvanized iron or steel drag wire for pulling the permanent wiring. Sufficient length shall be left in manholes or handholes to bend the drag wire back to prevent it from slipping back into the duct. Where spare ducts are installed, as indicated on the Plans, the open ends shall be plugged with removable tapered plugs, designed by the duct manufacturers, or with hardwood plugs conforming accurately to the shape of the duct and having the larger end of the plug at least 1/4 inch greater in diameter than the duct.

All ducts shall be securely fastened in place during construction and progress of the work and shall be plugged to prevent seepage of grout, water, or dirt. Any duct section having a defective joint shall not be installed.

All ducts, except steel conduit, installed under runways, taxiways, aprons, and other paved areas shall be encased in a concrete envelope.

Where turf is well established and the sod can be removed, it shall be carefully stripped and properly stored.

Trenches for ducts may be excavated manually or with mechanical trenching equipment. Walls of trenches shall be essentially vertical so that a minimum of shoulder surface is disturbed. Blades of road patrols or graders shall not be used to excavate the trench. The Contractor shall ascertain the type of soil or rock to be excavated before bidding. All excavation shall be unclassified.

Trenches for burial of duct or conduit shall be of sufficient width to provide a minimum of 2 inches of lateral clearance between the duct or conduit and trench walls on both sides as shown on the Plans. Trenches for burial of duct or conduit shall be of sufficient depth as to assure 1.5 feet minimum duct or conduit burial depth below finished grade, plus 2 inches minimum of below duct or conduit bedding as shown on the Plans, plus adequate over excavation depth as required to slope and grade all duct or conduit installations to drain toward light bases or hand holes.

The bottom of all trenches shall be sloped and lined with a layer of bedding material of minus 1/4-inch material that is not less than 2 inches in depth, before placing any duct or conduit in the trenches. Bedding material shall be, sand, gravel, crushed aggregate, or other suitable material containing no organic, frozen, or other deleterious material.

Excavate foundations, footings, slabs, pads, manholes, handholes, ducts and/or duct banks, or light base assemblies so as to permit the placing or construction of the full width, length, and depth of the structure or object and the layer of bedding material, whenever bedding is required.

110-3.2 DUCTS ENCASED IN CONCRETE. Unless otherwise shown in the Plans, concrete-encased ducts shall be installed so that the top of the concrete envelope is not less than 1.5 feet below the finished subgrade where installed under runways, taxiways, aprons, or other paved areas, and not less than 1.5 feet below finished grade where installed in unpaved areas. Ducts under paved areas shall extend at least 3 feet beyond the edges of the pavement or 3 feet beyond any underdrains which may be installed alongside the paved area. Trenches for concrete-encased ducts shall be opened the complete length before concrete is laid so that if any obstructions are encountered, proper provisions can be made to avoid them. All ducts for concrete encasements shall be placed on a layer of concrete not less than 3 inches thick prior to its initial set. Where two or more ducts are encased in concrete, the Contractor shall space them not less than 1-1/2 inches apart (measured from outside wall to outside wall) using spacers applicable to the type of duct. As the duct laying progresses, concrete not less than 3 inches thick shall be placed around the sides and top of the duct bank. End bells or couplings shall be installed flush with the concrete encasement where required.

When specified, the Contractor shall reinforce the bottom side and top of encasements with steel reinforcing mesh or fabric or other approved metal reinforcement. When directed, the Contractor shall supply additional supports where the ground is soft and boggy, where ducts cross under roadways, or where otherwise shown on the Plans under such conditions, the complete duct structure shall be supported on reinforced concrete footings, piers, or piles located at approximately 5-foot intervals.

When clay or soapstone ducts are specified, they shall be installed with concrete encasement as described above. Clay conduit shall be of the single-bore type. Where the self-centering socket-joint type of single clay duct is used, conduit shall be built up, tier by tier, and separated only by sufficient mortar or fine aggregate concrete to bed the ducts evenly and fill all voids between ducts. Single ducts shall be jointed together and the joints grouted with Portland cement mortar. A suitable gasket (of rubber or other approved material) shall first be placed in the receptacle end of the duct, prior to the joining operation, in order to exclude all mortar from the duct.

Where the square bore butt joint type of clay duct, single or multicell, is used, sections shall be aligned with at least 4 steel dowel pins and joints wrapped with duct tape 6 inches wide and lapped 6 inches. All joints in a bank of single-bore ducts shall be staggered, beginning evenly from the manhole or handhole, by means of short lengths 6, 8, 9, 12, and 15 inches long. Cement mortar shall be troweled around each and every joint. Voids in the duct bank, caused by the external shape of the corners of the conduit, shall also be filled with mortar. The joining and joints of soapstone duct shall be done in accordance with the manufacturer's recommendations.

110-3.3 DUCTS WITHOUT CONCRETE ENCASEMENT. Trenches for single-duct lines shall be not less than 6 inches nor more than 12 inches wide, and the trench for 2 or more ducts installed at the same level shall be proportionately wider. Trench bottoms for ducts without concrete encasement shall be made to conform accurately to grade so as to provide uniform support for the duct along its entire length.

A layer of sand, at least 4 inches thick (loose measurement) shall be placed in the bottom of the trench as bedding for the duct. The bedding material shall consist of sand , and it shall contain no particles that would be retained on a 1/4-inch sieve. The bedding material shall be tamped until firm.

Unless otherwise shown in Plans, ducts for direct burial shall be installed so that the tops of all ducts are at least 1.5 feet below the finished grade.

When two or more ducts are installed in the same trench without concrete encasement, they shall be spaced not less than 2 inches apart (measured from outside wall to outside wall) in a horizontal direction and not less than 6 inches apart in a vertical direction.

Trenches shall be opened the complete length before duct is installed so that if any obstructions are encountered, proper provisions can be made to avoid them.

110-3.4 PVC Conduit. Install PVC conduit where indicated on the Plans.

Fabricate the conduit runs as recommended by the conduit manufacturer. Make all joints square, tight, and leakproof. Do not allow bends or breaks in the joints. Use only solvents and cements, which are specifically recommended by the conduit manufacturer. Join together the complete run between each light base alongside the trench. Place in the trench and connect to the base assembly after the minimum cure time of the joint cement has elapsed and after inspection and approval is granted by the Engineer.

Make field cuts of the conduit true and square with a tool or lathe designed for the purpose. Debur and ream the conduit as required.

Bend PVC conduit at the job site only with a "Hot Box" or as recommended by the conduit manufacturer. Heat the conduit uniformly to obtain smooth bends without overheating. Conduit with a brown appearance shall not be used. Conduit with extremely sharp bends, kinks in the bends or which exhibits a significant visual defect shall not be used.

Install expansion fittings in each run of conduit between light base assemblies, at spacing not exceeding 60 feet. The expansion fitting shall be of the same manufacturer as the conduit and shall be installed in accordance with the manufacturer's instruction. Expansion joints shall be installed a maximum of 10 feet from the edge light bases or hand holes and shall be installed with joints 1/4 inch expanded, resulting in a minimum requirement of four expansion joints per 190-foot run of conduit.

After the conduit run has been completed, pull a standard flexible mandrel not less than 12 inches long, having a diameter approximately 1/4 inch less than the inside diameter of the conduit, through the entire length of the conduit run, after which a brush with stiff bristles of at least the diameter of the inside of the conduit shall be pulled through the entire length of the conduit run to make certain that no particles of earth, sand, or gravel have been left in the line.

110-3.5 HDPE Conduit. Assemble high-density polyethylene conduit into runs on the surface and install in trenches after coupling of the section. Butt-weld the duct using the manufacturer's recommended procedures and equipment. Assure that the conduit is open, continuous and free of water and debris prior to installing cable. In underground conduit, pull a stiff bristle brush through the entire length of the conduit run immediately prior to the cable being installed.

110-3.6 DUCT MARKERS. Place marker tape 0.5 foot below final grade or below bottom of Crushed Aggregate Base Course in paved areas for the full length of the trenches above all ducts installed as indicated on the Plans.

When called for in the Plans, the location of the ends of all ducts shall be marked by a concrete slab marker 2 feet square and 4 inches thick extending approximately 1 inch above the surface. The markers shall be located above the ends of all ducts or duct banks, except where ducts terminate in a handhole, manhole, or building.

The Contractor shall impress the word “DUCT” on each marker slab. He shall also impress on the slab the number and size of ducts beneath the marker. The letters shall be 4 inches high and 3 inches wide with width of stroke 1/2 inch and 1/4 inch deep or as large as the available space permits.

110-3.7 BACKFILLING. Backfill only after the duct has been placed, inspected and accepted by the Engineer.

After concrete-encased ducts have been properly installed and the concrete has had time to set, the trench shall be backfilled in at least two layers with excavated material not larger than 2 inches in diameter and thoroughly tamped and compacted to at least the density of the surrounding undisturbed soil. If necessary to obtain the desired compaction, the backfill material shall be moistened or aerated as required. If duct is placed in the structural section (P-154, P-208, P-209) of a pavement such as for a runway or taxiway, the Contractor shall construct the backfill in accordance with the specifications for the material in which the duct is placed.

Trenches shall not be excessively wet and shall not contain pools of water during backfilling operations.

The trench shall be completely backfilled and tamped level with the adjacent surface: except that, when sod is to be placed over the trench, the backfilling shall be stopped at a depth equal to the thickness of the sod to be used, with proper allowance for settlement.

Any excess excavated material shall be removed and disposed of in accordance with instructions issued by the Engineer.

For ducts without concrete envelope, sand shall be placed around the ducts and carefully tamped around and over them with hand tampers. Sand shall be non frost susceptible with no particle larger than 1/4 inch. Sand shall be placed to provide a minimum of 2 inches of cover when compacted over and to the sides of the duct. The remaining trench may be filled with regular run of excavated material and thoroughly tamped as specified above. If duct is placed in the structural section (P-154, P-208, P-209) of a pavement such as for a runway or taxiway, the Contractor shall construct the backfill in accordance with the specifications for the material in which the duct is placed.

110-3.8 RESTORATION. Where sod has been removed, it shall be replaced as soon as possible after the backfilling is completed. All areas disturbed by the trenching, storing of dirt, cable laying, pad construction and other work shall be restored to its original condition. The restoration shall include any necessary topsoil, fertilizing, liming, seeding, sprigging, or mulching. All such work shall be performed in accordance with the FAA Standard Turfing Specifications. The Contractor shall be held responsible for maintaining all disturbed surfaces and replacements until final acceptance.

# METHOD OF MEASUREMENT

110-4.1 Underground duct shall be measured by the linear foot of duct installed, measured in place, completed, and accepted. Separate measurement shall be made for the various types and sizes.

Items shown as lump sum will not be measured for payment.

# BASIS OF PAYMENT

110-5.1 Payment will be made at the contract unit price for each type and size of single-way or multi-way duct completed and accepted. This price shall be full compensation for furnishing all materials and for all preparation, assembly, and installation of these materials, and for all labor, equipment, tools, and incidentals necessary to complete this item.

Payment will be made under:

Item L-110a	2-1/8 inch Rigid Steel Conduit - per linear foot

Item L-110b	2-1/8 inch Rigid Steel Conduit - per lump sum

Item L-110c	2-inch PVC Conduit - per linear foot

Item L-110d	2-inch PVC Conduit - per lump sum

Item L-110e	1-1/4 inch PVC Conduit - per linear foot

Item L-110f	1-1/4 inch PVC Conduit - per lump sum

Item L-110g	2-inch PE Conduit - per linear foot

Item L-110h	2-inch PE Conduit - per lump sum

Item L-110i	Multi-Way Duct in Concrete (# of conduit) - per linear foot

Item L-110j	Multi-Way Duct in Concrete (# of conduit) - per lump sum

MATERIAL REQUIREMENTS

Fed. Spec. W-C-571	Conduit and Fittings, Nonmetal, Rigid; (Asbestos-Cement or Fire-Clay Cement), (For Electrical Purposes)

Fed. Spec. W-C-1094	Conduit and Fittings; Nonmetallic, Rigid, (Plastic)

UL Standard 6	Rigid Metal Conduit

UL Standard 514	Fittings for Conduit and Outlet Boxes

UL Standard 543	Impregnated-Fiber Electrical Conduit

UL Standard 1242	Intermediate Metal Conduit

ITEM L-119	OBSTRUCTION LIGHTS

DESCRIPTION

119-1.1 This item shall consist of furnishing and installing obstruction lights in accordance with these specifications. Included in this item shall be the furnishing and installing of wood poles, steel or iron pipes, or other supports as required in the Plans or specifications.

This item shall also include all wire and cable connections, the furnishing and installing of all necessary conduits and fittings, insulators, pole steps, pole crossarms, and the painting of poles and pipes. In addition, it includes the furnishing and installing of all lamps and, if required, the furnishing and installing of insulating transformers, the servicing and testing of the installation and all incidentals necessary to place the lights in operation as completed units to the satisfaction of the Engineer.

EQUIPMENT AND MATERIALS

119-2.1 GENERAL.

- Airport lighting equipment and materials covered by FAA specifications shall be certified and listed in accordance with AC 150/5345-53, Airport Lighting Equipment Certification Program. This AC, the latest certified equipment list, and the address list of certified airport lighting equipment manufacturers are available on the Internet home page for the FAA Office of the Associate Administrator for Airports (ARP). The direct Internet address is <www.faa.gov/arp/arphome.htm>.

- All other equipment and materials covered by other reference specifications shall be subject to acceptance through manufacturer's certification of compliance with the applicable specification when requested by the Engineer.

119-2.2 OBSTRUCTION LIGHTS. The obstruction lights shall conform to the requirements of AC 150/5345-43, Specification for Obstruction Lighting Equipment.

119-2.3 INSULATING TRANSFORMERS. Where required for series circuits, the insulating transformers shall conform to the requirements of AC 150/5345-47, Isolation Transformers for Airport Lighting Systems.

119-2.4 TRANSFORMER HOUSING. Transformer housings, if specified, shall conform to AC 150/5345-42, Specification for Airport Light Base and Transformer Housings, Junction Boxes, and Accessories.

119-2.5 CONDUIT. Steel conduit and fittings shall be in accordance with UL Standard 6, 514, and 1242.

119-2.6 WIRES. Wires in conduit rated up to 5,000 volts shall conform to AC 150/5345-7, Specification for L-824 Underground Electrical Cable for Airport Lighting Circuits, for rubber insulated neoprene covered wire, or Fed. Spec. J-C-30, Type RHW, for rubber insulated fibrous covered wire. For ratings up to 600 volts, thermoplastic wire conforming to Fed. Spec. J-C-30, Types TW, THW, and THWN, shall be used. The wires shall be of the type, size, number of conductors, and voltage shown in the Plans or in the specifications. Overhead line wire from pole to pole, where specified, shall conform to ANSI/ICEA S-70-547.

119-2.7 MISCELLANEOUS. Paint, poles, pole steps, insulators, and all other miscellaneous materials necessary for the completion of this item shall be new and first-grade commercial products. These products shall be as specified in the Plans or specifications.

CONSTRUCTION METHODS

119-3.1 PLACING THE OBSTRUCTION LIGHTS. The Contractor shall furnish and install single- or double-obstruction lights as specified and shown in the Plans. The obstruction lights shall be mounted on poles, buildings, or towers approximately at the location shown in the Plans. The exact location shall be as directed by the Engineer.

119-3.2 INSTALLATION ON POLES. Where obstruction lights are to be mounted on poles, each obstruction light shall be installed with its hub at least as high as the top of the pole. All wiring shall be run in not less than 1 inch galvanized rigid steel conduit. If specified, pole steps shall be furnished and installed, the lowest step being 5 feet above ground level. Steps shall be installed alternately on diametrically opposite sides of the pole to give a rise of 18 inches for each step. Conduit shall be fastened to the pole with galvanized steel pipe straps and shall be secured by galvanized lag screws. Poles shall be painted as shown in the Plans and specifications.

When obstruction lights are installed on existing telephone or power poles, a large fiber insulating sleeve of adequate diameter and not less than 4 feet long, shall be installed to extend 6 inches above the conductors on the upper crossarm. In addition, the sleeve shall be at least 18 inches below the conductors on the lower crossarm. The details of this installation shall be in accordance with the Plans.

119-3.3 INSTALLATION ON BEACON TOWER. Where obstruction lights are installed on a beacon tower, two obstruction lights shall be mounted on top of the beacon tower using 1-inch conduit. The conduit shall screw directly into the obstruction light fixtures and shall support them at a height of not less than 4 inches above the top of the rotating beacon. If obstruction lights are specified at lower levels, the Contractor shall install not less than 1/2-inch galvanized rigid steel conduit with standard conduit fittings for mounting the fixtures. The fixtures shall be mounted in an upright position in all cases. The conduit shall be fastened to the tower members with "wraplock" straps, clamps, or approved fasteners spaced approximately 5 feet apart. Three coats of aviation-orange paint shall be applied (one prime, one body, and one finish coat) to all exposed material installed.

119-3.4 INSTALLATION ON BUILDINGS, TOWERS, SMOKESTACKS, ETC. Where obstruction lights are to be installed on buildings or similar structures, the installation shall be made in accordance with details shown in the Plans. The hub of the obstruction light shall be not less than 12 inches above the highest point of the obstruction except in the case of smokestacks where the uppermost units shall be mounted not less than 5 feet, nor more than 10 feet below the top of the stack. Conduit supporting the obstruction light units shall be fastened to wooden structures with galvanized steel pipe straps and shall be secured by 1-1/2-inch No. 10 galvanized wood screws. Conduit shall be fastened to masonry structures by the use of expansion shields, screw anchors, or toggle bolts using No. 10, or larger, galvanized wood or machine screws. Conduit fastened to structural steel shall have the straps held with not less than No. 10 roundhead machine screws in drilled and tapped holes. Fastenings shall be approximately 5 feet apart. Three coats of aviation-orange paint shall be applied (one prime, one body, and one finish coat) to all exposed material installed.

119-3.5 SERIES INSULATING TRANSFORMERS. The L-810 series obstruction light does not include a film cutout; therefore, an insulating transformer is required with each series lamp. Double series units of this type require two series insulating transformers. The transformer shall be housed in a base or buried directly in the earth in accordance with the details shown in the Plans.

119-3.6 WIRING. The Contractor shall furnish all necessary labor and materials and shall make complete electrical connections from the underground cable or other source of power in accordance with the wiring diagram furnished with the project plans. If underground cable is required for the power feed and if duct is required under paved areas, the cable and duct shall be installed in accordance with (and paid for) under Item L-108, Underground Cable, and Item L-110, Underground Electrical Duct.

119-3.7 LAMPS. The Contractor shall furnish and install in each unit one or two lamps, as required, conforming to the following requirements:

- Series lamp: 6.6 ampere, 1020-lumen, a-21 clear bulb, medium prefocus base.

- Multiple lamp: 100, 107, or 116 watts; 115, 120, or 125 volts; a-21 clear bulb, medium screw base.

119-3.8 TESTS. The installation shall be fully tested by continuous operation for not less than 1/2 hour as a completed unit prior to acceptance. These tests shall include the functioning of each control not less than 10 times.

METHOD OF MEASUREMENT

119-4.1 The quantity of lights to be paid for under this item will be the number of single- or double-type obstruction lights installed and accepted as completed units, in place, ready for operation.

BASIS OF PAYMENT

119-5.1 Payment will be made at the contract unit price for each completed obstruction light installed, in place by the Contractor, and accepted by the Engineer.

Payment will be made under:

Item L-119a 	Obstruction Light - per each

MATERIAL REQUIREMENTS

AC 150/5345-7 	L-824 Underground Electrical Cable for Airport Lighting Circuits

AC 150/5345-42 	Airport Light Base and Transformer Housings, Junction Boxes, and Accessories

AC 150/5345-43 	Obstruction Lighting Equipment

AC 150/5345-47 	Isolation Transformers for Airport Lighting Systems

ANSI/ICEA S-70-547	Weather-Resistant Polyolefin-Covered Wire and Cable

Fed.Spec.J-C-30 	Cable and Wire, Electrical (Power, Fixed Installation)

PART XII - STRUCTURES

ITEM S-143	FUEL TANK

143.1.1 DESCRIPTION. This item consists of furnishing and installing a protected aboveground fuel tank, of the capacity specified, complete with hand pump and fuel, in accordance with these specifications and the Plans.

143.2.1 MATERIALS.

- Fuel Tank. Skid-mounted, doublewall, aboveground steel tank with a positive pressure alarm system. The tank shall meet or exceed the requirements of UL 2085, Underwriters Laboratories Standard for Safety for Protected Aboveground Tanks for Flammable and Combustible Liquids. The tank shall be of the capacity shown in the bid schedule. The tank shall have a 2-inch fill opening with locking cap, 1-1/4 -inch vent with screen, and a threaded opening for the specified fuel pump.

- Hand Pump. Double-action pump, equipped with detachable, self-venting bung adapter, set screws and strainer screen. The pump shall have 16 feet of 3/4-inch diameter hose with shut-off nozzle and deliver a minimum of 20 gallons/100 strokes. The pump supplied shall be a Gasboy, Model 1720, or approved equal.

- Fuel. No. 1 diesel.

143.3.1 CONSTRUCTION METHODS. Mount and secure the tank on the skid base. Install hand pump assembly and all fittings and hose. Place tank at the location shown on the Plans, or as directed. Fill to capacity with specified fuel.

143.4.1 METHOD OF MEASUREMENT. By the number of tanks specified, installed and accepted as completed units in place.

143.5.1 BASIS OF PAYMENT. At the contract unit price for the pay items listed below that appear in the bid schedule.

Payment will be made under:

Item S-143a	Fuel Tank(Capacity) - per each

Item S-143b	Fuel - per lump sum

PART XIII - CONTRACTOR FURNISHED SERVICES

ITEM G-100	MOBILIZATION AND DEMOBILIZATION

DESCRIPTION

100-1.1 This item consists of preparatory work and operations, including but not limited to operations necessary to move personnel, equipment, supplies and incidentals to the project site; to establish offices, buildings and other facilities, except as provided under Section 130; to perform all other work and operations, including costs incurred, before beginning work on the project; and to complete similar demobilization activities, including submittals such as as-builts, certificates, payrolls, civil rights reports, equipment warranties, etc.

# METHOD OF MEASUREMENT

100-2.1 Payment for mobilization and demobilization will be made in partial payments as follows:

- Up to sixty percent of the amount bid for mobilization and demobilization may be paid when equipment and supplies are landed in serviceable condition at the project site and other necessary preparations have been completed so that work can commence on other pay items.

- The remaining balance will be paid as contractor facilities are dismantled and equipment is removed from the airport property, with the final increment paid upon completion of demobilization or as approved by the Engineer.

The right is reserved to require submittal of invoices, receipted bills, payrolls, and other appropriate documents to justify any or all payments under this item.

# BASIS OF PAYMENT

100-3.1 Payment will be made at the contract lump sum price for mobilization and demobilization. This price and payment shall be full compensation for all costs associated with this item.

Payment will be made under:

Item G-100a	Mobilization and Demobilization - per lump sum

ITEM G-120	DISADVANTAGED BUSINESS ENTERPRISE (DBE) PROGRAM

(Federal-Aid Contracts)

120-1.1 DESCRIPTION. The work consists of providing Disadvantaged Business Enterprises (DBEs), as defined in Title 49, CFR (Code of Federal Regulations), Part 26, with the opportunity to participate on an equitable basis with other contractors in the performance of contracts financed in whole, or in part, with funding through the United States Department of Transportation (USDOT). The Contractor or subcontractor shall not discriminate on the basis of race, color, national origin, or sex in the performance of this contract. The Contractor shall carry out applicable requirements of 49 CFR Part 26 in the award and administration of USDOT-assisted contracts.

120-1.2 INTERPRETATION. It is the intent of this section to implement the requirements of 49 CFR, Part 26, and the Department's federally approved DBE Program.

120-1.3 ESSENTIAL CONTRACT PROVISION. Failure to comply with the provisions of this section will be considered a material breach of contract, which may result in the termination of this contract or such other remedy as the Department deems appropriate. The Department also considers failure to comply with this section to be so serious as to justify debarment action as provided in AS 36.30.640(4).

120-1.4 DEFINITIONS AND TERMS. The following definitions will apply.

- Broker. A DBE certified by the Department that arranges for the delivery or provision of creditable materials, supplies, equipment, transportation/hauling, insurance, bonding, etc., within its certified category, that is necessary for the completion of the project. A broker of materials certified in a supply category must be responsible for scheduling the delivery of materials and fully responsible for ensuring that the materials meet specifications before credit will be given.

- Commercially Useful Function (CUF). The execution of the work of the Contract by a DBE carrying out its responsibilities by actually performing, managing, and supervising the work involved using its own employees and equipment. The DBE shall be responsible, with respect to materials and supplies used on the Contract, for negotiating price, determining quality and quantity, ordering the material, and installing (where applicable) and paying for the material itself. To determine whether a DBE is performing a commercially useful function, an evaluation of the amount of work subcontracted, industry practices, whether the amount the firm is to be paid under the Contract is commensurate with the work it is actually performing and the DBE credit claimed for its performance of the work. Other relevant factors will be considered. The determination of CUF is made by the Engineer after evaluating the way in which the work was performed during the execution of the Contract.

- Disadvantaged Business Enterprise (DBE). An enterprise which is a for-profit small business concern

- that is at least 51 percent owned by one or more individuals who are both socially and economically disadvantaged or, in the case of a corporation, in which 51 percent of the stock is owned by one or more such individuals;

- whose management and daily business operations are controlled by one or more of the socially and economically disadvantaged individuals who own it; and

- has been certified by the Department in accordance with 49 CFR, Part 26.

- DBE Key Employee. Permanent employees identified by the DBE owner in its certification file in the Department's Civil Rights Office (CRO).

- DBE Utilization Goal.The percent of work to be performed by certified DBEs that is established by the Department and specified in the Contract.

- Good Faith Efforts. Efforts by the bidder or Contractor to achieve a DBE goal or other requirement of 49 CFR Part 26, by their scope, intensity, and appropriateness to the objective, that can reasonably be expected to fulfill the program requirement.

- Manufacturer. A DBE certified by the Department in a supply category that changes the shape, form, or composition of original material in some way and then provides that altered material to the project and to the general public or the construction industry at large on a regular basis.

- Notification. For purposes of soliciting DBE participation on a project and to count toward a contractor’s Good Faith Efforts, notification shall be by letter or fax transmission, with a return receipt requested or successful transmission report. Telephonic contact with a DBE may be allowed, however it shall be based on the ability of the CRO to independently verify this contact.

- Regular Dealer. A DBE certified by the Department in a supply category that

- maintains an in-house inventory on a regular basis of the particular product provided to this project; and

- keeps an inventory in an amount appropriate for the type of work using that product; and

- offers that inventory for sale to the general public or construction industry at large (private and public sectors), not just supplied as needed on a project by project basis during the construction season, except where the product requires special or heavy equipment for delivery and the DBE possesses and operates this equipment on a regular basis throughout the construction season in order to deliver the product to the general public or construction industry at large. If the distribution equipment is rented or leased, it must be on a repetitive, seasonal basis; and may additionally

- fabricate (assembles large components) for use on a construction project, consistent with standard industry practice, for delivery to the project.

120-2.1 UTILIZATION GOAL. The DBE Utilization Goal for this contract is shown on Form 25A-324 (DBE Subcontractable Items) as a percentage of the total basic bid amount. A DBE may be considered creditable towards meeting the DBE Utilization Goal at time of Contract award, if the DBE is certified by the Department in a category covering the CUF to be performed at the time of listing on Form 25A-325C (DBE Utilization Report).

A bidder shall demonstrate the ability to meet the DBE Utilization Goal or perform and document all of the required Good Faith Efforts under Subsection 120-3.2 in order to be eligible for award of this Contract.

If the quantity of work of a bid item involving a DBE firm is reduced by the Department, the DBE Utilization Goal on Form 25A-325C will be reduced proportionately.

120-3.1 DETERMINATION OF COMPLIANCE.

- Phase I - Bid. Each bidder must register with the CRO annually in accordance with §§26.11 & 26.53(b)(2)(iv) of 49 CFR, Part 26. Use Form 25D-6. No contract may be awarded to a bidder that has not registered.

- Phase II - Award. The apparent low bidder will provide the following within 15 days of receipt of notice of intent to award:

- Written DBE Commitment. Written commitments from DBEs to be used on the project. The written commitment shall contain the following information:

- A description of the work that each DBE will perform;

- The dollar amount of participation by the DBE firm;

- Written documentation of the bidder/offeror’s commitment to use a DBE subcontractor whose participation it submits to meet a contract goal; and

- Written confirmation from the DBE that it is participating in the contract as provided in the prime Contractor’s commitment.

- DBE Utilization Report. Form 25A-325C listing the certified DBEs to be used to meet the DBE Utilization Goal.

- Good Faith Effort Documentation. Summary of Good Faith Effort Documentation (Form 25A-332A and attachments) and DBE Contact Reports (Form 25A-321A) if the Contractor submits less DBE utilization on Form 25A-325C than is required to meet the DBE Utilization Goal. If accepted by the Department, this lower DBE utilization becomes the new DBE Utilization Goal. If the bidder cannot demonstrate the ability to meet the DBE Utilization Goal, and can not document the minimum required Good Faith Efforts (as outlined in Subsection 120-3.2 below), the Contracting Officer will determine the bidder to be not responsible.

- Phase III - Construction.

- Designation of DBE/EEO Officer. At the preconstruction conference, the Contractor shall submit, in writing, the designation of a DBE/EEO officer.

- DBE Creditable Work. The CUF work items and creditable dollar amounts shown for a DBE on the DBE Utilization Report (Form 25A-325C) shall be included in any subcontract, purchase order or service agreement with that DBE.

- DBE Replacement. If a DBE replacement is approved by the Engineer, the Contractor shall replace the DBE with another DBE for the same work in order to fulfill its commitment under the DBE Utilization Goal. In the event that the Contractor cannot obtain replacement DBE participation, the Engineer may adjust the DBE Utilization Goal if, in the opinion of the Engineer and the CRO, both of the following criteria have been met:

- The Contractor has not committed any discriminatory practice in its exercise of good business judgement to replace a DBE.

- If the Contractor is unable to find replacement DBE participation and has adequately performed and documented the Good Faith Effort expended in accordance with Subsection 120-3.2.

- DBE Utilization Goal. The DBE Utilization Goal will be adjusted to reflect only that amount of the DBE's work that can not be replaced.

120-3.2 GOOD FAITH EFFORT.

- Good Faith Effort Criteria. The Contracting Officer will use the following criteria to judge if the bidder, who has not met the DBE Utilization Goal, has demonstrated sufficient Good Faith Effort to be eligible for award of the contract.

Failure by the bidder to perform and document all of the following actions constitutes insufficient Good Faith Effort.

- Consideration of all subcontractable items. The bidder shall, at a minimum, seek DBE participation for each of the subcontractable items upon which the DBE goal was established as identified by the Department (on Form 25A-324) prior to bid opening. It is the bidder’s responsibility to make the work listed on the subcontractable items list available to DBE firms, to facilitate DBE participation.

- If the bidder can not achieve the DBE Utilization Goal using the list of available DBE firms based on the subcontractable items list, then the bidder may consider other items that could be subcontracted to DBEs.

- Notification to all active DBEs listed for a given region in the Department's most current DBE Directory at least 7 calendar days prior to bid opening. The bidder must give the DBEs no less than five days to respond. The bidder may reject DBE quotes received after the deadline. Such a deadline for bid submission by DBEs will be consistently applied. DBEs certified to perform work items identified on Form 25A-324 must be contacted to solicit their interest in participating in the execution of work with the Contractor. Each contact with a DBE firm will be logged on a Contact Report (Form 25A-321A).

- Non-competitive DBE quotes may be rejected by the bidder. Allegations of non-competitive DBE quotes must be documented and verifiable. A DBE quote that is more than 10.0% higher than the accepted non-DBE quote will be deemed non-competitive, provided the DBE and non-DBE subcontractor quotes are for the exact same work or service. Bidders must have a non-DBE subcontractor quote for comparison purposes. Such evidence shall be provided in support of the bidder’s allegation. Where the bidder rejects a DBE quote as being non-competitive under this condition, the work must be performed by the non-DBE subcontractor and payments received by the non-DBE subcontractor during the execution of the Contract shall be consistent with the non-DBE's accepted quote. This does not preclude increases as a result of Change documents issued by the Department.

- Provision of assistance to DBEs who need help in obtaining information about bonding or insurance required by the bidder.

- Provision of assistance to DBEs who need help in obtaining information about securing equipment, supplies, materials, or related assistance or services.

- Providing prospective DBEs with adequate information about the requirements of the Contract regarding the specific item of work or service sought from the DBE.

- Follow-up of initial notifications by contacting DBEs to determine whether or not they will be bidding. Failure to submit a bid by the project bid opening or deadline by the bidder is de facto evidence of the DBE’s lack of interest in bidding. Documentation of follow-up contacts shall be logged on the Contact Report (Form 25A-321A).

- Items (3) through (8) will be utilized to evaluate any request from the Contractor for a reduction in the DBE Utilization Goal due to the default or decertification of a DBE and the Contractor's subsequent inability to obtain additional DBE participation.

- Administrative Reconsideration. Under the provisions of 49 CFR. Part 26.53(d), if it is determined that the apparent successful bidder has failed to meet the requirements of this subsection, the bidder must indicate whether they would like an opportunity for administrative reconsideration. Such an opportunity must be exercised by the bidder within 3 calendar days of notification it has failed to meet the requirements of this subsection. As part of this reconsideration, the bidder must provide written documentation or argument concerning the issue of whether it met the goal or made adequate good faith efforts to do so.

- The decision on reconsideration will be made by the DBE Liaison Officer.

- The bidder will have the opportunity to meet in person with the DBE Liaison Officer to discuss the issue of whether it met the goal or made adequate good faith efforts to do so. If a meeting is desired, the bidder must be ready, willing and able to meet with the DBE Liaison Officer within 4 days of notification that it has failed to meet the requirements of this subsection.

- The DBE Liaison Officer will render a written decision on reconsideration and provide notification to the bidder. The written decision will explain the basis for finding that the bidder did or did not meet the goal or make adequate good faith efforts to do so.

- The result of the reconsideration process is not administratively appealable to USDOT.

120-3.3 COMMERCIALLY USEFUL FUNCTION (CUF).

- Creditable Work. Measurement of attainment of the DBE Utilization Goal will be based upon the actual amount of money received by the DBEs for creditable CUF work on this project as determined by the Engineer in accordance with this Section. CUF is limited to that of a:

- regular dealer;

- manufacturer;

- broker;

- subcontractor;

- joint-venture; or

- prime contractor.

- Determination of Commercially Useful Function. In order for the CUF work of the DBE to be credited toward the goal, the Contractor will ensure that all of the following requirements are met:

- The CUF performed by a DBE certified in a supply category will be evaluated by the Engineer to determine whether the DBE performed as either a broker, regular dealer, or manufacturer of the product provided to this project.

- A DBE trucking firm certified and performing work in a transportation/hauling category is restricted to credit for work performed with its own trucks and personnel certified with the CRO prior to submitting a bid to a contractor for DBE trucking. The DBE trucking firm must demonstrate that it owns all trucks (proof of title and/or registration) to be credited for work and that all operators are employed by the DBE trucking firm. A DBE trucking firm that does not certify its trucks and personnel that it employs on a job will be considered a broker of trucking services and limited to credit for a broker. (This does not effect the CUF of that same firm, when performance includes the hauling of materials for that work.)

- The DBE is certified in the appropriate category at the time of

- the Engineer's approval of the DBE subcontract, consistent with the written DBE commitment; and

- the issuance of a purchase order or service agreement by the Contractor to a DBE performing as either a manufacturer, regular dealer, or broker (with a copy to the Engineer).

- The Contractor will receive credit for the CUF performed by DBEs as provided in this Section. Contractors are encouraged to contact the Engineer in advance of the execution of the DBE's work or provision of goods or services regarding CUF and potential DBE credit.

- The DBE may perform work in categories for which it is not certified, but only work performed in the DBE's certified category meeting the CUF criteria may be credited toward the DBE Utilization Goal.

- The work of the DBE firm must meet the following criteria when determining when CUF is being performed by the DBE:

- The work performed will be necessary and useful work required for the execution of the Contract.

- The scope of work will be distinct and identifiable with specific contract items of work, bonding, or insurance requirements.

- The work will be performed, controlled, managed, and supervised by employees normally employed by and under the control of the certified DBE. The work will be performed with the DBE’s own equipment. Either the DBE owner or DBE key employee will be at the work site and responsible for the work.

- The manner in which the work is sublet or performed will conform to standard, statewide industry practice within Alaska, as determined by the Department. The work or provision of goods or services will have a market outside of the DBE program (must also be performed by non-DBE firms within the Alaskan construction industry). Otherwise, the work or service will be deemed an unnecessary step in the contracting or purchasing process and no DBE credit will be allowed.

There will be no DBE credit for lower-tier non-DBE subcontract work.

- The cost of the goods and services will be reasonable and competitive with the cost of the goods and services outside the DBE program within Alaska. Materials or supplies needed as a regular course of the Contractor's operations such as fuel, maintenance, office facilities, portable bathrooms, etc. are not creditable.

The cost of materials actually incorporated into the project by a DBE subcontractor is creditable toward the DBE goal only if the DBE is responsible for ordering and scheduling the delivery of creditable materials and fully responsible for ensuring that the materials meet specifications.

- All subcontract work, with the exception of truck hauling, will be sublet by the same unit of measure as is contained in the Bid Schedule unless prior written approval of the Engineer is obtained.

- The DBE will control all business administration, accounting, billing, and payment transactions. The prime contractor will not perform the business, accounting, billing, and similar functions of the DBE. The Engineer may, in accordance with AS 36.30.420(b), inspect the offices of the DBE and audit the records of the DBE to assure compliance.

- On a monthly basis, the Contractor shall report on Form 25A-336 (Monthly Summary of DBE Participation) to the CRO the payments made (canceled checks or bank statements that identify payor, payee, and amount of transfer) for the qualifying work, goods and services provided by DBEs.

- Decertification of a DBE. Should a DBE performing a CUF become decertified during the term of the subcontract, purchase order, or service agreement for reasons beyond the control of and without the fault or negligence of the Contractor, the work remaining under the subcontract, purchase order, or service agreement may be credited toward the DBE Utilization Goal.

Should the DBE be decertified between the time of Contract award and the time of the Engineer's subcontract approval or issuance of a purchase order or service agreement, the work of the decertified firm will not be credited toward the DBE Utilization Goal. The Contractor must still meet the DBE Utilization Goal by either

- withdrawing the subcontract, purchase order or service agreement from the decertified DBE and expending Good Faith Effort (Subsection 120-3.2, Items (3) through (8) to replace it with one from a currently certified DBE for that same work or service through subcontractor substitution (GCP Subsection 30-01); or

- continuing with the subcontract, purchase order or service agreement with the decertified firm and expending Good Faith Effort to find other work not already subcontracted out to DBEs in an amount to meet the DBE Utilization Goal through either

- increasing the participation of other DBEs on the project;

- documenting Good Faith Efforts [Subsection 120-3.2, items (3) through (8)]; or

- by a combination of the above.

- DBE Rebuttal of a Finding of no CUF. Consistent with the provisions of 49 CFR, Part 26.55(c)(4)&(5), before the Engineer makes a final finding that no CUF has been performed by a DBE firm the Engineer will coordinate notification of the presumptive finding through the CRO to the Contractor, who will notify the DBE firm.

The Engineer, in cooperation with the CRO, may determine that the firm is performing a CUF if the rebuttal information convincingly demonstrates the type of work involved and normal industry practices establishes a CUF was performed by the DBE. Under no circumstances shall the Contractor take any action against the DBE firm until the Engineer has made a final determination. The Engineer’s decisions on CUF matters are not administratively appealable to USDOT.

120-3.4 DEFAULT OF DBE. In the event that a DBE firm under contract or to whom a purchase order or similar agreement has been issued defaults on their work for whatever reason, the Contractor shall immediately notify the Engineer of the default and the circumstances surrounding the default.

The Contractor shall take immediate steps, without any order or direction from the Engineer, to retain the services of other DBEs to perform the defaulted work. In the event that the Contractor cannot obtain replacement DBE participation, the Engineer may adjust the DBE Utilization Goal if, in the opinion of the Engineer, the following criteria have been met:

- The Contractor was not at fault or negligent in the default and that the circumstances surrounding the default were beyond the control of the Contractor; and

- The Contractor is unable to find replacement DBE participation at the same level of DBE commitment and has adequately performed and documented the Good Faith Effort expended in accordance with items (3) through (8) of Subsection 120-3.2 for the defaulted work; or

- It is too late in the project to provide any real subcontracting opportunities remaining for DBEs.

The DBE Utilization Goal will be adjusted to reflect only that amount of the defaulted DBE's work that can not be replaced.

120-4.1 METHOD OF MEASUREMENT. The Contractor will be entitled to count toward the DBE Utilization Goal those monies actually paid to certified DBEs for CUF work performed by the DBE as determined by the Engineer. The Contractor will receive credit for the utilization of the DBEs, as follows:

- Credit for the CUF of a DBE prime contractor is 100% of the monies actually paid to the DBE under the contract for creditable work and materials in accordance with 49 CFR 26.55.

- Credit for the CUF of a subcontractor is 100% of the monies actually paid to the DBE under the subcontract for creditable work and materials. This shall include DBE trucking firms certified as a subcontractor and not a broker. Trucks leased from another DBE firm shall also qualify for credit and conforms to the provisions of 49 CFR 26.55(d).

- Credit for the CUF of a manufacturer is 100% of the monies paid to the DBE for the creditable materials manufactured.

- Credit for the CUF of a regular dealer of a creditable material, product, or supply is 60% of its value. The value will be the actual cost paid to the DBE but will not exceed the bid price for the item.

- Credit for the CUF of a broker performed by a DBE certified in a supply category for providing a creditable material, product or supply is limited to a reasonable brokerage fee. The brokerage fee will not exceed 5% of the cost of the procurement contract for the creditable item.

- Credit for the CUF of a broker performed by a DBE certified in the transportation/hauling category for arranging for the delivery of a creditable material, product or supply is limited to a reasonable brokerage fee. The brokerage fee will not exceed 5% of the cost of the hauling subcontract.

- Credit for the CUF of a broker performed by a DBE certified in a bonding or insurance category for arranging for the provision of insurance or bonding is limited to a reasonable brokerage fee. The brokerage fee will not exceed 5% of the premium cost.

- Credit for the CUF of a joint venture (JV) (either as the prime contractor or as a subcontractor) may not exceed the percent of the DBE's participation in the joint venture agreement, as certified for this project by the Department. The DBE joint venture partner will be responsible for performing all of the work as delineated in the certified JV agreement.

120-5.1 BASIS OF PAYMENT. Work under this item is subsidiary to other contract items and no payment will be made for meeting or exceeding the DBE Utilization Goal.

If the Contractor fails to utilize the DBEs listed on Form 25A-325C as scheduled or fails to submit required documentation to verify proof of payment or documentation requested by the Department to help in the determination of CUF, the Department will consider this to be unsatisfactory work. If the Contractor fails to utilize Good Faith Efforts to replace a DBE, regardless of fault (except for Subsection 120-3.4 item c.), the Department will also consider this unsatisfactory work. Unsatisfactory work may result in disqualification of the Contractor from future bidding under GCP Subsection 20-13 and withholding of progress payments consistent with GCP Subsection 90-06.

ITEM G-130	SERVICES TO BE FURNISHED BY THE CONTRACTOR

DESCRIPTION

130-1.1 This work consists of furnishing and maintaining facilities specified in the Contract and listed in the bid schedule for the Department’s project administrative personnel to use during the project. Facilities must be fully usable for the specified service. Maintain facilities adequately to preserve their utility. Services include heat, electricity, water and any others required to operate the facility. All facilities remain your property when you complete the work. Locate the sites and acquire all permits required unless otherwise shown on the Plans or specified.

### REQUIREMENTS

130-2.1 FIELD OFFICE. Furnish and maintain a suitable office for the Engineer to use during construction. If this office is part of your building, completely partition it from the rest of the structure and provide a separate outside door equipped with a lock. Provide a suitable stove or other heating device with fuel. Furnish adequate electrical lighting and 120-volt, 60-cycle power. Construct the office with at least 500 ft2 of floor space and at least 60 ft2 of window area, along with adequate ventilation. Provide at least 12 linear feet of shelf space. Equip the field office with sanitary facilities. Provide janitorial services at least weekly. Furnish a telephone with a private line for the exclusive use of the Engineer. All long distance calls made by State personnel will be paid for by the State.

Provide at least one designated handicap parking space. Make the field office accessible according to the requirements of Americans with Disabilities Act Accessibility Guidelines (ADAAG).

Make the field office available for occupancy 2 weeks before commencing work on the project through one week after Project Completion.

130-2.2 FIELD LABORATORY. Furnish and maintain a field laboratory for the Engineer to use exclusively throughout the contract. Provide a completely functional installation 2 weeks before commencing construction work through one week after Project Completion.

- Site. Grade and compact a site for the lab acceptable to the Engineer. Locate and level the structure on this site. If subsequent ground movement causes an unlevel or unstable condition, re-level or re-locate the facility as directed.

- Main Lab. Provide a weatherproof structure suitable to field test construction materials, with the following minimum functional requirements:

- Floor space of 300 ft2.

- Two 10 ft2 windows that open and lock.

- Lockable door(s).

- Work bench(es), 30 inches X 16 feet total, 3 feet high.

- Shelf space, 12 inches X 16 feet.

- One 20-inch deep sink with attached faucet and approved drain.

- A gravity-fed 250-gallon tank or pressurized constant water supply of acceptable quality .

- Electrical service and facilities as follows:

- Electrical current, 120/240 V (ac), 60-cycle on 24-hour basis.

- Wiring system to support a 40-amp user load demand. At least one 15-amp and one 20-amp circuit, both GFI protected.

- Outlets, 6 conveniently spaced around the lab, consistent with local codes.

- Lights, four 100-watt incandescent or eight 40-watt fluorescent.

- Exhaust fan, 5 cfs.

- Heating equipment suitable to maintain a uniform 70 ºF room temperature.

- Storage cabinet, 3 ft X 3 ft X 3 ft, lockable, securely fixed to an inside wall with a hinged door opening outward.

- Office desk and 2 chairs.

If the lab is a mobile unit mounted on axles and wheels, block the structure under the frame so that the wheels do not touch the ground and the blocking rests firmly on the prepared site.

- Auxiliary Lab. Provide a separate weatherproof shed within 20 feet of the main lab structure with the following minimum functional requirements:

- Floor 8 ft X 12 ft, ceiling height 8 ft.

- Door 48 inches wide and window 5 ft2 that opens, both lockable.

- Electrical service and facilities as in b.(8), except for the following:

- Lighting fixtures, 2 ea.

- Outlets, 3 conveniently spaced around the structure.

- Wiring system with each circuit GFI protected to satisfy a 20-amp user load demand.

- Work table 3 ft X 20 in X 3 ft high, capable of supporting 250 pounds and affixed to an inside wall as directed.

- Concrete-slab floor, 8 ft X 8 ft X 4 inches thick, cast-in-place or pre-cast. Install anchor bolts in the floor to accommodate the mounting pattern of the Gilson sieving machine at a location as directed.

- Comply with a. above for slab foundation requirements.

- Found the slab directly on the prepared site.

- Access. For all types of installations, if the entryway is located higher than a single 7-inch rise, provide the following:

- Stairway, 36-inch width X 11-inch tread X 7-inch rise.

- Landing, 4 ft X 4 ft centered on the entryway.

- Handrail(s) firmly affixed to the stairway.

- Lab Equipment and Services. Provide the following:

- Propane necessary for the lab operation, including two 100-lb tanks, regulators, hoses, fittings, and incidentals for a functional system.

- Specialized sampling equipment such as belt templates or belt sampling devices as required.

- Fuel and power necessary to continuously operate the facilities.

130-2.3 CURING SHED. Furnish and maintain a suitable weather tight shed for curing concrete test cylinders, with a suitable box or bins for curing concrete test cylinders.

Provide a box large enough or enough bins to contain at least 6 test cylinders from each pour that the Contractor proposes to make during any 28-day period. Use a box or bins at least 18 inches high and constructed of sturdy wood. Line the box or bins with a canvas or plastic liner to help retain moisture in the sand. Construct a lid to provide access to the box or bins.

Provide suitable heating to maintain the temperature in the box (or shed) between 60 and 80 °F at all times when curing the test cylinders. In addition, provide a suitable room thermometer in the shed to check the temperature.

Provide enough sand at the shed to fill the box or bins to be used for curing and enough water to keep the sand in the box or bins moist during the curing period.

130-2.4 CAMP FACILITIES. Furnish and maintain suitable camp facilities for Department employees and other authorized personnel. The Special Provisions will list an estimated number of employees.

Provide the following camp facilities:

- Lodging (Bunkhouse and Bedding)

- Meals (Mess Hall and Kitchen)

- Sanitary and Other Facilities

Provide all camp facilities according to the applicable chapters of the State of Alaska Department of Labor, Occupational and Industrial Structures Code, and the State of Alaska Department of Environmental Conservation, Food Service Regulations.

Camp facilities for your employees, that meet these requirements, may also be used for State employees.

These Specifications do not exclude the use of roadhouses or lodges located near the project that are available for your use. The Engineer may approve a roadhouse, lodge, or camp, providing the accommodations conform with contract requirements.

Provide camp facilities for use by State employees and other authorized personnel while you are engaged in work at the project site, or in material sources used to supply materials to this project.

Department employees and other authorized personnel must sign a meal and/or lodging sheet after each meal and each night's lodging.

When you use camp facilities, completely remove and dispose of all garbage and/or trash piles, cesspools, septic tanks and leach fields as required by applicable laws and regulations and as directed.

130-2.5 SCALES. When the bid schedule calls for payment for material by weight, other than the barge displacement method, provide one of the following:

- Commercial weighing system. Permanently installed commercial scales.

- Project weighing system. Acceptable automatic digital scales and scale house.

Provide scales that record weight at least to the nearest 100 pounds. Maintain scale accuracy to within 0.5% of the correct weight throughout the range of use.

Do not use spring balances.

Do not use belt conveyor scales to determine pay weight. You may use belt conveyor scales to proportion plant blends and mixtures if the scales meet the general requirements for weighing equipment and are calibrated according to the manufacturer’s instructions.

You may use batch weights to determine pay quantities when the batching equipment includes an approved and certified automatic weighing, cycling, and monitoring system.

Install and maintain platform scales with the platform level and rigid bulkheads at each end. Use a platform long enough to permit simultaneous weighing of all axle loads of the hauling vehicle, including coupled vehicles.

Maintain the accuracy of scales according to the specifications, tolerances and regulations for commercial weighing and measuring devices contained in the National Bureau of Standards, Handbook 44, as adopted by Alaska Statute, Section 45.75.050.(d). All commercial scales are subject to approval according to the Weights and Measures Act, AS 45.75. Have scales reinspected, as directed, to ensure their accuracy, and sealed to prevent tampering or other adjustment after certification.

Provide a weatherproof housing for platform scales to protect the recording equipment and allow the scale operator convenient access to the weigh indicator, scale computer, ticket printer, and the sequential printer. Furnish sanitary lavatory facilities, heating, adequate electrical lighting and 120-volt, 60-cycle power for the scale house.

Furnish competent scale operators to operate the system.

Weighing System: Provide an electronic computerized weighing system (ECWS) with the following capabilities:

- Computer.

- Provide a scale computer that can store project numbers and all pay item descriptions for multiple projects and products that are weighed with the scale system.

Use a computer with a self-reading scale system that includes the scale load cell, a sealed direct reading weight indicator, scale computer, ticket printer, and sequential printer, and can record a complete shift’s transaction on a 3.5-inch high-density diskette or other approved storage media.

- The scale computer must store the following for each hauling vehicle used on the project:

- Vehicle identification number marked on the vehicle

- Tare weight

- Maximum allowable gross vehicle weight (MAVW)

Make sure the scale operator tares vehicles at least once a day. Perform additional tares, as directed, during hauling operations. Perform tares in the presence of the Engineer, when requested.

The Engineer will calculate the MAVW for each vehicle and list all vehicles and their MAVW(s) in the scale house. The MAVW is either the maximum allowable legal weight determined by the Engineer when you cannot haul overloads in the traffic stream, or the manufacturer’s recommended maximum allowable gross vehicle weight as certified by the Contractor when vehicles are allowed to haul overloads.

The scale operator should only use MAVWs that the Engineer has provided in writing. Do not issue any tickets to a vehicle until the Engineer provides the MAVW.

- During weighing operations, the ECWS should compare each vehicle’s gross weight to its MAVW. If the vehicle exceeds its MAVW, the system must alert the scale operator that an “overload” exists. The system should not issue a ticket.

- Provide a battery backup for the computer and protection for power surges or brown outs. The computer system must retain all stored data during a power outage and must operate during a power outage to allow you to shut down the hard drive without losing information.

- Tickets. Furnish a ticket printer that prints a legible, serially numbered weigh ticket for the Engineer with the following information on each ticket in the order listed. All weights must be at least to the nearest 100 pounds:

- Project number

- Item number and description

- Date weighed

- Time weighed

- Ticket number

- Vehicle Identification Number

- MAVW

- Gross weight

- Tare weight

- Net weight

- Subtotal item net weight for each haul unit since start of shift

- Accumulated item net weight for all haul units since start of shift

After printing, the weigh ticket must automatically advance to a perforation so it can be torn off and handed to the driver.

Manually weigh and record weights for up to 48 hours during a printer malfunction or break-down, when the Engineer gives you prior written authorization. The manual weighing operation must meet all other contract requirements.

Unless the Engineer gives prior written authorization, you will not receive payment for any material weighed without using the ECWS.

- Sequential Printer. Provide a sequential printer that prints out all transactions (keystrokes) made by the computer concurrently with the ticket printer. For permanent commercial scales, the printer may print at the end of the company’s daily shift with the Engineer’s approval. The printer must print all scales transactions including tares, voided tickets, and data changes made by the scale operator. The printer must allow for advancing the paper manually so that the scale operator can write notes on the paper when special situations occur, such as voided tickets, incorrect vehicle identification number used, etc. The scale operator should also note these special situations in the Scales Diary.

Submit the printout to the Engineer at the end of each shift. You will not receive payment for any hauled material until the printout is submitted.

- Data Diskettes. Provide the Engineer with a 3.5-inch high-density diskette or other approved storage media at the end of the shift. Record all ticket information produced during the shift. Store data in an approved format.

Download data from the permanent commercial vendor scale computer hard drive directly to a disk at the end of the shift. Do not convert or manipulate data. Provide conversion programs and training so that you can convert data into the information the Engineer requires.

If the diskette is not completely usable, then correct, construct, or reconstruct the data file. Use the sequential printout or other information as a data source, as directed. You will not receive payment for hauled material on a given date until you deliver an accurate “daily” data file to the Engineer. If the Engineer gives you written permission to weigh without the ECWS for a minor equipment failure, construct an acceptable data file as described above.

- Scale Diary. The Scale Diary is a computer printout or bound book provided by the Engineer. The scale person must complete the Scale Diary and include the following information: dates of action, type of material, source, time the scale opened and time the scale closed, times of scale balance, ticket sequence, time the haul for each material started and stopped, voided ticket numbers, vehicle identification numbers, times of tare and tare weights, and the scale person’s signature. Also include the following information on any scale used to weigh materials for payment:

- Owner of the scales and scale locations.

- Manufacturer’s name, model serial number, maximum capacity, and type of scales (single beam, double beam, self-reading, etc.).

- Date(s) the scales were installed and/or adjusted.

- Scale service company inspections and accuracy checks (attach copy).

- Division of Measurement Standards inspections and accuracy checks (attach copy).

- Time and dates of notification of any malfunctions.

The Scale Diary remains the Engineer’s property.

Submit the Scale Diary to the Engineer at the end of each shift. You will not receive payment for any hauled material until you deliver the Scale Diary to the Engineer.

The system must generate a report, either during or at the end of the day or shift, that summarizes the number of loads and total net weight for each date, project, and product. Submit the original report at the end of each shift.

You will not receive payment for any material hauled in a vehicle that does not conform to the requirements of Subsection 50-12, Load Restrictions, and this Subsection. Dump material from non-conforming vehicles until they conform, then reweigh the vehicles.

When a weighing device indicates less than true weight, you will not receive additional payment for material previously weighed and recorded. When a weighing device indicates more than true weight, all material received after the last previously correct weighing accuracy test will be reduced by the percentage of error that exceeds 0.5%.

If the Engineer incurs extra construction engineering expenses from checking non-machine data entries or other data irregularities, the total value of those expenses will be deducted from the value of the contract item before payment.

Platform scales, scale house and the ECWS remain your property after you complete the work.

### METHOD OF MEASUREMENT

130-3.1 Meal. By each meal served to authorized personnel, based on signed meal sheets.

130-3.2 Lodging. By each night's lodging received by authorized personnel based on signed lodging sheets.

### BASIS OF PAYMENT

130-4.1 Lump Sum Items. Payment for Items G-130a, G-130b and G-130c will be made as follows:

- A percentage of the lump sum amount, to be determined by the Engineer, will be paid as full compensation for furnishing the facility at the site.

- The balance of the lump sum amount will be prorated over the anticipated active construction period with a portion included as part of each interim payment, for maintenance, repairs, providing all utilities, and for removing it from the site. If anticipated construction period changes, the final increment will be held until final payment.

130-4.2 Meal. Includes all labor, materials, tools, equipment and supplies required to provide meals to all authorized personnel assigned to, or associated with, the project.

130-4.3 Lodging. Includes all labor, materials, tools, equipment and supplies required to provide lodging for all authorized personnel assigned to, or associated with, the project.

Furnishing the following is subsidiary: platform scales, scale operators, tickets, scale house, and the ECWS, including all supplies such as weigh tickets, paper, printer ribbons, diskettes, etc., and all maintenance and repair services necessary to keep the system functional.

Payment will be made under:

Item G-130a 	Field Office - per lump sum

Item G-130b 	Field Laboratory - per lump sum

Item G-130c 	Curing Shed - per lump sum

Item G-130d 	Meal - per each

Item G-130e 	Lodging - per each

ITEM G-131	ENGINEERING TRANSPORTATION

# DESCRIPTION

131-1.1 Furnish and maintain vehicles for the exclusive use of the Engineer and his staff throughout the duration of the project.

# REQUIREMENT

131-2.1 Provide the specified number of the following vehicle types:

- Truck. Full-size four wheel drive pickup or sport utility vehicle. Less than 3 model years old, in good condition and with less than 36,000 miles on the odometer. Equip vehicles with strobe beacons (Whelen 360 or equivalent) and two-way radios set on the airport CTAF (Common Traffic Advisory Frequency).

- ATV. All-terrain vehicle, 4x4, 300 cc minimum, with a 500-lb capacity trailer.

- Snowmachine. 440 cc minimum with a 500-lb capacity sled.

Furnish all fuels and maintenance.

The Contractor is responsible for normal wear and tear, and any other incidental damage, including broken windshields, that might arise during the Departments operation and use.

The Department is responsible for physical damage to any vehicle provided under this section if proximately caused by its negligent operation.

Obtain the Engineer’s approval of vehicles prior to their shipment to the site.

Vehicles remain the property of the Contractor and shall be removed from the site following the completion of the work.

# METHOD OF MEASUREMENT

131-3.1 Engineering transportation will not be measured for payment.

## BASIS OF PAYMENT

131-4.1 Payment will be made as follows:

- A percentage of the lump sum amount, to be determined by the Engineer, will be paid as full compensation for furnishing the vehicles at the site.

- The balance of the lump sum amount will be prorated over the anticipated active construction period, with a portion included as part of each interim payment, for maintenance, fuel and repairs, and for removing vehicles from the site. If the anticipated construction period changes, the final increment will be held until final payment.

Payment will be made under:

Item G-131a	Engineering Transportation - per lump sum

ITEM G-135	CONSTRUCTION SURVEYING AND MONUMENTS

DESCRIPTION

135-1.1 GENERAL. Perform all surveying and staking essential for the completion of the project and perform the necessary calculations required to accomplish the work in conformance with the Plans and Specifications and standard survey and engineering practices.

Furnish and install survey monuments and monument cases in conformance with the Plans or as directed.

135-1.2 DEFINITIONS.

- Monument: A fixed physical object marking a point on the surface of the earth; used to commence or control a survey; mark the boundaries of a parcel of land; or the centerline of a right-of-way corridor. Monuments will be Primary or Secondary, as shown on the Plans.

- Point: Any identified spot located on the surface of the earth. For purposes of this definition, a point can be a PK nail, wooden hub, rebar, large nail or any other structure capable of being utilized as a marker.

- Witness Corner: A material mark or point usually placed on a property or survey line, at a known distance from a property corner or other survey point. A witness corner is employed to witness the location of a corner/point that cannot be monumented at its true location.

- Reference Monument: A material mark or point placed at a known distance and direction from a property corner or other survey point, usually not on a property or survey line. A reference monument is employed to perpetuate a corner/point that cannot be monumented at its true location or where the corner monument is subject to destruction.

- Surveyor: The Contractor’s Professional Land Surveyor, currently registered in the State of Alaska.

# MATERIALS

135-2.1 Monument Cases. Castings shall conform to AASHTO M 105, Class 30A. Castings shall be coated with a bituminous damp-proof coating. Bolting tops shall be used.

135-2.2 Primary Monument. A minimum 2-inch diameter nonferrous pipe at least 30 inches long, with a minimum 4-inch flange at the bottom and having magnets attached at the top and bottom. A minimum 2-1/4-inch diameter nonferrous metal cap must be permanently attached to the top. Mark the cap around the outside edge with the words “STATE OF ALASKA DOT&PF". Permanently stamp every monument with the Surveyor’s registration number, the year set, and the point/corner identification. Orient cap so that the data may be read facing up-station.

135-2.3 Secondary Monument. A minimum 5/8-inch x 30-inch rebar with a 2-inch aluminum cap attached to the top. Permanently stamp every secondary monument with the Surveyor’s registration number and the year set.

CONSTRUCTION REQUIREMENTS

135-3.1 GENERAL. Use competent, qualified personnel and suitable equipment for the layout work required and furnish all traffic control, stakes, templates, straight-edges and other devices necessary for establishing, checking and maintaining the required points, lines and grades.

Furnish such computer services as necessary to accomplish the work. Check all data received from the computer for completeness and accuracy. As soon as practical after completion of the work, and in no case later than acceptance of the project, deliver all field books, computer forms and computer output data to the Engineer. This data becomes the property of the Department.

Supervise construction surveying personnel. Correct any errors resulting from the operations of said personnel at Contractor expense. The Contractor is responsible for the accuracy of the work.

Work classified as Land Surveying under AS 08.48, and work involving the location, control, and monumentation of construction centerline and right-of-way, shall be performed by or under the responsible charge of a Professional Land Surveyor.

Follow the Department’s Construction Surveying Requirements.

The Department will provide sufficient centerline or reference thereto, and at least one benchmark to enable the establishment of planned elevations and centerline.

Keep field notes in standard bound notebooks in a clear, orderly, and neat manner consistent with Departmental procedures, including titles, numbering, and indexing. Make field books available for inspection by the Engineer’s project personnel at any time. Legible copies of the reduced field notes shall be made daily. Store the field books in the Engineer’s Project Office during periods of non-use. Copies of the field books shall be kept in a separate secure location.

Perform the following:

- Staking necessary to delineate clearing and/or grubbing limits.

- Cross sections necessary for determination of excavation and embankment quantities, including intermediate and/or remeasure cross sections as needed. Take cross sections after clearing and grubbing has been completed.

- Slope staking.

- Staking of signs, culverts, minor drainage structures and other appurtenances, including the necessary checking to establish the proper location and grade to best fit the conditions on site.

- Bridge staking.

- Setting finishing stakes, as required.

- Measurement of pay quantities that require measurement.

- Staking of right-of-way and material source limits as deemed necessary.

- Staking, referencing and other actions required to preserve or restore land monuments and property corners.

- All other surveying and staking necessary to complete the project.

Notify the Engineer immediately if a Department-established reference point is discovered to be in error or a reset point is not in harmonious relationship to the adjacent centerline points.

Furnish a notekeeper to record all field survey notes, including those which become documentation from which quantities for payment are computed. The notekeeper shall be thoroughly familiar with generally accepted standards of good survey notekeeping practice and the Department’s Construction Surveying Requirements.

The Engineer may randomly spot check the Contractor's surveys, staking, and computations. After the survey or staking has been completed, provide the Engineer with a minimum of 72 hours notice prior to performing any work, and furnish the appropriate data as required, to allow for such random spot checking. The Department assumes no responsibility for the accuracy of the work.

135-3.2 CROSS-SECTION SURVEYS. When required, obtain right-angle cross sections to the construction centerline at the interval detailed in the Department’s Construction Surveying Requirements.

The following will be supplied by the Department:

- Construction Plans and Specifications.

- Design Cross Sections, if any.

- State of Alaska Land Survey Monument Record forms.

- Department’s Construction Surveying Requirements. One copy.

- Design centerline grades.

The following shall be required of the Contractor:

- Field Books (Level, Cross-Section, Slope Stake, etc. ). “Rite-in-the-Rain” or similar weather resistant books. Field books become the property of the Department upon completion of the work.

- Label the books and number the pages. Make a heading in the appropriate book (date, weather, names and duties of crew members) at the beginning of each day's work.

- The notekeeper shall update the index of the appropriate book at the end of each day's work.

- Level notes shall be reduced, checked and adjusted.

- Cross-section level notes and slope stake catches shall be computed by the notekeeper and checked by a different crew member in the field on a continual basis.

- Enter the grade data, shoulder width and/or ditch distance, stationing, slope, etc., in the slope stake books.

- Maintain the position and identifying marks of slope stakes and reference points until used for their intended purpose.

- Errors shall have a line drawn through them with the correct entry made directly above. Erasures will not be allowed.

- Return field books and copies of the field books to the Project office at the end of each work day or as directed.

- Provide copies of all grade sheets and temporary bench mark elevations to the Engineer 48 hours before commencing work on unclassified excavation or embankment.

- The Contractor’s survey crews shall comply with all approved traffic control plans.

- A survey Party Chief diary shall be kept daily and contain the following information, (a copy shall be given to the Engineer daily):

- Date.

- Weather.

- Crew members’ names and duties.

- Type and location of work performed.

- Hours worked.

- Type of equipment used (brand) and date equipment was double centered or “peg” test was performed.

- Signature of person in responsible charge.

- Submit the survey field notes, for any specific area, relating to monument referencing, prior to any initiation of clearing, grubbing or excavation.

135-3.3 MONUMENTS. Install primary and secondary monuments, as called for in the Plans, at the positions established by the Department. Reference all monuments, property markers/corners, or accessories which may be disturbed or buried during construction, and re-establish them in their original position prior to the completion of the project. Keep such records and report to the Engineer evidence that a monument has been disturbed and is no longer reliable or cannot be located and is presumed to be missing. The referencing work shall consist of a minimum of two in-line reference points, or three swing-tie reference points in situations where in-line referencing is not desirable. Set all reference points outside of the construction limits. Measure distances from the monument to the nearest 0.01 foot. Record all referencing of monuments in a separate field book stamped by the Surveyor.

Replace all existing monuments disturbed by construction with Primary or Secondary Monuments meeting the requirements of Subsections 135-2.1 through 3. When it is impractical to establish a monument in its original position, install a witness corner (WC). Place the WC to a property corner on the property line when the other property corner which defines said line is existing or there has been sufficient retracement to define said line. In other cases, place a reference monument (RM) perpendicular to the centerline at the station of the original position and at a distance from the original position measured in whole feet.

Those monuments found that are not shown on the Plans will be recognized by the Engineer when the following is provided by the Surveyor: Field notes identifying type and location of the monument, and a description of the point the monument marks, with the reason to preserve its location. Monuments not shown on the Plans will be considered additional work and paid by Item G-135b, Three Person Survey Party.

The Surveyor shall complete a State of Alaska Land Survey Monument Record form for each primary and secondary monument installed, relocated or replaced. In addition to the required survey information, including section, township and range, each record shall meet all requirements for recording at the District Recorder’s Office in which the project is located. Deliver these forms to the Engineer prior to project completion. The Department will file all original records as required by current State Statutes using the information provided by the Contractor.

Set each monument and monument case accurately to lines established at the required location and in such a manner as to insure its being held firmly in place. Set existing monuments and monument cases to be adjusted to new elevations in the manner and at the elevations directed.

135-3.4 OFFICE ENGINEERING. Calculate finish grades for the embankments as specified per Plans and/or Specifications. Use information available in the field, on as-builts, or as provided by the Engineer. This work shall be performed by or under the responsible charge of a Professional Land Surveyor or a Professional Engineer currently Registered in the State of Alaska.

135-3.5 FINAL TRAVERSE. Within 30 days after the Engineer receives from the Contractor a letter which states that all construction activities that may disturb the monuments have ceased, the Surveyor shall run a final closed traverse to verify the positional accuracy of installed survey monuments. Tie into the traverse the primary and secondary monuments placed or replaced and any undisturbed Department-provided control points. Meet the requirements of a secondary monument for all traverse points established during this work. The Surveyor shall sign and stamp a letter which lists each monument and its coordinates. The letter shall certify that the monuments are each located within 0.1 foot of their proposed position based on the project survey control points provided by the Department. Deliver the certification letter and field notes for this work to the Engineer.

METHOD OF MEASUREMENT

135-4.1 Construction Surveying. No measurement of quantities will be made.

135-4.2 Three Person Survey Party. By the hour for extra, additional, or unanticipated work made necessary by changes in the project, as directed.

If staking for extra, additional or unanticipated work, as stated above, is performed by a two person survey party, measurement will be made at 75% of the hours worked and paid under Item G-135b, Three Person Survey Party. If a single person is required for additional office computations or other work requiring only one person, payment will be made at 32% of the hours worked and paid under Item G-135b.

Calculations of all pay quantities will be performed by Department personnel.

135-4.3 Monuments. No measurement of quantities will be made.

BASIS OF PAYMENT

135-5.1 Construction surveying and monuments by the Contractor as specified in the bid schedule includes all necessary personnel, equipment, transportation, and supplies to accomplish the work.

Payment will be made under:

Item G-135a 	Construction Surveying by the Contractor - per lump sum

Item G-135b 	Three-Person Survey Party - per hour

Item G-135c 	Monuments by the Contractor - per lump sum

G-150	 EQUIPMENT RENTAL

DESCRIPTION

150-1.1 This item consists of furnishing construction equipment, operated, fueled and maintained, on a rental basis for use in construction of the proposed improvements and in performing work incidental to construction at the direction of the Engineer as such work is generally defined in these Plans and Specifications. Construction equipment is defined as that equipment actually used for performing the items of work specified and shall not include support equipment such as, but not limited to, hand tools, power tools, electric power generators, welders, small air compressors and other shop equipment needed for maintenance of the construction equipment.

# REQUIREMENTS

150-2.1 EQUIPMENT FURNISHED. The construction equipment to be provided under this contract shall be that shown in the Special Provisions supplemented by such non-rental maintenance equipment and support equipment as the Contractor elects to provide. The equipment shall be of modern design and in good working condition and shall be maintained in good working condition throughout the life of the project. All equipment to be used in the construction of this project as noted in the Bid Schedule shall be made available for inspection by the Engineer prior to its shipment to the project site. Each item of equipment shall have company numbers clearly displayed for ready identification. The Engineer shall have the authority to prohibit the use of rental payment for any equipment which is not maintained in good working condition or which has a production capacity below construction industry standards.

150-2.2 EQUIPMENT OPERATORS. Equipment operators shall be competent and experienced and shall be capable of operating the equipment to its capacity. The Contractor shall replace those operators who, in the opinion of the Engineer, misconduct themselves, either on the job or in the community, or are incompetent or negligent in the operation of the equipment.

150-2.3 HOURS OF OPERATION AND TIMEKEEPING. The Engineer shall begin recording time for payment each shift when the equipment begins work on the project. Time during which the equipment is being serviced or repaired shall not be included. The stated equipment rental rates shall apply only to that time during which the equipment is actively engaged in construction, as directed by the Engineer. No standby payment will be made for any piece of equipment prior to, during the life of, or after the project has been completed. "Stuck Time" payment shall be made for each piece of equipment that becomes stuck while actively engaged in construction work on the airport and shall be limited to 1 hour per shift for each piece of equipment that becomes stuck.

150-2.4 CONSTRUCTION METHODS. The work shall be constructed in accordance with the Plans, Special Provisions and as directed by the Engineer.

## METHOD OF MEASUREMENT

150-3.1 The serial number and brief description of each item of equipment listed in the bid schedule will be recorded by the Engineer, and he will record the number of hours, or fractions thereof to the nearest one-quarter hour, during which the equipment is actively engaged in construction of the project. The furnishing and operating of equipment of heavier type, larger capacity, or higher horsepower than specified will not entitle the Contractor to any extra compensation over his applicable contract unit price. Each day's activity will be recorded on a separate sheet or sheets, which shall be verified and signed by the Contractor's representative at the end of each shift, and a copy will be provided to the Contractor's representative. No idle time will be recorded unless authorized by the Engineer.

### BASIS OF PAYMENT

150-4.1 Payment will be made at the contract unit price bid for equipment rental per hour. This payment shall be full compensation for all fuel, operator's and mechanic's wages, parts, tools, maintenance items, shop equipment, camp, camp personnel wages, and all other incidentals necessary to keep the equipment in good condition and available for work on the project. No payment for equipment standby time resulting from unfavorable weather, or any other reason, is implied or intended and no payment therefore will be made by the Department. No payment will be made separately or directly for embankments.

Payment will be made under:

#### Item G-150a	Equipment Rental - per hour

APPENDIX

| Excavation P-152 | Acceptance | (5) | Gradation, P.I. (4), Moisture (or visual organic content) | 1 per 5,000 yd3 undesignated waste | Minimum of 1 gradation, P.I., and moisture content per undesignated waste cut is necessary. |
| --- | --- | --- | --- | --- | --- |
|  | Independent Assurance | (5) | Gradation, P.I., Moisture (or visual organic content) | 1 per 50,000 yd3 undesignated waste |  |
| Embankment P-152 | Acceptance | (5) | Standard Density | As required by changes in material | Number consecutively SM-SD-1 |
|  |  |  | Field Density (1) | 1 per 3,000 tons (1,500 yd3) | Number consecutively SM-D-1 |
|  |  |  | Gradation , P.I. (4), Deleterious (visual) | 1 per 10,000 tons (5,000 yd3) | Number consecutively SM-G-1 |
|  | Independent Assurance | (5) | Standard Density (2) | 1 per source | Numbers correspond to acceptance samples |
|  |  |  | Field Density | 1 per 30,000 tons (15,000 yd3) |  |
|  |  |  | Gradation, P.I., Deleterious (visual) | 1 per 100,000 tons (50,000 yd3) |  |
| Bedding & Backfill for Structures: Foundation Fill and Filter Material D-701, D-702, D-705, D-751, D-752, D-754 | Acceptance | (5) | Standard Density | As required by changes in material |  |
|  |  |  | Field Density (1) | See Note (3) |  |
|  |  |  | Gradation, P.I. (4), Deleterious (visual) | 1 per source or 1 per 500 feet of pipe |  |
| GENERAL: When the Regional Laboratory performs Acceptance Testing, Independent Assurance Testing may also be performed by the Regional Laboratory provided other personnel and other equipment are used to perform these tests. Material containing more than 40% + 3/4 inch may be impractical to test for field density. If after running a field test on material it is determined impractical to test for field density, then the proctor and the results of the field density gradation will be documented for each different type of material. Quantity and/or area represented, percent + 3/4 inch, and compactive effort used will also be documented on a proper regional density acceptance form. Required when Standard Density test is run in the field. Submit copy of the field worksheet with the sample. One density per concrete structure (manhole, catch basin, inlet, utility vault, abutments, etc.) or pipe and minimum of one density per 100 linear feet of pipe (ie. water, sewer, culvert, etc.) installed. Take pipe densities within 18 inches of the outside diameter of the pipe. Run P.I. tests on the first 5 samples at the start of production from any source. If these tests indicate the material to be nonplastic, additional tests need only be performed on the assurance samples. Size of sample for gradation determined by nominal maximum particle size. See WAQTC FOP for AASHTO T 27 and T 11 for minimum sample size. |

| Subbase P-154 | Acceptance | 50 lbs. | Standard Density | 1 per source and as required based on changes in material | Number consecutively SB-SD-1 |
| --- | --- | --- | --- | --- | --- |
|  |  |  | Field Density (1) | 1 per 2,000 tons (1,000 yd3) | Number consecutively SB-D-1 |
|  |  |  | Gradation, P.I. (3) | 1 per 5,000 tons (2,500 yd3) | Number consecutively SB-G-1 |
|  | Independent Assurance | 50 lbs. | Standard Density (2) | 1 per source | Numbers correspond to Acceptance samples |
|  |  |  | Field Density | 1 per 20,000 tons (10,000 yd3) |  |
|  |  |  | Gradation, P.I. | 1 per 50,000 tons (25,000 yd3) |  |
| Crushed Aggregate Base and Surface Course P-208 P-209 | Quality | 50 lbs. | Wear, degradation, soundness | 1 per source prior to use | Allow minimum of 14 days for testing and transport |
|  | Acceptance | 50 lbs. | Standard Density | As required by changes in material | Number consecutively BC-SD-1 |
|  |  |  | Field Density | 1 per 1,000 tons (500 yd3) | Number consecutively BC-D-1 |
|  |  |  | Gradation, Fracture (4), P.I. (3), Sand Equivalent (3) | 1 per 2,000 tons (1,000 yd3) | Number consecutively BC-G-1 |
|  |  |  | Thickness | P-209: 1 per 500 yd2 | Number consecutively BC-TH-1 |
|  | Independent Assurance | 50 lbs. | Standard Density (2) | 1 per source | Numbers correspond to Acceptance samples |
|  |  |  | Field Density | 1 per 10,000 tons (5,000 yd3) |  |
|  |  |  | Gradation, P.I., Fracture, Sand Equivalent | 1 per 20,000 tons (10,000 yd3) |  |
|  |  |  | Thickness | P-209: 1 per 5,000 yd2 |  |
| Material containing more than 40% + 3/4 inch may be impractical to test for field density. If after running a field test on material it is determined impractical to test for field density, then the proctor and the results of the field density gradation will be documented for each different type of material. Quantity and/or area represented, percent + 3/4 inch, and compactive effort used will also be documented on a proper regional density acceptance form. Required when Standard Density is run in the field. Submit copy of the field worksheet with the sample. Run tests on the first five samples at the start of production from any source. If these tests indicate the material meets specifications, additional tests need only be performed on the assurance samples. Run fracture tests on the first ten samples at the start of production and after each change in material. If these tests indicate the fracture to be 5% or more above specification, additional tests need only be performed on the assurance samples. |

| Hot Asphalt Pavement P-401 | Quality | 100 lbs. Aggregate | Wear, degradation, soundness, (1) | 1 per source prior use | Allow 25 days for testing and transport |
| --- | --- | --- | --- | --- | --- |
|  | Mix Design | 125 lbs. Aggregate | Gradation | 1 per source | Allow 15 days for design and testing after receiving contractor’s proposed gradation |
|  |  | 3 gal. of AC | 1/2 pint of Anti Strip |  |  |
|  | Acceptance | (4) | Mat Density, Joint Density, Gradation, Oil Content, P.I. (2), Fracture (3), Flat & Elongated (3), Sand Equivalent (2), Thickness | 1 per 400 tons | Coating test (AASHTO T-195) required for batch plants |
|  |  |  | Smoothness, Grade | On 50 ft. centers | Lot size is 2,000 yd2 |
|  | Independent Assurance | (4) | Density, Gradation, Oil Content, P.I., Fracture, Flat & Elongated, Sand Equivalent | 1 per 4,000 tons | Sampled and Tested as required by QAE/ME. |
| Asphalt Cement P-401 | Quality | N/A | N/A | N/A | Supplier Certification Required |
|  | Information | 1 qt. | ASTM D 3381 | 1 per 50,000 gal. or 1 per 200 tons | Sampled on project. Test for anti-strip if required by QAE/ME |
| Liquid Asphalt for: a. Prime Coat, P-602 b. Tack Coat, P-603 c. Seal Coats and Surface Treat, P-609, P-625, P-626 | Quality | N/A | N/A | N/A | Supplier Certification Required |
|  | Information | 1 gal. in plastic or glass jug | Various | 1 per 50,000 gal. or 1 per 200 tons | Sample must be tested by Lab which did not test material for Quality. Material sampled prior to dilution. |
| Cover Coat Material for Surface Treatment P-609 | Quality | 75 lbs. Aggregate | Wear, soundness, degradation, (1) | 1 per source prior to use | Allow 25 days for testing and transport. |
|  | Acceptance | (4) | Gradation, Fracture (3) | 1 per 500 tons | May be taken from stockpile or production. |
|  | Independent Assurance | (4) | Gradation, Fracture | 1 per 5,000 tons |  |
| Recommendations regarding stripping must be determined for each project. Run tests on the first 5 samples at the start of production from any source. If these tests indicate the material meets specifications, additional tests need only be performed on the assurance samples. Run tests on the first 10 samples at the start of production and after each change in material. If these tests indicate the material to be 5% or more above specification, additional tests need only be performed on the assurance samples. Size of sample for gradation determined by nominal maximum particle size. See the specified test method for minimum sample size. |

| Concrete P-501, P-605, P-610 Cement Water Coarse Aggregate Fine Aggregate Air Entraining Agent Joint Sealer Joint Filler Curing Materials | Quality | (a) 10 lbs. in can | ASTM C 150 | Approved Manufacturer or 1 per shipment | Allow 20 days for testing and transport. Manufacturer’s certification required. (1) |
| --- | --- | --- | --- | --- | --- |
|  |  | (b) N/A | N/A | N/A | Supplier Certification Required or accepted by the Project Engineer (PE) |
|  |  | (c) 100 lbs. | Wear, soundness | 1 per source | Allow 25 days for testing and transport |
|  |  | (d) 25 lbs. | Soundness | 1 per source | Allow 25 days for testing and transport. |
|  |  | (e ) N/A | N/A | N/A | Supplier Certification Required |
|  |  | (f) N/A | N/A | N/A | Supplier Certification required |
|  |  | (g) N/A | N/A | N/A | Supplier Certification Required |
|  |  | (h) N/A | N/A | N/A | Supplier Certification Required |
|  | Mix Design (2) | Aggregate: Coarse: 300 lbs. Fine: 100 lbs. Cement: 1 sack Additives: 1 qt. | Mix design | 1 per source prior to use. | Contractor furnished material. Allow 45 days for testing and transport. |
| Re-test any cement stored in silos or bins over six months, or in bags over two months. Complete the Concrete Plant Inspection prior to production. |

| Concrete (P-501, P-605, P-610) cont'd. |
| --- |
| Coarse Agg. | Acceptance (5) | (4) | Flat & Elongated (6), Gradation | 1 per 200 yd3 | Number consecutively CA-G-1 (2) |
| Fine Agg. |  | (4) | Gradation, Fineness Modulus | 1 per 200 yd3 | Number consecutively FA-G-1 (2) |
| Mix |  |  | Yield, Cement Factor, Slump, Water Cement Ratio, % Air, Smoothness, Grade | 1 per ½ days pour (1) or 1 per 200 yd3 | (2) |
| Mix |  | 2 cylinders or beams | Compressive Strength or Flexural Strength (3) | 1 per ½ days pour (1) or 1 per 200 yd3 | Test at 28 days. (2) |
| Mix | Information | Cylinders or beams | Compressive Strength or Flexural Strength (3) | As required (e.g. for 7 day break) |  |
| Coarse Aggregate | Independent Assurance | (4) | Gradation, All Deleterious, Flat & Elongated | 1 per 2,000 yd3 (with minimum of 1 per project if over 100 yd3 is placed) | Number correspond to acceptance samples |
| Fine Aggregate |  | (4) | Gradation, All Deleterious, Fineness Modulus |  |  |
| Mix |  |  | Yield, Cement Factor, Slump, Water Cement Ratio, % Air | 1 per project |  |
| Mix |  | 2 cylinders or beams | Compressive Strength or Flexural Strength (3) | 1 per 2,000 yd3 |  |
| Half day’s pour considered to be 6 hours or less. Commercial sources which are periodically inspected do not have to be tested if total quantity of concrete pour is less than 5 yd3 as determined by the PE. Placement reports summarizing all minor pours will be satisfactory. See page 6. Only required when strength criteria is included for the item. Size of sample for gradation determined by nominal maximum particle size. See WAQTC FOP for AASHTO T 27 and T 11 for minimum sample size. Truck inspections are required for each pour. Run tests on the first 10 samples at the start of production and after each change in material. If these tests indicate the material to be 5 % or more above specification, additional tests need only be performed on the assurance samples. |

| Misc. Hardware | Quality | See contract special provisions, PE’s inspection and acceptance | Certs/Mill reports approved by QA/ME or SME |
| --- | --- | --- | --- |
| Reinforcing Steel P-501, P-610 | Quality | 2 pieces 36 inches long per size and grade | 1 per 20 tons with minimum of 1 per project when a pay item | Mill reports approved by QA/ME or SME in lieu of testing, or APL. |
| Porous Backfill P-705 P-752 | Quality |  | Standard Density | As required by changes in material | Number consecutively PB-SD-1 |
|  | Acceptance |  | Density | 1 per installation | Number consecutively PB-D-1 |
|  |  | (2) | Gradation | 1 per source | Number consecutively PB-G-1. |
| Topsoil T-905 | Quality | 10 lbs. | Organic content, pH | 1 per source prior to use | Allow 15 days for testing and transport. |
|  | Acceptance | (2) | Gradation | 1 per 2,500 yd3 | Number consecutively TS-G-1 |
| Lighting Equipment L-100, L-104, L-107, L-111 | Within 30 days following contract award, the contractor must submit to the PE for approval a complete list of material and equipment that is proposed to be used for this item. The data must include catalogue cuts, diagrams, test reports, manufacturers’ certifications, etc. The above data must be submitted in 8 sets. Any proposed deviation from the Plans must also be submitted. |
| Reports to include heat numbers, fabrication date, physical and chemical properties. Size of sample for gradation determined by maximum particle size. See WAQTC FOP for AASHTO T 27 and T 11 for minimum sample size. |

MINOR QUANTITIES

A. Portland Cement Concrete. Concrete for the following items may be accepted on the basis of an approved mix design and placement reports documenting batch information and pour location, time, and quantity. Under this system, the producer must state on the delivery ticket accompanying each load of concrete, the class of concrete being furnished, the weights of cement, aggregates and water used in the batch, and the time of batching. Only State-tested aggregates and cement, or supplier certified cement, approved by the State Materials Engineer, may be used. Document each pour on a Concrete Placement Report. 1. Slope paving and headers 2. Paved ditch 3. Small culvert headwalls 4. Fence post footings 5. Catch basins, manhole bases, and inlets B. Small Quantities of Miscellaneous Materials. The primary documentation of delivery and placement may be the Project Materials Report Aggregates: -- Not to exceed 500 tons per item per project. Asphalt/Aggregate Mixtures: -- Not to exceed 900 tons per approved mix design. Bituminous Material: -- Not to exceed 60 tons per project. Paint: -- Not to exceed 20 gallons per project. Acceptance to be based on weights and analysis on the container label. Lumber: -- Not to exceed 10 MBM per project. Recognized commercial grades only may be used. Masonry Items: -- Not to exceed approximately 100 pieces. Subject to checking of nominal size and visual inspection. Plain concrete or clay pipe: -- Not to exceed 100 linear feet. Hardware: -- When a minor component to other small quantities of work. Topsoil: -- Not to exceed 6,000 yd2.