ITEM L-110
UNDERGROUND ELECTRICAL DUCT

DESCRIPTION
110-1.1 This item shall consist of underground electrical ducts installed in accordance with this specification at the locations and in accordance with the dimensions, designs, and details shown in the Plans. This item shall include the installation of all underground electrical ducts or underground conduits. It shall also include all trenching, marking, backfilling, removal, and restoration of any paved areas; manholes, concrete encasement, mandreling installation of steel drag wires and duct markers, capping, and the testing of the installation as a completed duct system ready for installation of cables, to the satisfaction of the Engineer. 

EQUIPMENT AND MATERIALS

110-2.1 GENERAL. All equipment and materials covered by referenced specifications shall be subject to acceptance through manufacturer's certification of compliance with the applicable specification when so requested by the Engineer.

110-2.2 BITUMINOUS FIBER DUCT. Bituminous fiber duct and fittings shall conform to the requirements of UL Standard 543.

a. Type I, for concrete encasement.

b. Type II, for direct burial.

110-2.3 ASBESTOS CEMENT DUCT. Asbestos cement duct and fittings shall conform to the requirements of Fed. Spec. W-C-571 and shall be one of the following, as specified in the proposal:

a. Type I, for concrete encasement.

b. Type II, for direct burial.

110-2.4 STEEL CONDUIT. Rigid steel conduit and fittings shall conform to the requirements of UL Standard 6, 514, and 1242.

110-2.5 CONCRETE. Concrete shall conform to Item P-610, Structural Portland Cement Concrete, 25 mm maximum size coarse aggregate.

110-2.6 PLASTIC CONDUIT. Plastic conduit and fittings shall conform to the requirements of Fed. Spec. W-C-1094 Type I, suitable for underground use either directly in the earth or encased in concrete. The conduit shall be one of the following as shown on the Plans:

a. Underground Plastic Duct shall be rigid, non-metallic, conduit, Schedule 40 PVC conforming to UL Standard 651 and NEMA TC-2, nominal size as indicated on the Plans. All fittings such as elbows, couplings, connectors, expansion joints, adapters, etc., used in the installation shall be Schedule 40 PVC conforming to UL Standard 514 and NEMA TC-3.

b. Underground Plastic Duct shall be Type III, rigid, HDPE pipe. The material shall have a cell classification of 345434C or better in accordance with ASTM D 3350. The nominal size shall be as indicated on the Plans with a minimum wall thickness of 3.9 mm. All fittings such as saddle fittings, elbows, couplings, connectors, adapters, etc., used in the installation shall be HDPE and shall be of the same material as the duct.

110-2.7 FLEXIBLE METAL CONDUIT. Flexible metal conduit shall be water-tight, listed for exposed or direct bury per UL-360, as a grounding conductor per NEC Article 351-9, and rated for temperatures between -55 oC and +105 oC.

110-2.8 TAPES.

a. Pipe sealing tape shall be Teflon, "Scotch" No. 48 or approved equal.

b. Corrosion preventive tape shall be "Scotch" No. 50 or approved equal.
CONSTRUCTION METHODS

110-3.1 GENERAL. The Contractor shall install underground ducts at the approximate locations indicated in the airport layout plans. The Engineer shall indicate specific locations as the work progresses. Ducts shall be of the size, material, and type indicated in the Plans or specifications. Where no size is indicated in the Plans or specifications, the ducts shall be not less than 75 mm inside diameter. All duct lines shall be laid so as to grade toward handholes, manholes and duct ends for drainage. Grades shall be at least 75 mm per 30 m. On runs where it is not practicable to maintain the grade all one way, the duct lines shall be graded from the center in both directions toward manholes, handholes, or duct ends. Pockets or traps where moisture may accumulate shall be avoided.

Seal all joints in the rigid steel conduit runs with Teflon pipe sealing tape applied to the threaded couplings. Wrap the completed joint with 2 layers of corrosion preventative tape, 1/2 lapped and extending 40 mm on both sides of the joints.

After the conduit run has been completed, pull a standard flexible mandrel not less than 300 mm long, having a diameter approximately 6 mm less than the inside diameter of the conduit, through the entire length of the conduit run, after which a brush with stiff bristles of at least the diameter of the inside of the conduit shall be pulled through the entire length of the conduit run to make certain that no particles of earth, sand, or gravel have been left in the line.
All ducts installed shall be provided with a No. 10 gauge galvanized iron or steel drag wire for pulling the permanent wiring. Sufficient length shall be left in manholes or handholes to bend the drag wire back to prevent it from slipping back into the duct. Where spare ducts are installed, as indicated on the Plans, the open ends shall be plugged with removable tapered plugs, designed by the duct manufacturers, or with hardwood plugs conforming accurately to the shape of the duct and having the larger end of the plug at least 6 mm greater in diameter than the duct.

All ducts shall be securely fastened in place during construction and progress of the work and shall be plugged to prevent seepage of grout, water, or dirt. Any duct section having a defective joint shall not be installed.

All ducts, except steel conduit, installed under runways, taxiways, aprons, and other paved areas shall be encased in a concrete envelope.

Where turf is well established and the sod can be removed, it shall be carefully stripped and properly stored.

Trenches for ducts may be excavated manually or with mechanical trenching equipment. Walls of trenches shall be essentially vertical so that a minimum of shoulder surface is disturbed. Blades of road patrols or graders shall not be used to excavate the trench. The Contractor shall ascertain the type of soil or rock to be excavated before bidding. All excavation shall be unclassified.

Trenches for burial of duct or conduit shall be of sufficient width to provide a minimum of 50 mm of lateral clearance between the duct or conduit and trench walls on both sides as shown on the Plans. Trenches for burial of duct or conduit shall be of sufficient depth as to assure 450 mm minimum duct or conduit burial depth below finished grade, plus 50 mm minimum of below duct or conduit bedding as shown on the Plans, plus adequate over excavation depth as required to slope and grade all duct or conduit installations to drain toward light bases or hand holes.
The bottom of all trenches shall be sloped and lined with a layer of bedding material of minus 6.3 mm material that is not less than 50 mm in depth, before placing any duct or conduit in the trenches. Bedding material shall be, sand, gravel, crushed aggregate, or other suitable material containing no organic, frozen, or other deleterious material.
Excavate foundations, footings, slabs, pads, manholes, handholes, ducts and/or duct banks, or light base assemblies so as to permit the placing or construction of the full width, length, and depth of the structure or object and the layer of bedding material, whenever bedding is required.
110-3.2 DUCTS ENCASED IN CONCRETE. Unless otherwise shown in the Plans, concrete-encased ducts shall be installed so that the top of the concrete envelope is not less than 450 mm below the finished subgrade where installed under runways, taxiways, aprons, or other paved areas, and not less than 450 mm below finished grade where installed in unpaved areas. Ducts under paved areas shall extend at least 900 mm beyond the edges of the pavement or 900 mm beyond any underdrains which may be installed alongside the paved area. Trenches for concrete-encased ducts shall be opened the complete length before concrete is laid so that if any obstructions are encountered, proper provisions can be made to avoid them. All ducts for concrete encasements shall be placed on a layer of concrete not less than 75 mm thick prior to its initial set. Where two or more ducts are encased in concrete, the Contractor shall space them not less than 37 mm apart (measured from outside wall to outside wall) using spacers applicable to the type of duct. As the duct laying progresses, concrete not less than 75 mm thick shall be placed around the sides and top of the duct bank. End bells or couplings shall be installed flush with the concrete encasement where required.

When specified, the Contractor shall reinforce the bottom side and top of encasements with steel reinforcing mesh or fabric or other approved metal reinforcement. When directed, the Contractor shall supply additional supports where the ground is soft and boggy, where ducts cross under roadways, or where otherwise shown on the Plans under such conditions, the complete duct structure shall be supported on reinforced concrete footings, piers, or piles located at approximately 1.5 meter intervals.

When clay or soapstone ducts are specified, they shall be installed with concrete encasement as described above. Clay conduit shall be of the single-bore type. Where the self-centering socket-joint type of single clay duct is used, conduit shall be built up, tier by tier, and separated only by sufficient mortar or fine aggregate concrete to bed the ducts evenly and fill all voids between ducts. Single ducts shall be jointed together and the joints grouted with Portland cement mortar. A suitable gasket (of rubber or other approved material) shall first be placed in the receptacle end of the duct, prior to the joining operation, in order to exclude all mortar from the duct.

Where the square bore butt joint type of clay duct, single or multicell, is used, sections shall be aligned with at least 4 steel dowel pins and joints wrapped with duct tape 150 mm wide and lapped 150 mm. All joints in a bank of single-bore ducts shall be staggered, beginning evenly from the manhole or handhole, by means of short lengths 150, 200, 230, 300, 380 mm long. Cement mortar shall be troweled around each and every joint. Voids in the duct bank, caused by the external shape of the corners of the conduit, shall also be filled with mortar. The joining and joints of soapstone duct shall be done in accordance with the manufacturer's recommendations.
110-3.3 DUCTS WITHOUT CONCRETE ENCASEMENT. Trenches for single-duct lines shall be not less than 150 mm nor more than 300 mm wide, and the trench for 2 or more ducts installed at the same level shall be proportionately wider. Trench bottoms for ducts without concrete encasement shall be made to conform accurately to grade so as to provide uniform support for the duct along its entire length.

A layer of sand, at least 100 mm thick (loose measurement) shall be placed in the bottom of the trench as bedding for the duct. The bedding material shall consist of sand , and it shall contain no particles that would be retained on a 6.3 mm sieve. The bedding material shall be tamped until firm.

Unless otherwise shown in Plans, ducts for direct burial shall be installed so that the tops of all ducts are at least 450 mm below the finished grade.

When two or more ducts are installed in the same trench without concrete encasement, they shall be spaced not less than 50 mm apart (measured from outside wall to outside wall) in a horizontal direction and not less than 150 mm apart in a vertical direction.

Trenches shall be opened the complete length before duct is installed so that if any obstructions are encountered, proper provisions can be made to avoid them.

110-3.4 PVC Conduit. Install PVC conduit where indicated on the Plans.

Fabricate the conduit runs as recommended by the conduit manufacturer. Make all joints square, tight, and leakproof. Do not allow bends or breaks in the joints. Use only solvents and cements, which are specifically recommended by the conduit manufacturer. Join together the complete run between each light base alongside the trench. Place in the trench and connect to the base assembly after the minimum cure time of the joint cement has elapsed and after inspection and approval is granted by the Engineer.

Make field cuts of the conduit true and square with a tool or lathe designed for the purpose. Debur and ream the conduit as required.

Bend PVC conduit at the job site only with a "Hot Box" or as recommended by the conduit manufacturer. Heat the conduit uniformly to obtain smooth bends without overheating. Conduit with a brown appearance shall not be used. Conduit with extremely sharp bends, kinks in the bends or which exhibits a significant visual defect shall not be used.

Install expansion fittings in each run of conduit between light base assemblies, at spacing not exceeding 18 m. The expansion fitting shall be of the same manufacturer as the conduit and shall be installed in accordance with the manufacturer's instruction. Expansion joints shall be installed a maximum of 3 m from the edge light bases or hand holes and shall be installed with joints 6 mm expanded, resulting in a minimum requirement of four expansion joints per 58 m run of conduit.
After the conduit run has been completed, pull a standard flexible mandrel not less than 300 mm long, having a diameter approximately 6 mm less than the inside diameter of the conduit, through the entire length of the conduit run, after which a brush with stiff bristles of at least the diameter of the inside of the conduit shall be pulled through the entire length of the conduit run to make certain that no particles of earth, sand, or gravel have been left in the line.

110-3.5 HDPE Conduit. Assemble high-density polyethylene conduit into runs on the surface and install in trenches after coupling of the section. Butt-weld the duct using the manufacturer's recommended procedures and equipment. Assure that the conduit is open, continuous and free of water and debris prior to installing cable. In underground conduit, pull a stiff bristle brush through the entire length of the conduit run immediately prior to the cable being installed.
110-3.6 DUCT MARKERS. Place marker tape 150 mm below final grade or below bottom of Crushed Aggregate Base Course in paved areas for the full length of the trenches above all ducts installed as indicated on the Plans. 

When called for in the Plans, the location of the ends of all ducts shall be marked by a concrete slab marker 600 mm square and 100 mm thick extending approximately 25 mm above the surface. The markers shall be located above the ends of all ducts or duct banks, except where ducts terminate in a handhole, manhole, or building.

The Contractor shall impress the word “DUCT” on each marker slab. He shall also impress on the slab the number and size of ducts beneath the marker. The letters shall be 100 mm high and 75 mm wide with width of stroke 12 mm and 6 mm deep or as large as the available space permits.

110-3.7 BACKFILLING. Backfill only after the duct has been placed, inspected and accepted by the Engineer. 

After concrete-encased ducts have been properly installed and the concrete has had time to set, the trench shall be backfilled in at least two layers with excavated material not larger than 50 mm in diameter and thoroughly tamped and compacted to at least the density of the surrounding undisturbed soil. If necessary to obtain the desired compaction, the backfill material shall be moistened or aerated as required. If duct is placed in the structural section (P-154, P-208, P-209) of a pavement such as for a runway or taxiway, the Contractor shall construct the backfill in accordance with the specifications for the material in which the duct is placed.

Trenches shall not be excessively wet and shall not contain pools of water during backfilling operations.

The trench shall be completely backfilled and tamped level with the adjacent surface: except that, when sod is to be placed over the trench, the backfilling shall be stopped at a depth equal to the thickness of the sod to be used, with proper allowance for settlement.

Any excess excavated material shall be removed and disposed of in accordance with instructions issued by the Engineer.

For ducts without concrete envelope, sand shall be placed around the ducts and carefully tamped around and over them with hand tampers. Sand shall be non frost susceptible with no particle larger than 6 mm. Sand shall be placed to provide a minimum of 50 mm of cover when compacted over and to the sides of the duct. The remaining trench may be filled with regular run of excavated material and thoroughly tamped as specified above. If duct is placed in the structural section (P-154, P-208, P-209) of a pavement such as for a runway or taxiway, the Contractor shall construct the backfill in accordance with the specifications for the material in which the duct is placed.

110-3.8 RESTORATION. Where sod has been removed, it shall be replaced as soon as possible after the backfilling is completed. All areas disturbed by the trenching, storing of dirt, cable laying, pad construction and other work shall be restored to its original condition. The restoration shall include any necessary topsoil, fertilizing, liming, seeding, sprigging, or mulching. All such work shall be performed in accordance with the FAA Standard Turfing Specifications. The Contractor shall be held responsible for maintaining all disturbed surfaces and replacements until final acceptance.

METHOD OF MEASUREMENT

110-4.1 Underground duct shall be measured by the meter of duct installed, measured in place, completed, and accepted. Separate measurement shall be made for the various types and sizes.

Items shown as lump sum will not be measured for payment.

BASIS OF PAYMENT

110-5.1 Payment will be made at the contract unit price for each type and size of single-way or multi-way duct completed and accepted. This price shall be full compensation for furnishing all materials and for all preparation, assembly, and installation of these materials, and for all labor, equipment, tools, and incidentals necessary to complete this item.

Payment will be made under:

Item L-110a
53 mm Rigid Steel Conduit - per meter

Item L-110b
53 mm Rigid Steel Conduit - per lump sum

Item L-110c
50 mm PVC Conduit - per meter

Item L-110d
50 mm PVC Conduit - per lump sum

Item L-110e
32 mm PVC Conduit - per meter 

Item L-110f
32 mm PVC Conduit - per lump sum

Item L-110g
50 mm PE Conduit - per meter

Item L-110h
50 mm PE Conduit - per lump sum

Item L-110i
Multi-Way Duct in Concrete - per meter


(# of conduit)

Item L-110j
Multi-Way Duct in Concrete - per lump sum


(# of conduit)

MATERIAL REQUIREMENTS
Fed. Spec. W-C-571
Conduit and Fittings, Nonmetal, Rigid; (Asbestos-Cement or Fire-Clay Cement), (For Electrical Purposes)

Fed. Spec. W-C-1094
Conduit and Fittings; Nonmetallic, Rigid, (Plastic)

UL Standard 6
Rigid Metal Conduit

UL Standard 514
Fittings for Conduit and Outlet Boxes

UL Standard 543
Impregnated-Fiber Electrical Conduit

UL Standard 1242
Intermediate Metal Conduit


L-110-

6/01


